## TABLE
|  |  | Firm Pipeline Capacity into Southern California |  |  | (MMcfd)
Wheeler Ridge
| Incoming Interstate Capacity |  |  |  | Take-Away Capacity
| PGT/PG&E | 600 |  |  | SoCalGas | 680 | 1,2,3,4
| Kern/Mojave | 1100 |  |  | PG&E No. Calif. | 520
| Occidental | 200 |  |  | EOR Market | 700
| Total | 1900 |  |  | Hector Rd. | 50
[5 empty] | K/M to PG&E | 200
[5 empty] | K/M to Las Vegas | 150
[5 empty] | OXY to PG&E | 200
[5 empty] | Total | 2500
(1) Take-away from PG&E limited to 520 MMcfd by Line 225 capacity from KRS to Wheeler Ridge w/650 psig from PG&E.
| (2) Mojave meters currently set to 500 MMcfd. |  |  | (3) Interconnect Capacity with Occidental is 200 MMcfd
(4) Total combined PG&E, Occidental, Kern/Mojave capacity assumes minimum flow of 160 MMcfd from Kern/Mojave.
Hector Road
| Incoming Interstate Capacity |  |  |  | Take-Away Capacity
| Mojave | 400 |  |  | SoCalGas | 50 | *
[5 empty] | EOR market | 400
[5 empty] | Wheeler Ridge | 400
[5 empty] | Total | 850
* Firm capacity is limited by TW deliveries at Needles. Hector Rd. meter capacity is 200 MMcfd.
No. Needles
| Incoming Interstate Capacity |  |  |  | Take-Away Capacity
| Transwestern | 1090 |  |  | SoCalGas | 750
[5 empty] | PG&E | 340
[5 empty] | Mojave | 340
[5 empty] | Total | 1430
Topock (South Needles)
| Incoming Interstate Capacity |  |  |  | Take-Away Capacity
| El Paso | 2230 |  |  | SoCalGas | 540
| Transwestern | 340 |  |  | PG&E | 1140
|  | 2570 |  |  | Mojave | 400
[5 empty] | SWGas | 150
[5 empty] | Total | 2230
Blythe
| Incoming Interstate Capacity |  |  |  | Take-Away Capacity
| El Paso | 1210 |  |  | SoCalGas | 1210
[5 empty] | East of California | na
[5 empty] | Total | 1210