## TABLE
|  |  | Firm Pipeline Capacity to Southern California |  |  | Exhibit No. 28
|  |  | MMcfd |  |  | I.99-07-003
INCOMING CAPACITY |  |  | SCG TAKE-AWAY |  | TAKE-AWAY CAPACITY
Wheeler Ridge |  |  | Wheeler Ridge |  | Wheeler Ridge
PG&E@KRS | 600 | {12} | 680 |  | SoCalGas | 680
Kern River@WR | 700 |  | {1,2,3,4} |  | Kern--EOR or other direct serve | 540 | {9}
Mojave@WR | 400 | {5} |  |  | Mojave--EOR or other direct serve | 400 | {5}
Occidental@Gosford | 200 |  |  |  | Occidental to PG&E Line 300 | 200 | {8} {11}
Total | 1900 |  |  |  | Total | 1820
Hector Road |  |  | Hector Road |  | Hector Road
Mojave | 400 |  | 50 | {6} | SoCalGas | 50
[5 empty] | EOR or Wheeler Ridge | 350
[5 empty] | Total | 400
No. Needles |  |  | No. Needles |  | No. Needles
Transwestern | 750 |  | 750 |  | SoCalGas | 750
Topock (South Needles) |  |  | Topock |  | Topock
El Paso | 2080 |  | 540 |  | SoCalGas | 540
Transwestern | 340 |  |  |  | PG&E Line 300 | 1140
Total | 2420 |  |  |  | Mojave | 400 | {5}
[5 empty] | Total | 2080
Blythe |  |  | Blythe |  | Blythe
El Paso | 1210 |  | 1210 |  | SoCalGas | 1210
L85, San Joaquin Calif |  |  | L85 |  | L85
Calif. | 150 |  | 150 |  | SoCalGas | 150
N. Coastal California |  |  | N. Coast |  | N. Coast
Calif. | 120 |  | 120 |  | SoCalGas | 120
TOTAL INCOMING CAPACITY |  |  | SCG TAKE-AWAY |  | TOTAL TAKE-AWAY CAPACITY
| 6150 | {10} | 3500 |  |  | 5530 | {7}
(1) Take-away from PG&E limited to 520 MMcfd by Line 225 capacity from Kern River St. to Wheeler Ridge w/650 psi pressure from PG&E
(2) Mojave meters currently set to 500 MMcfd but K/M noted capacity can be raised to 680 by adjusting existing meters.
(3) Interconnect Capacity with Occidental is 200 MMcfd projected to be in-service by 9/2000.
(4) Total combined PG&E, Occidental, Kern/Mojave of 680 MMcfd capacity assumes minimum flow of 160 MMcfd from Kern/Mojave.
(5) Mojave 400 counted under Hector Road. Not included in totals to avoid double counting
{6} Interconnect is for 200 MMcfd, but firm capacity limited to 50 MMcfd if 750 MMcfd TW supply flows at N. Needles
{7} Total is sum of SoCalGas (3500), Kern Direct serve (540), Mojave Direct Serve (350, assuming 50 to Hector Rd.), and PG&E Lines 300(1140)
{8} PG&E Line 300 has 1140 MMcfd capacity, and serves N. Calif., not S. Calif.
{9} Kern has 700 MMcfd capacity, but 160 MMcfd is already included in fow to SoCalGas at Wheeler Ridge.
{10} Upsteam Capacity flowing to SCG interconnects that could theoretically serve SCG given unlimited take-away and market demand
{11} Subject to Occidental pressures and final operational details of SCG/PG&E access agreements
{12} Source: Rich Hall of PG&E.
Avg. Daily Market
Source: 1999 Adopted BCAP forecast, including SCG-served EOR |  |  |  |  | SoCalGas | 2690
Source: 1999 CGR, p.14 All PG&E sources other than Calif/Canada/Other. |  |  |  |  | PG&E L300 flow to N. Calif. | 612
Source: 1998 FERC Form 567 for Kern (360 MMcfd) and Mojave (250 MMcfd) |  |  |  |  | Enhanced Oil Recovery (EOR), and Other Load Directly Served by K/M in S. Calif. | 610
[5 empty] | Total | 3912