## Links
Summaries	Histories	Descriptions	Sheets Total	Welcome to Alternative Energy.ods! / This is a large and intricately complex spreadsheet for equipment records / The column widths have been set up for a maximized window on a display with 1920 horizontal pixels
Batteries	B	Batteries	42
Chargers	BC	Battery Chargers	13
Controllers	C	Solar Charge Controllers	11
Converters	V	DC to DC Voltage Converters	15
HomeSolar	H	Home Solar Systems	2
Inverters	I	DC to AC Inverters	1
Locations	L	Location/Site Specific Information	21
Miscellaneous	Z	Miscellaneous Equipment	23
MobileApps	MA	VAPS Mobile Applications	2
Modules	M	Modbus devices (Wattmon Modules)	10
OneWires	O	OneWire Devices	18
Panels	P	Solar Panels	5
Supplies	S	Power Supplies	21
UPSs	A	AC UPSs	32
USBs	U	USB Devices (for Wattmons)	3
Wattmons	W	Wattmons	10
WebRelays	R	IP Addressable Relays	2
WISPers	WP	WISPer DC UPSs Built/Sold	18
Workbook Information
Codes	Other Sources for Information		Letter codes used throughout this workbook (mostly in "Other Sources" columns but also in descriptions)
Names	Named Ranges and Expressions		These are mostly self-documenting but the Names sheet elaborates on the names, what they mean, how they are used and tips for particularly confusing formulas
Tips	Notes and Tips for Editing this Workbook		Sheet Types, Cautions and Warnings, Shortcut Keys and Techniques
Versions	History of This Workbook		Chronological historical milestones, developments and notes on revisions for both the original Excel and present Calc versions of this workbook (development began in 2016)
LibreOffice Documentation (External Links)

## Codes
Codes	Other Sources for Information	Last General Review	Notes
Code	Source
AED	20150430^20211216 Alternative Energy (Wattmons).doc	1/4/23	Located in 20150430^20211216 Wattmon (Cynergy); Previously named as Alternative Energy.doc and before 7/5/16 it was Wattmon Setup Notes.doc
Ai11P	Apple iPhone 11 Pro Max		Paper file
BDC	BoltDepot.Com	11/25/22	Paper file for orders and invoices only
BII	BroadWave / Initial Inquiries	2/9/23	FTR and paper file; Also see DBB; Code has only been used twice for WP2 (2/9/23)
BFMS	Bill's Floor Machine Service	3/9/22	Paper file for orders and invoices only
BR	Battery Recycling		Paper files
CC	Consumer Cellular
CPSN	CradlePoint MBR95 Setup.doc	6/27/23	Was previously known as CradlePoint MBR95 Setup Notes.doc; Folder Setup Notes and TODO\CradlePoint MBR95 Wireless Router 4G (CP)
DBB	Documents > Business > ... > BroadWave (Florida)	2/9/23	This code not being used yet (2/9/23); Also see BII
DBD	Documents > Business > ... > Data Vision Services	2/7/23	Computer folder
DBS	Documents > Business > ... > ShowMe Ziplines (Swafford)		20170122;20190129;0213 ShowMe Ziplines (Swafford).zip
DBT	Documents > Business > ... > TurboNet	5/8/19	Includes related email files saved
DFD	David Fuller Solar.docx
DFP	Fuller, David C. - Home Solar System		Paper file
DKE	DigiKey Electronics	3/11/22	Paper file for orders and invoices only
DLG	DVS / Light Gig Colorado	11/30/22	FTRs and paper files
DNT	DVS / Non-Technical	11/27/22
DORM	DVS/ ONWT Remote Monitoring	11/30/22
DRD	DVS / Technical R&D	11/27/22
DTU	DVS / TurboNet Ukraine	11/30/22
DWP	DVS / WISPers	12/18/22
EBC	Electrolife Battery Company		Paper file for orders and invoices only
EML	Emails	*
FS	Income & Expense (Food Stamps).xlsx	5/9/19	Direct costs
FTR	For The Record	3/10/22	Any of a number of MS Word .docx files that are detailed chronological notes of a project, both technical lab notes and customer relations; Code used in Descriptions, "Other Sources" should use the FTR Code (many listed here in this table)
IMG	Images	2/4/23	Includes references to videos
JAK2	JAK2 Setup.doc	6/27/23	Was previously known as Setup JAK2.doc; Folder Setup Notes and TODO\JAK2
KTD	Karen Thomas Solar.docx
KTP	Thomas, Karen - Home Solar System		Paper file
KTX	Karen Thomas Solar.xlsx
LIB	Library	*	Manufacturer Downloads/Datasheets
LIPC	Listed Items Price Calculator.ods	5/2/22	In DBT folder (Documents > Business > TurboNet)
LBX	Brother Label Printer P-touch .lbx	3/12/22	Label file in D:\Documents\Brother P-Touch Labels
MBTF	Metal By The Foot	11/4/22	Paper files for orders and invoices only
MOU	Mouser Electronics	3/11/22
PBC	Precision Beer Cooler	1/13/23	Acronym used in descriptions for my $2,000 beer cooler (Engel, Dinico)
PLN	Pencil / Post-It Lab Notes	2/26/22	Paper file; Birddogging process notes; Times, voltages, temperatures, etc.
PTD	PTouchDirect.com	11/25/22	Paper files for orders and invoices only
SBC	Schauer Battery Chargers	3/7/22
SMS	SMS / Phone Messages	*	Refers to any type of phone messaging (SMS, MMS, photos, videos, recorded audio, etc.); Also see VIB
SOW	2008 Subaru Outback Wagon		3-ring binder, Service Manual Printouts & SAPS Notes; Also see SSRP
SPF	(Special Projects Fund) - Budget Management.xlsm	3/9/22	Sheet SPF - USB (US Bank balance and expenditures for business); Also see USB
SPSE	Sager Power Systems / Electronics	11/2/22	Paper file for orders and invoices only
SSC	Screenshots (ScreenShot Captor)		Referenced by date and time or filename
SSRP	Subaru - SAPS Related Purchases	5/15/19	Paper file; Also see SOW; Not to be confused with my old, old DE accounting file that was SSRW "Supplies for Shop and Repair Work"
T400s	T400s Setup.doc	6/27/23	Was previously known as Setup T400s.doc; Folder Setup Notes and TODO\T400s
T450s	T450s Setup.doc	6/27/23	Was previously known as Setup T450s.doc; Folder Setup Notes and TODO\T450s
T48P	TurboNet / MikroTik 48v Systems Pilot Project	1/23/22	FTRs and paper files
T48S	TurboNet / MikroTik 48v Systems Spares Orders	1/24/22
T48-2	TurboNet / MikroTik 48v System LWT	3/29/22
T48-3	TurboNet / MikroTik 48v System LSWT	6/14/22
T48-4	TurboNet / MikroTik 48v System CFS	7/22/22
TA1	TurboNet / Modified AC UPS #1	1/22/22	Paper file; Lexington Fiber Backup installed at TL TLNB
TA2	TurboNet / Modified AC UPS #2	1/22/22	Paper file; Richmond High School (RHS)
TEDS	TurboNet / Enclosures Design Specifications & Procurement	1/24/22	FTR and paper file
TFTP	Thoughts From The Porch	7/23/22	Used in descriptions
TM21F	TurboNet / Maintenance 2021 Fall	1/23/22	FTR and paper file
TM21S	TurboNet / Maintenance 2021 Spring	1/23/22	Paper file; (12) Site Visits 3/11/21 -> 6/21/21
TM22	TurboNet / Maintenance 2022	2/9/23	FTRs and paper files
TM23	TurboNet / Maintenance 2023	2/9/23
TMD	ThermoMart (Dinico)	3/12/22	Paper file for orders and invoices only
TOI	TurboNet / ONWT Installation	1/24/22	FTRs and paper files
TPC1	TurboNet / Power Cable Specifications (ONWT)	1/24/22
TPC2	TurboNet / Power Cable Splices	1/26/22
TSP	TurboNet / Solar Power Systems	1/19/22	Paper file; RW RN
TW1	TurboNet / WISPOWER #1	1/20/22	Paper file; W50 installed at RCWT
TW2-3	TurboNet / WISPOWER #2 and #3	1/20/22	Paper file; W100s installed at WWT RW
TW4-5	TurboNet / WISPOWER #4 and #5	1/20/22	Paper file; W100s installed at OSWT LWT
TW6-10	TurboNet / WISPOWER #6 to #10	1/21/22	Paper file; W100s installed at RWWT RHST ST ONWT OT
USB	US Bank	3/9/22	Paper file; Purchasing funds source; Generally used in Descriptions to refer to the bank in Richmond; Also see SPF which is better to use in Other Sources column as it isn't confused with USB "Universal Serial Bus" devices
UFS	20150821^20180504 UPSs For Sale.xlsx	1/4/23	Located in Setup Notes and TODO\Alternative Energy - Tracked Equipment and Locations
VIB	Viber
WCA	Wattmon (Cynergy) (Akash Heimlich)	1/4/23	Paper file
WCX	20180624^20190717 Wattmon Calibrations.xlsx	1/4/23	Located in 20150430^20211216 Wattmon (Cynergy); Previously named as Wattmon Calibrations.xlsx
WMBS	Warranties, Manuals, Bills of Sale	5/10/19	Paper file
WRD	20170310^20190919 WISPer DC UPS R&D Notes.doc	1/1/23	Or files in folder DBT > 20170310^20200615 WISPer DC UPS R&D
WS	White Sheet(s)	6/2/23	Drawings and notes on white sheets or scraps of paper, usually created in the "spur of the moment" to put down ideas for development of any type; Usually filed in project file if it exists, otherwise could be anywhere
WSN	20041213^20200922 Websites Setup Notes.doc	1/4/23	Located in Setup Notes and TODO\2001^20221020 Old, Decommissioned, Tabled\20041213^20200922 Websites

## Names
Names

## Tips
Tips	Notes and Tips for Editing this Workbook
Sheet Types
Beyond the Links and Codes sheets there are 3 distinct sheet types: Summary, History and Assembly (be careful in selecting groups of sheets as the different types have different arrangements)
Row 1 Groups
	Summary sheets: Identical; A1 link and C1 title from column C of Links
	History sheets: Most of them are A1 link and I1 title from columns B and C of Summary sheet; Except H0-H1 and WP1-WP6 use columns C and D from Summary sheet
	Assembly sheets: Identical; A1 link, D1 title from columns C and D of Summary sheet, E1 “Assembly / Parts List”
Row 2 is hidden on all Summary, History and Assembly sheets: It is used to construct the hyperlinks for cells A1 and the references for the titles in Row 1
	Summary sheets: Columns A, E, F and G with exactly the same formulas
	History sheets: Columns A, J, K, L and M with the same formulas except for K2 which matches on 1 or 2 characters (as needed) of the Links column B history sheet prefix
	Assembly sheets: Same as the History sheets matching on 2 characters (‘WP’)
Row 3 is hidden on all History sheets: It is used to find the last entry in the column below (which is then used by Row 6); Note that Summary and Assembly sheets don’t do this
History sheets: Columns A-H is Date/Time (all the same width), I is Description (varying widths), J is Other Sources (usually 0.8” wide), and K to AK depend heavily on the type of sheet that is needed
	As can be seen in the table to the left the History sheets often have widely differing structure beyond column J and the widths are optimized to maximize the Description column
	At present the most amount of time maintaining this sheet has to do with word wrapping in the Description column (perhaps the LibreOffice people will get this fixed soon)
Cautions and Warnings
Do NOT format cells that contain the HYPERLINK() function as Text! If the formula is edited then the hyperlink is destroyed and replaced with the function text
Particularly Useful Calc Shortcut Keys and Techniques
Ctl+F5		Toggle Sidebar, Navigator
Ctl+Home		Go to cell A1
Ctl+Space		Select entire column
Shift+Space		Select entire row
Ctl+PageUp		Go to previous sheet
Ctl+PageDn		Go to next sheet
Alt+Shift+Arrow		Optimal height/width based on current cell
Click Headers (select), ClickHold in Selection, Alt+Drag to new location, Drop (release mouse button)		Move column(s) or row(s) between two other columns/rows in one step
Click Headers (select), ClickHold in Selection, Ctl+Drag to new location, Drop (release mouse button)		Copy columns(s) or row(s) to another location (destination clobbered)
Click Headers (select), ClickHold in Selection, Ctl+Alt+Drag to new location, Drop (release mouse button)		Copy columns(s) or row(s) between two other columns/rows in one step
Click Headers (select), ClickHold in Selection, Drag to new location, Drop (release mouse button)		Move columns(s) or row(s) to another location (destination clobbered)
Alt+Space		Select Visible Rows Only (user defined)
Alt+V		Formula to Value (user defined)

## Versions
Versions	History of This Workbook
YYYYMMDD	History of the Microsoft Excel Workbook (Converted May 14, 2020 to LibreOffice Calc)
20160607	Created as Wattmon History & Maintenance.xlsx
20160611	Completed entering relevant records from Wattmon Setup Notes.doc, and also created Battery History & Maintenance.xlsx
20160623	Combined both of the previous efforts into one file Alternative Energy.xlsx (Wattmon Setup Notes.doc is in use for details that don't belong in this primary file)
20160705	Completed reorganization (tabs renamed and reordered, Links sheet, History links, Navigation links, summary information in row 1, etc.); Wattmon Setup Notes.doc renamed as Alternative Energy.doc
20160720	Added column "Battery C-Rating" to Locations, L1 and L2
20170205	Completed renaming of all Wattmon backups (short codes LnWnMn etc.) both here and in Alternative Energy.doc
20180409	Edits for Location "L0" completed (backup files renamed); Alternative Energy.doc Chronological MDY restructured to take advantage of short codes (LnWnMn etc.)
20180410	Added Summary and History sheets for WISPers
20180504	Added Summary and History sheets for AC UPSs
20180511	"Photos / Videos" column added to all History sheets, entries for all photos/videos completed
20180512	Added Summary and History sheets for Power Supplies and Battery Chargers
20180513	Defined Names 'Sheets' and 'SheetNames' (using Excel 4 macro function 'Get.Workbook'); Added sheet "Sheets" with links to all sheets in the workbook; Workbook is now Alternative Energy.xlsm (macro enabled)
20180513	Hyperlinks added to all History sheets headers for column lookups (row 4 LOOKUP, row 5 HYPERLINK in green): LOOKUPs don't error if nothing in column, HYPERLINKs go to sheet 'Sheets' if no matching sheet name
20180513	Hyperlinks added to all Summary sheets "Current" columns for values fetched from History sheets (green): History sheet is found from column A; Rows can be easily copied down for added items
20180513	"Locations" Summary sheet improved; Deleted locations no longer needed; Organized; Created detailed History sheets for locations that will have photos; "Latitude, Longitude" column with links to Google Maps
20180514	Reordered sheets: Sheets, Links, Summaries (alphabetical), Histories (alphabetical)
20180514	Row 1 link info moved to row 2 (hidden); All Summary and History Sheets use the same columns in row 2 (but History sheets have 1 or 2 character matching on Links sheet column B)
20180519	All sheets except "Sheets": A1 left justified; Row 1 font size 14; Column A Bold. Sheet "Sheets": Bold.
20180523	Added Summary Sheet 'MobileApps' (Histories MA, VAPS Mobile Applications) and populated with L_1->MA1 (HAPS) and L_2->MA2 (SAPS) from Summary Sheet 'Locations'
20180525	Added Summary and History sheets 'Miscellaneous' (Histories Z, Miscellaneous Equipment)
20180622	Added Summary sheet 'Inverters' (Histories I, DC to AC Inverters); Description for Summary Sheet Converters changed to 'DC to DC Voltage Converters'
20180727	Started adding WISPer Assembly / Parts List sheets (WP#A, modified summary sheet WISPers)
20190520	MAJOR MILESTONE: Completed review and update of History sheets for all Summaries that have been added since 4/10/18 and all entries are up to date
20190727	Introduced Code for Other Sources for Information; Added columns "Other Sources" to every History Sheet; Began review to use "Other Sources" and remove "Photos / Videos" columns (redundant)
20190730	Added Summary and History sheets 'HomeSolar' (Histories H, Home Solar Systems)
20190909	Completed review of all History sheets to use "Other Sources" and remove "Photos / Videos" columns [note added 5/15/20: a few got missed in sheets A1-A6]
20200514	On the Verge of Chronic "Insufficient Memory" Problems (Working Set >1.5 GB): Converted for use with LibreOffice Calc; Alternative Energy.xlsm is no longer being used (will be archived)
20230102	Alternative Energy.xlsm renamed as 20160607^20200514 Alternative Energy.xlsm and moved to new folder D:\Setup Notes and TODO\Alternative Energy - Tracked Equipment and Locations
	History of this LibreOffice Calc Workbook
20200514	Converted from Excel Alternative Energy.xlsm to Calc Alternative Energy.ods: Repaired all Row 1 and 2 links on the Summaries and Histories sheets; Man'f Data sheet hyperlinks corrected (caused by reorganization not port to Calc); History sheets Row 5 are all OK
20200515	Column widths of all sheets manually corrected (Calc uses about 25% more screen space than Excel); “Photos / Videos” column removed from sheets A1-A6 (missed in review on 9/9/19)
20200516	History sheets A1 shows Summary sheet name and History sheet name (i.e. “UPSs: A1”); Properties > Font > Embed fonts in the Document (file is 6x bigger but loading/saving speeds are about the same)
20200518	Moved WP Assembly sheets to the end (they are of a different structure and shouldn’t be selected together with the History sheets) / History sheets Row 6 HYPERLINKs simplified with no use of named ranges Sheets and Sheetnames, as these depend upon an Excel function not easy to replicate in Calc, see 20180513, and I’m OK with “bad hyperlinks” as they go nowhere / History sheets headers no borders/boxes, light blue (except cells for data from below are green as before); All History sheets column widths optimized to maximize the width of the Description column and Word wrap problems fixed / Added helpful information to Links sheet “History Sheet Column Width Groups” and “Notes and Tips for Editing this Worksheet”
20200518	Assembly sheets: Headers borders/boxes modified, light blue fill; Light gray fill to distinguish assembly groups; Column widths optimized
20200518	Summary sheets values from History sheets simplified (no named ranges, can still be copied down as before but to copy to the right must adjust static column numbers for the cells on the History sheets) / Sheet “Sheets” removed (no need, and I’m happy with F5 or ^F5 which opens the Navigator); Named ranges SheetNames, Sheets and SheetsCount deleted (no longer needed) / Links.A1 deleted and “Summaries, Histories, Description” table moved to top left (there are no links that go to Links.A1); Links sheet headers and tables “prettied up” with no boxes/borders and light blue headings
20200519	History sheets Row 5 moved to Row 3 (hidden); Added 2 more columns to the table on Links “History Sheet Column Width Groups” (Stop Column, Sheets)
20200527	Simplified formulas being used in “Hours” columns on History sheets: Regex search for ROUND\(\((.*?)\)\*24\*4,0\)/4 and replaced with ($1)*24 which results in (EndTime–StopTime)*24 (500+ occurrences; I no longer care to round to the nearest 15 minutes, that was a time-sheet need)
20200529	Summary sheets: Headers improved with light blue scheme as for all other sheets (includes eliminating and unifying columns for the removal of the “Inventory Sticker” section); Column widths optimized
20200604	Improved Summary sheet Locations: Columns added for WISPer/UPS and Battery
20220308	Adopted the convention of placing references to computer folders/paths and files/filenames in italics: This improves and simplifies this type of reference by removing the need to place a long path or filename in quotes, makes them stand out in a long description, and makes it possible to shorten and abbreviate these names in repeated occurances and still understand later that those words are talking about a file or path on the computer; Searched and italicized more than 1000 occurances (.doc .docx .pdf .jpg .jpeg .png .xls .xlsm .xlsx .ods .odt .txt .url .mov .mp4 .gz .csv .tar .cgi .cgs .js .ini .cgc .hex .epp .dat .lbx folders/paths TODO SPF FTR)
20220309	Moved Codes Table from sheet Links to new sheet Codes; It has grown so large that it was taking over the Links sheet, and this new sheet allows for more space for Notes
20220902	Expanded WISPers Summary sheet for new W150 product line: Columns added and reorganized; Newly created WP11 and WP12 History sheets have new columns for Charger, Load Supply and DC-DC; Other sheets that reference them have new column WISPer
20230102	Alternative Energy.ods moved to new folder D:\Setup Notes and TODO\Alternative Energy - Tracked Equipment and Locations
20230128	Description Linking implemented on all history sheets that benefit from this new technique: Reduced redundancy; Clearly shows which entries apply to a group of devices (or locations); Reduced file size; These are "one way" static links that are used only inside a Summary group / Vertical Merging in Columns: Especially for the Description Links, but being applied in other columns as well; Reduces eye strain and file size / Old Hyperlinks: There are many "one way streets" (mostly from before May 2020 conversion to Calc) / I am routinely leaving these in place, because the time to go back and correct them all would be immense, and they can be identified mostly by the fact they go to a sheet cell A1 or are underlined / Currently correcting the Old Hyperlinks only if I need to study historical information in more detail for business purposes (after all, the business was not founded to create the worlds largest most accurate collection of historical data on a hundred devices and locations)
20230203	YYYYMMDD formula on all History sheets in "Stop Column": The formula is complex, but only uses about 24 bytes per History sheet line; Easily copied/replicated; Enables searching the entire workbook for a particular date
20230613	Named Ranges and Expressions: Used to eliminate intermediate values (hidden formulas) in rows 2 and 3 of all Summary and History sheets; "Self-documentating" as the names greatly aid understanding when formulas are examined / Cell B1 on all History sheets (History sheet Type A, B, C or D): Used for the Summary column (letter) where the History Sheet_Name is found; These History Type letters are hidden by the merge of cell A1 over columns to the right; See named expressions SummaryCol and SummaryColText / The vast majority of History sheets are Type A (currently 249 sheets A1 to Z22), but WISPers Part, Order and Assembly sheets (currently 13 sheets WP1A to WP14-15A) are Types B (WP*P), C (WP*O) or D (WP*A)
20230614	Custom Color Palette for the highlight and text colors that are most commonly used: Enables choosing colors from a much shorter list and by name (hover tip); Names of colors are generally {where used} with additions to make the names unique or easier to understand / The Custom Color information is not saved in Alternative Energy.ods and I only set them up on T400s: Custom colors are part of the LibreOffice Configuration on each computer (Tools > Options), they are not properties of a single document / I haven't done a very good job making sure all those option settings are identical between T400s/T450s/JAK2; If we move to another computer for editing this workbook we'll have to replicate at least the Custom Color information / Tools > Options > LibreOffice > Advanced > Open Expert Configuration > Search for "CustomColor": Two keys (color #, name) could be used to copy to another computer; I'm not going to do it now because this list continues to be updated as I work with this workbook
20230615	Added sheets Names, Tips and Versions: Moved workbook history from Links to Versions; Moved "Notes and Tips for Editing this Worksheet" from Links to Tips; Deleted "History Sheet Column Width Groups" from Links (old info no longer relevant, not updated for years now) / Cleaned up Links and added new Sections: Workbook Information (Codes, Names, Tips and Versions); LibreOffice Documentation (external links); Welcome to Alternative Energy.ods! (to be used for very general introductory information)
20230617	Added column Sheets Total to the main table on Links to show the total number of History sheets listed in the Summary sheet's column A; These are array formulas that tally up only valid existing sheets (tabs) listed on each Summary
20230627	LibreOffice on T400s has been upgraded from version 7.2.6.2 to 7.4.7.2; Tested and examined notable improvements and bugs; Improvements to shortcut keys; New file Libre Office Setup Notes now being used for configuration changes and notes

## Batteries
Batteries		Batteries

History	Name	Description	Man'f Data		DCV	Capacity AH					Source / Supplier	Order Date	Warranty Expires	Rec'd Date	Cost	Paid With	Date Codes				Other Stickers and Man'f Labels	Current
		Man'f + Model No.		Type		3C	1C	C/3	C/5	C/10	C/20	C/100					Man'f	(Date)	Finishing	(Date)		Status	Location	Charger
B0	Old_Honda	Standard Battery B10		SLA	12					30?				FEB 2010	$80???					Armor Plate Automotive 4; 51-40 590 CA 575 CCA; FEB 10 [punched out date sold]; B0 Charging Parameters.lbx	Failing	L	S1
B1	20150422	Trojan 27TMX	20150704 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	Battery Outfitters, Columbia MO	4/22/15		4/22/15	$272.57	C1 MC	[not found]		A5	Jan 2015	Installed 5-1-15 [Mark Webb @ RW]	Sold	L7	WP4
B2	20150715_1/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	7/15/15		7/15/15	$177.09	C1 MC	U03C5AA	03/03/15	E5	May 2015	Purchased for Rayville Water Tower Summer 2015; Watered 12/31/15; Installed at Swafford Rayville N Tower 2/19/16	Sold	Salvaged	-
B3	20150715_2/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	7/15/15		7/15/15	$177.09	C1 MC	U03C5AA	03/03/15	E5	May 2015	Purchased for Rayville Water Tower Summer 2015; Watered 12/31/15; Installed at Swafford Rayville N Tower 2/19/16	Sold	Salvaged	-
B4	20150808_1/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	8/8/15		8/8/15	$177.09	C1 MC	X23E5AA	05/23/15	G5	Jul 2015	Purchased for SAPS Summer 2015, Used at Rayville Water Tower some; Watered 12/22/15; Removed from Rayville Water Tower 4/22/16	Applied	L	A3-4
B5	20150808_2/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	8/8/15		8/8/15	$177.09	C1 MC	X23E5AA	05/23/15	G5	Jul 2015	Purchased for SAPS Summer 2015, Used at Rayville Water Tower some; Watered 12/22/15; Removed from Rayville Water Tower 4/22/16	Applied	L	A3-4
B6	20150910_1/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	9/10/15		9/10/15	$165.06	CA VISA	X26E5AA	05/26/15	G5	Jul 2015	Purchased for and Installed at Swafford Rayville N Tower ~9/19/15; Watered 11/17/15; Removed from Swafford Rayville N Tower 2/19/16; Watered 2/19/16; Watered 4/22/16; Installed Rayville Water Tower 4/22/16	Applied	L	A3-4
B7	20150910_2/2	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	9/10/15		9/10/15	$165.06	CA VISA	X26E5AA	05/26/15	G5	Jul 2015	Purchased for and Installed at Swafford Rayville N Tower ~9/19/15; Watered 11/17/15; Removed from Swafford Rayville N Tower 2/19/16; Watered 2/19/16; Watered 4/22/16; Installed Rayville Water Tower 4/22/16	Applied	L	A3-4
B8	20160421_1/4	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	4/21/16		4/21/16	$154.53	CS VISA	XK125AA0754	11/12/15	A6	Jan 2016		Applied	MA2	BC1
B9	20160421_2/4	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	4/21/16		4/21/16	$154.53	CS VISA	UL085AA0550	12/08/15	[not found]		20160421_2/4 WWT 5/8/18	Sold	L3	WP7
B10	20160421_3/4	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	4/21/16		4/21/16	$154.53	CS VISA	XI215AA0699	09/21/15	[not found]		20160421_3/4 WWT 5/8/18	Sold	L3	WP7
B11	20160421_4/4	Trojan T-105	20180316 T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	BFMS (Bill's Floor Machine Service), Kansas City MO	4/21/16		4/21/16	$154.53	CS VISA	UK125AA0773	11/12/15	A6	Jan 2016		Applied	MA2	BC1
B12_13	20150805_7.5_1	SigmasTek SP12-7.5	20180503 SP12-7.5HR(T2).pdf	AGM	24		5.28	5.94	6.20	7.19	7.50		BatterySharks.com	7/31/15		8/5/15	$31.61	C1 MC	150702				SP12-7.5HR(12V7.5AH/T2); Standby 13.5-13.8; Cycle 14.4-14.9; Initial current <2.25A	Dead	Salvaged	-
B14_15	20150805_7.5_2	SigmasTek SP12-7.5	20180503 SP12-7.5HR(T2).pdf	AGM	24		5.28	5.94	6.20	7.19	7.50		BatterySharks.com	7/31/15		8/5/15	$31.61	C1 MC	150702				SP12-7.5HR(12V7.5AH/T2); Standby 13.5-13.8; Cycle 14.4-14.9; Initial current <2.25A	Dead	Salvaged	-
B16_17	20150805_7.5_3	SigmasTek SP12-7.5	20180503 SP12-7.5HR(T2).pdf	AGM	24		5.28	5.94	6.20	7.19	7.50		BatterySharks.com	7/31/15		8/5/15	$31.61	C1 MC	150702				SP12-7.5HR(12V7.5AH/T2); Standby 13.5-13.8; Cycle 14.4-14.9; Initial current <2.25A	Dead	Salvaged	-
B18_21	20150805_18	SigmasTek SP12-18	20180503 SP12-18(T2).pdf	AGM	48		11.7	14.6	15.2	17.0	18.2		BatterySharks.com	7/31/15		8/5/15	$123.95	C1 MC	150702				Received 8/5/15 Battery Sharks C1, $123.95/4 delivered; SP12-18HR(12V18AH/NB); Standby 13.5-13.8; Cycle 14.4-14.9; Initial current <5.4A; T2 UPS 2KVA	Dead	Salvaged	-
B22_25	20150813	SigmasTek SP12-18	20180503 SP12-18(T2).pdf	AGM	48		11.7	14.6	15.2	17.0	18.2		BatterySharks.com	8/8/15		8/13/15	$123.95	C1 MC	150702				Received 8/13/15 Battery Sharks C1, $123.95/4 delivered; SP12-18HR(12V18AH/NB); Standby 13.5-13.8; Cycle 14.4-14.9; Initial current <5.4A; T1 UPS 1.5KVA	Dead	Salvaged	-
B26	20170718	SigmasTek SP12-100	20180503 SP12-100(NB).pdf	AGM	12	65.1	82.8		88.0	101.0	105.8		BatterySharks.com	7/14/17		7/18/17	$170.39	BMW VISA DVS					SP12-100(12V100AH/NB); Standby 13.5-13.8; Cycle 14.4-15.0; Initial current <30A; [Inventory sticker added 6/28/22]	Sold	L18	WP1
B27_28	20171108	SigmasTek SP12-100	20180503 SP12-100(NB).pdf	AGM	24	65.1	82.8		88.0	101.0	105.8		BatterySharks.com	11/6/17		11/8/17	$330.98	Paypal					SP12-100(12V100AH/NB); Floating 13.5-13.8; Cycle 14.4-15.0; Initial current <30A	Sold	L16	A2
B29_34	20171212_1	SigmasTek SP12-9	20180504 SP12-9(T2).pdf	AGM	72		5.99	8.43	7.65	8.60	9.00		BatterySharks.com	12/7/17		12/12/17	$97.67	AB VISA					SP12-9(12V9AH/T2); Floating 13.5-13.8; Cycle 14.4-15.0; Initial current <2.55A	Dead	Salvaged	-
B35_40	20171212_2	SigmasTek SP12-9	20180504 SP12-9(T2).pdf	AGM	72		5.99	8.43	7.65	8.60	9.00		BatterySharks.com	12/7/17		12/12/17	$97.67	AB VISA					SP12-9(12V9AH/T2); Floating 13.5-13.8; Cycle 14.4-15.0; Initial current <2.55A	Dead	Salvaged	-
B41_46	20171212_3	SigmasTek SP12-9	20180504 SP12-9(T2).pdf	AGM	72		5.99	8.43	7.65	8.60	9.00		BatterySharks.com	12/7/17		12/12/17	$97.67	AB VISA					SP12-9(12V9AH/T2); Floating 13.5-13.8; Cycle 14.4-15.0; Initial current <2.55A	Dead	Salvaged	-
B47_52	20171212_4	SigmasTek SP12-9	20180504 SP12-9(T2).pdf	AGM	72		5.99	8.43	7.65	8.60	9.00		BatterySharks.com	12/7/17		12/12/17	$97.67	AB VISA					SP12-9(12V9AH/T2); Floating 13.5-13.8; Cycle 14.4-15.0; Initial current <2.55A	Dead	Salvaged	-
B53	LI_20180601	Sharpcost 5250mAh Li-Ion for Samsung GT-I9300		Li-Ion	3.8					Amazon.com (Sharpcost)	5/30/18		6/1/18	$18.13	USB VISA					Model: HB901; 5250mAh; 19.95Wh; Made in China	Discarded	-	-
B54	20190605	Trojan 27TMX	20150704 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	6/5/19	6/5/20	6/5/19	$211.74	Cash	[not found]				SG268FA0176 [printed, probably date/man'f code]	Sold	L1	WP3
B55	LI_20190618	Acevan Direct 2300mAh Li-Ion for Samsung GT-I9300 with Micro USB charger cable		Li-Ion	3.8					Amazon.com (Acevan Direct)	6/12/19		6/18/19	$15.98	USB VISA					X001LEVLOT Galaxy S3 Battery 2300mAh Battery (3 Year Warranty) [box with battery and USB micro charger]; Acevan For Galaxy SIII 2300mAh High Capacity Li-ion Battery [battery front]; Acevan Li-ion 3.8V Replacement for Galaxy S3/I9300/1747 3.8VDC 2300mAh 8.74 Wh [battery rear]	Lost	MO River	-
B56	20200507_1/2	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	5/7/20	5/7/21	5/7/20	$188.93	AB VISA	[not found]		B0	Feb 2020	RL079FA0437 [stamped on top middle, probably S/N]; MOTIVE	Sold	L10	WP5
B57	20200507_2/2	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	5/7/20	5/7/21	5/7/20	$188.93	AB VISA	[not found]		B0	Feb 2020	RL079FA0451 [stamped on top middle, probably S/N]; MOTIVE	Sold	L11	WP6
B58	20200610_1/4	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	6/8/20	6/10/21	6/10/20	$168.46	USB/AB VISAs	[not found]		D20	Apr 2020	RA239FA0094 [stamped on top middle, probably S/N]; Circular sticker D20 [black on white, same location as Motive batteries date code, so probably date code]	Sold	L17	WP11
B59	20200610_2/4	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	6/8/20	6/10/21	6/10/20	$168.46	USB/AB VISAs	[not found]		D20	Apr 2020	SG268FA0171 [stamped on top middle, probably S/N]; Circular sticker D20 [black on white, same location as Motive batteries date code, so probably date code]	Sold	L13	WP8
B60	20200610_3/4	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	6/8/20	6/10/21	6/10/20	$168.46	USB/AB VISAs	[not found]		E0	May 2020	RC270FA0530 [stamped on top middle, probably S/N]; MOTIVE	Sold	L14	WP9
B61	20200610_4/4	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	6/8/20	6/10/21	6/10/20	$168.46	USB/AB VISAs	[not found]		E0	May 2020	RC270FA0533 [stamped on top middle, probably S/N]; MOTIVE	Sold	L15	WP10
B62	20201215_1/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0092 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B63	20201215_2/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0094 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B64	20201215_3/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0096 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B65	20201215_4/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0165 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B66	20201215_5/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0171 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B67	20201215_6/6	Trojan 27TMX	20200508 27TMX_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	12				85	97	105	117	BFMS (Bill's Floor Machine Service), Kansas City MO	12/11/20	12/15/21	12/15/20	$164.73	USB VISA	[not found]		K0	Oct 2020	SH310FA0177 [stamped on top middle, S/N]; MOTIVE	Sold	L5	A27
B68	20211001_1/4	Trojan T-105	20210825 T-105 Data Sheet - T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	EBC (Electrolife Battery Co, Lawrence KS)	9/28/21	10/1/22	10/1/21	$203.41	USB VISA	LH281	08/28/21	J1	Sep 2021	LH281AAD0629 [stamped top middle, man'f date code & S/N]; MOTIVE	Sold	L14	BC6
B69	20211001_2/4	Trojan T-105	20210825 T-105 Data Sheet - T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	EBC (Electrolife Battery Co, Lawrence KS)	9/28/21	10/1/22	10/1/21	$203.41	USB VISA	SI131	09/13/21	K1	Oct 2021	SI131AAD0349 [stamped top middle, man'f date code & S/N]; MOTIVE	Sold	L14	BC6
B70	20211001_3/4	Trojan T-105	20210825 T-105 Data Sheet - T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	EBC (Electrolife Battery Co, Lawrence KS)	9/28/21	10/1/22	10/1/21	$203.41	USB VISA	RI131	09/13/21	K1	Oct 2021	RI131AAD0822 [stamped top middle, man'f date code & S/N]; MOTIVE	Sold	L18	WP12
B71	20211001_4/4	Trojan T-105	20210825 T-105 Data Sheet - T105_Trojan_Data_Sheets.pdf	Flooded Deep Cycle	6				185	207	225	250	EBC (Electrolife Battery Co, Lawrence KS)	9/28/21	10/1/22	10/1/21	$203.41	USB VISA	RI131	09/13/21	K1	Oct 2021	RI131AAD0835 [stamped top middle, man'f date code & S/N]; MOTIVE	Sold	L18	WP12

## Chargers
Chargers		Battery Chargers

History	Name	Description		Man'f Data	AC Input		DCV	Max Charge Amps	Battery Temp Sensor	Stages	Flooded Lead Acid (Voltages)				Sealed Lead Acid (Voltages)				Other Charge Profiles?	Source / Supplier	Order Date	Warranty Expires	Rec'd Date	$.$$ Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description		V	A					B	A	F	E	B	A	F	E					Status	Location	Batteries	WISPer
BC1	TS_1	Trace Engineering TS812SB	TS Series Inverter / Charger	20150221 - 3141ts-series_revnew.pdf	80-120	15	12	30	Optional	3	14.7	60 min	13.4		14.3	60 min	13.6		No	Bargain place in Richmond			~2004	~$78		419561	120VAC 60Hz; SSRW 9-11-06 [felt tip]; Nuetral Bonded to GND Inside this Device (GFCI requires it); Man'f 2nd Q 2002	Applied	MA2	B8/11
BC2	BTJ_1	DelTran 021-0123	Battery Tender Junior	20170319 021-0123 man.pdf	120	0.18	12	0.75	No	3		<80hrs					NewEgg.com	5/24/15	5/24/20	5/29/15	24.99	PSC		12V 750mA; INPUT 120V~,0.18A,60Hz; OUTPUT 12V 750mA	Applied	L	Gravely
BC3	ENC	Mean Well ENC-180-12	Desktop Battery Charger	20170721 ENC-180 Series Desktop Battery Charger.pdf	90-264	1.9	12	12	Optional	3	14.2	<10%	13.4		14.0	<10%	13.6		Yes	TRC Electronics	7/13/17	7/14/20	~7/20/17	84.85	BMW DVS VISA	RB6B002680	INPUT 100-240V~2.2A 50/60Hz; OUTPUT 13.8V 12A	Available	L	-
BC4	SCP_PS1	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					MOU	7/28/17	7/28/19	~8/1/17	27.93	BMW DVS VISA			Sold	L18	B26	WP1
BC5	SCP_PS2	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Optional	2			15.0					MOU	7/28/17	7/28/19	~8/1/17	27.93	BMW DVS VISA			Sold	L18	B26	WP1
BC6	SBC_1	Schauer JAC2512B	25A 12V with BTS	20210904.0 Schauer Charger Specifications, compiled @ DVS.pdf	115/230	12/6	12	25	Yes	3	14.8	2.9 A	13.5		14.4	2.9 A	13.5		Yes	SBC	9/27/21	9/30/23	10/2/21	285.11	USB VISA	J2512121-902134	AC INPUT: 115V or 230V by MANUAL SWITCH; 50/60 Hz (15A at 115V); [front panel above jack] EXTERNAL TEMPERATURE SENSOR; [front panel FLA/SLA switch has been removed and black tape covers labels]	Sold	L14	B68/69
BC7	SBC_2	Schauer JAC2512B	25A 12V with BTS	20210904.0 Schauer Charger Specifications, compiled @ DVS.pdf	115/230	12/6	12	25	Yes	3	14.8	2.9 A	13.5		14.4	2.9 A	13.5		Yes	SBC	11/17/21	11/22/23	12/10/21	291.61	USB VISA	J2512121-902202	AC INPUT: 115V or 230V by MANUAL SWITCH; 50/60 Hz (15A at 115V)	Prep	L	-
BC8	SBC_3	Schauer JAC2512B	25A 12V with BTS	20210904.0 Schauer Charger Specifications, compiled @ DVS.pdf	115/230	12/6	12	25	Yes	3	14.8	2.9 A	13.5		14.4	2.9 A	13.5		Yes	SBC	11/17/21	11/22/23	12/10/21	291.61	USB VISA	J2512121-902201	AC INPUT: 115V or 230V by MANUAL SWITCH; 50/60 Hz (15A at 115V)	Prep	L
BC9	SCP_PS3	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					DKE	6/24/22	6/24/24	6/27/22	39.99	USB VISA	SC184J6650	INPUT: 100-240VAC 1.5A 50/60Hz; OUTPUT: +V & B+ +13.8V 5.4A; MAX. 74.5W	Sold	L17	B58	WP11
BC10	SCP_PS4	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					DKE	6/24/22	6/24/24	6/27/22	39.99	USB VISA	SC184J6654	INPUT: 100-240VAC 1.5A 50/60Hz; OUTPUT: +V & B+ +13.8V 5.4A; MAX. 74.5W	Sold	L18	B70-71	WP12
BC11	SCP_PS5	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					DKE	11/25/22	11/25/24	11/29/22	36.38	USB VISA	SC26575666	INPUT: 100-240VAC 1.5A 50/60Hz; OUTPUT: +V & B+ +13.8V 5.4A; MAX. 74.5W	Sold	L		WP13
BC12	SCP_PS6	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					MOU	3/8/23	3/8/25	3/10/23	37.80	USB VISA	SC26575714	INPUT: 100-240VAC 1.5A 50/60Hz; OUTPUT: +V & B+ +13.8V 5.4A; MAX. 74.5W	Assembly	L		WP14
BC13	SCP_PS7	Mean Well SCP-75-12	75 W Battery Charger Power Supply	20170718 SCP-75.pdf	85-264	1.5	12	5.4	Yes	2			13.5					MOU	3/8/23	3/8/25	3/10/23	37.80	USB VISA	SC26575720	INPUT: 100-240VAC 1.5A 50/60Hz; OUTPUT: +V & B+ +13.8V 5.4A; MAX. 74.5W	Assembly	L		WP15

## Controllers
Controllers		Solar Charge Controllers

History	Name	Description		Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Serial Number	Build Date	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description					Status	Location	WISPer
C1	Genasun_1	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	4/22/15	4/22/20	4/27/15	$106.63	C1 MC	60804		4/29/15 Jumper Installed for Flooded battery, Remove to use Sealed battery; 20 Amp Fuse Replaced 7/11/15; Genasun #1	Sold	L7	WP4
C2	Genasun_2	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/4/15	5/4/20	5/15/15	$111.57	C1 MC	61264	4/17/15	5/20/15 Jumper Installed for Flooded battery, Remove to use Sealed battery; Genasun #2	Sold	L10	WP5
C3	TriStar_1	TriStar TS-MPPT-60 with TS-RM-2 Morningstar Meter			WholeSaleSolar.com	5/22/15		5/29/15	$183.62	C1 MC				Returned	-
C4	Genasun_3	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	8/16/15	8/16/20	8/23/15	$111.53	PSC	62692	6/4/15	Left-side base plate cut off for SAPS application [rear]; 34V Max 12V + - - +	Sold	L	WP2
C5	Genasun_4	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	9/10/15	9/10/20	9/15/15	$105.41	CA VISA	62687		9/16/15 Jumper Installed for Flooded battery, Remove to use Sealed battery; Genasun #4	Sold	L2
C6	Genasun_5	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	9/10/15	9/10/20	9/15/15	$105.41	CA VISA	62683	6/4/15	Genasun #5; 1/19/17 Jumper Installed for Flooded battery, Remove to use Sealed battery; Genasun_5 (C6), Rec'd 9/15/15, $105.41 CA VISA [base underside]	Sold	L1	WP3
C7	Genasun_6	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/26/20	5/26/25	6/2/20	$92.50	USB VISA	123740	1/6/20	C7 Genasun_6	Sold	L11	WP6
C8	Genasun_7	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/26/20	5/26/25	6/2/20	$92.50	USB VISA	126736	3/17/20	C8 Genasun_7	Sold	L3	WP7
C9	Genasun_8	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/26/20	5/26/25	6/2/20	$92.50	USB VISA	126737	3/17/20	C9 Genasun_8	Sold	L13	WP8
C10	Genasun_9	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/26/20	5/26/25	6/2/20	$92.50	USB VISA	126738	3/17/20	C10 Genasun_9	Sold	L14	WP9
C11	Genasun_10	Genasun GV-10-Pb-12V	10.5A MPPT, 12V Lead Acid	20150422 GV-10_2012_manual_1112.pdf	alteEstore.com	5/26/20	5/26/25	6/2/20	$92.50	USB VISA	126739	3/17/20	C11 Genasun_10	Sold	L15	WP10

## Converters
Converters		DC to DC Voltage Converters

History	Name	Description		Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description					Status	Location	WISPer
V1	EPE_1	EDACPOWER ELEC. ED1075	ED1075-24V-5.5x2.1 center positive [PowerStream]; DC INPUT: 11-16Vdc; DC OUTPUT: 24V 4.0A Max. 75W MAX.		PowerStream.com	4/22/15	Voided	4/24/15	$85.45	PSC	67 [Man'f]; DATE CODE 9/2013 [Man'f punches]; #1; Repaired 7/9/15, Internal Fuse Removed, ONLY Use a 10 Amp Fast Blow Fuse	Available	L
V2	EPE_2	EDACPOWER ELEC. ED1075	ED1075-24V-5.5x2.1 center positive [PowerStream]; DC INPUT: 11-16Vdc; DC OUTPUT: 24V 4.0A Max. 75W MAX.		PowerStream.com	5/4/15	Voided	5/6/15	$85.45	PSC	67 [Man'f]; DATE CODE 9/2013 [Man'f punches]; Spare (#2)	Input Cut	L
V3	PS_1	PowerStream SR700-24	12V to 24V DC/DC Converter		PowerStream.com	5/16/15		5/23/15	$52.67	C1 MC		Returned	-
V4	PS_2	PowerStream NBPSU150	150 Watt Universal Laptop Power Supply, 12V input		PowerStream.com	5/22/15		5/29/15	$79.09	PSC		Returned	-
V5	SPS_1	SuperPowerSupply.com Car Charger	Buck regulator with cigarette lighter input		eBay.com	8/16/15		8/20/15	$0.00	PSC	V#5	Available	SAPS Box
V6	PS_3	PowerStream DC2012	DC/DC 10-20V Input (12V), 12V 50W Output	20180615 PowerStream DC2012.pdf	PowerStream.com	8/30/15		9/4/15	$95.15	PSC	V#6 [PCB front & back]	Assembly	MA2
V7	PS_4	[Moved to Summary sheet Inverters]	I1
V8	EPE_3	EDACPOWER ELEC. ED1075	ED1075-24V-5.5x2.1 center positive [PowerStream]; DC INPUT: 11-16Vdc; DC OUTPUT: 24V 4.0A Max. 75W MAX.		PowerStream.com	9/10/15	Voided	9/14/15	$85.45	C1 MC	67 [Man'f]; DATE CODE [Really not sure]	Parts	L
V9	TP_1	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	DKE	10/7/21	10/7/24	10/11/21	$225.29	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Sold	L14
V10	TP_2	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	DKE	11/17/21	11/17/24	11/19/21	$221.80	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Sold	L10
V11	TP_3	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	DKE	11/17/21	11/17/24	11/19/21	$221.80	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Sold	L17	WP11
V12	TP_4	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	SPSE	10/14/22	10/14/25	10/18/22	$223.31	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; T995891832; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Sold	L18	WP12
V13	TP_5	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	SPSE	10/14/22	10/14/25	10/18/22	$223.31	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Sold	L	WP13
V14	TP_6	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	SPSE	10/14/22	10/14/25	10/18/22	$223.31	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Available	L	WP14
V15	TP_7	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	SPSE	10/14/22	10/14/25	10/18/22	$223.31	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Available	L	WP15
V16	TP_8	Traco Power TEP 150-2418WI	150w, Wide Input 9-36vdc , Output 48-57.6vdc	20210821.22 TEP 150WI Series Application Notes - tep150wi_application.pdf	SPSE	10/14/22	10/14/25	10/18/22	$223.31	USB VISA	IN: 9-36 VDC; OUT: 48 VDC / 3.2 A; AFN15024S48W; U112521848; +Vi +Vi -Vi -Vi Ctrl +Vo -Vo Trim1 Trim2	Available	L	WP16

## HomeSolar
HomeSolar		Home Solar Systems

History	Assembly	Name	Description	Other Names and Descriptions	Order Date	Contract Total	Operational Date	Warranty Expires	Current
							Total Cost	Total Hours	Status	Location	Batteries
H0		KT	Karen Thomas	Off-Grid Hybrid with Propane Generator and Backup Heat	5/28/19	$0.00			$60	80	Cancelled	L8
H1		DF	David C. Fuller	Off-Grid Small House, Consulting	8/21/19	$729.00	9/13/19		$71	91	Operational	L9	(8) L16RE-B

## Inverters
Inverters		DC to AC Inverters

History	Name	Description		Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description					Rec'd Date				Status	Location
I1	PS_4	PowerStream INV1224	12VDC to 24VAC Inverter, 40 Watts	20180629 PowerStream PST-INV1224 User's Manual Scan_2pages.pdf	PowerStream.com	9/8/15		9/18/15	$106.15	C1 MC	V#7 [On discarded package, PS_4 was 'Converters' V7 until moved to Inverters 6/22/18]	Available	L

## Locations
Locations		Location/Site Specific Information

History	Short Name	Description	Latitude, Longitude	Status	Solar Panel Total Watts	Tilt Angle	Charge Controller Maximum Watts	Battery AH	Battery C-Rating	Charge Efficiency	Peukert Constant	7 Day Average Total Load Watts	Battery	WISPer	Charger	Load Supply	DC-DC

L	Shop	202 W 3rd ST, Rayville (also used if in storage somewhere in the building)	39.349365,-94.064525	Active
L0	Bench	202 W 3rd ST, Rayville, being worked on (various devices)	39.349365,-94.064525	Active
L1	RW	Rayville Water Tower	39.348980,-94.066326	Active	-	-	-	105	C/20	-	-	-	B54	WP3
L2	RN	Rayville North (Swafford) Tower	39.380940,-94.068300	Active	200	54	140	215	C/20	-	-	11.0	Swafford		C5
L3	RCWT	Richmond City Water Tower	39.288350,-93.996220	Active					B9/10	WP7
L4	TL	TurboNet Lexington office, 924 Main ST	39.185820,-93.883690	Moved					-		-
L5	RHS	Richmond High School, 451 E South St, Richmond, MO 64085	39.269550,-93.968100	Active					B62-B67		A26-A27
L6	WWT	Wellington Water Tower	39.132755,-93.986800	No Backup					-	-
L7	OSWT	Odessa South Water Tower	38.959434, -93.940953	Active					B1	WP4
L8	KT	Karen Thomas, 10 Acres near W 174th & Dowdy RD	39.403331, -94.088216	Cancelled
L9	DF	David C. Fuller, Small House S of 12696 Cave Lane, Excelsior Springs (Wood Heights) MO 64024	39.320038, -94.164780	Active					(8) L16RE-B
L10	LWT	Lexington Water Tower	39.188175, -93.851851	Active					B56	WP5			V10
L11	RWWT	Richmond West Water Tower	39.245579, -94.064835	Active					B57	WP6
L12	RHST	Richmond High School Tower	39.269588, -93.969147	No Backup					-	-
L13	ST	Skeeter Tower	39.175663, -93.781672	Active					B59	WP8
L14	ONWT	Odessa North Water Tower, 7909 Barkertown Rd, Odessa, MO 64076	39.044733, -93.964203	Active					B60 B68/69	WP9	BC6		V9
L15	OT	Oak Tower, 43364 Walnut Lane, Richmond, MO 64085	39.275718, -93.915323	Active					B61	WP10
L16	TLNB	TurboNet Lexington New Building, 109 S 10th ST	39.184941, -93.883650	Active					B27_28		A2
L17	LSWT	Lexington South Water Tower ("Big Blue"), 16245 Locust Grove Ln	39.145240, -93.854221	Active					B58	WP11
L18	CFS	Carrollton Fire Station Water Tower, 708 Harvest Hills DR	39.364303, -93.480816	Active					B26 B70-71	WP1 WP12
L19	CCC	Carrollton Country Club Water Tower, Country Club Drive, 9FJX+7Q7, Carrollton, MO 64633	39.380670, -93.500553	No Backup

	MobileApps	VAPS Mobile Applications (Locations)

	Locations without detailed History sheets
	India	Akash Heimlich, Wattmon.com, Aureville
	SAPS Box	A collection of parts slated to be installed in the Subaru Auxiliary Power System, W side, 202 W 3rd ST, Rayville
	TurboNet Toolbag	Collection of tools for working on tower installations; Usually 202 W 3rd ST, Rayville, but sometimes in Subaru (or on gray rolling cart)
	Jen	Jen and Travis, W 2nd ST, Rayville (temporary loan of Trace and 27TMX)
	Garage	Temporary staging location for loading into a vehicle
	Salvage	To be recycled (Shop) or already recycled (Salvage Yard) - Used for Batteries
	Subaru	Temporary staging location for onsite work

	These codes and short names are used in the notes, as a guide to finding inventory and to label files and backup sets from the Wattmons.

## Miscellaneous
Miscellaneous		Miscellaneous Equipment

History	Name	Description		Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	$ Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description					Rec'd Date					Status	Location	WISPer
Z0	E_1	Engel MT35F-U1	Dual Voltage Refrigerator, 32 Quarts, Sawafuji Electric Co., Ltd.	20190513 Owner's Guide + Invoice Scan_7pages.pdf	Engel, FL	8/29/11		~9/1/11	919.00	CS	NKT-0005	Fridge/Freezer; POWERED BY ENGEL SWINGMOTOR; EQUIPPED WITH Turbo Fan COOLING BOOSTER; AC120V 0.71A 60 Hz; DC 12/24V 2.5/1.3A; HFC-134a 1.8 OZ; DESIGN PRESSURE P.S.I.HIGH235 LOW 135; SERIAL NO. N_DE SERIE NKT-0005 TT; MADE IN THAILAND	Applied	L
Z1	CP_1	CradlePoint MBR95	Wireless "N" Router	20150205 MBR95_Manual_3.6.3.pdf	3Gstore	2/20/13		2/25/13	104.98	PSC	MM120239001515	Default Password: 4414a48e; MAC Address: 00304414a48e; SSID: MBR95-48e; MFG DATE: SEP 2012	Applied	L
Z2	CP_2	CradlePoint MBR95	Wireless "N" Router	20150205 MBR95_Manual_3.6.3.pdf	eBay	8/16/15		8/20/15	88.00	PSC	MM130191900141	Default Password: 44160841; MAC Address: 003044160841; SSID: MBR95-841; H/W ver: 1.0	Available	L
Z3	TEC_1	TE Connectivity V23130-C2021-A412	Latching Relay 260A 12V SPST	20180310 ENG_DS_V23130-X0000-A001_0612.pdf	DigiKey	8/16/15		8/19/15	68.04	C1		Tyco Electronics; 13 37; 1-1414939-4; Load 14V/Coil 14V	Assembly	MA2
Z4	TEC_2	TE Connectivity V23130-C2021-A412	Latching Relay 260A 12V SPST	20180310 ENG_DS_V23130-X0000-A001_0612.pdf	DigiKey	8/16/15		8/19/15	68.04	C1		Tyco Electronics; 14 46; 1-1414939-4; Load 14V/Coil 14V	Assembly	MA2
Z5	MS_1	Murata 3020-01101-0	Shunt 200A/50mV	20150819 Shunts - dpm_shunts-25677.pdf	Mouser	8/19/15		8/22/15	27.65	C1		50MV; 200AMP	Assembly	MA2
Z6	MS_2	Murata 3020-01101-0	Shunt 200A/50mV	20150819 Shunts - dpm_shunts-25677.pdf	Mouser	8/19/15		8/22/15	27.65	C1		50MV; 200AMP	Assembly	MA2
Z7	MA_1	Murata DCA5-20PC-6-DC4-RL-C	Digital Panel Ammeter 2/20/200/2000A 50mV Low Power Red LED	20150819 Ammeters - dca520pc.pdf	Mouser	8/19/15		8/22/15	60.42	C1		DATEL Digital Panel Meters; PN: 4978758; B409C; REV H; 16924B409C [barcode]	Assembly	MA2
Z8	MA_2	Murata DCA5-20PC-6-DC4-RL-C	Digital Panel Ammeter 2/20/200/2000A 50mV Low Power Red LED	20150819 Ammeters - dca520pc.pdf	Mouser	8/19/15		8/22/15	60.42	C1		DATEL Digital Panel Meters; PN: 4978758; B409C; REV H; 16924B409C [barcode]	Assembly	MA2
Z9	MV_1	Murata DMS-20PC-0-DCM-B-C	Digital Panel Voltmeter 4.50 to 19.99V Blue LED	20150819 Voltmeters - pc0-dcms.pdf	Mouser	8/19/15		8/22/15	60.42	C1		DATEL Digital Panel Meters; PN: 4942132; B522C; REV H; 13mA(MAX); 13770B522C [barcode]	Assembly	MA2
Z10	MV_2	Murata DMS-20PC-0-DCM-B-C	Digital Panel Voltmeter 4.50 to 19.99V Blue LED	20150819 Voltmeters - pc0-dcms.pdf	Mouser	8/19/15		8/22/15	60.42	C1		DATEL Digital Panel Meters; PN: 4942132; B522C; REV H; 13mA(MAX); 13728B522C [barcode]	Assembly	MA2
Z11	DI_1	Dwyer Instruments PLVT1	Compact Digital Thermostat		Amazon	9/8/15		9/10/15	38.89	CA		Date Code: 2014-01-22	Available	L
Z12	VC_1	Vag Com KKL 409.1	OBD-II USB Adapter for use with FreeSSM software (Subaru and other vehicles)	20180522_1350 VagCom Adapter eBay Detailed Description.pdf	eBay	5/22/18		5/25/18	19.88	USB VISA		OBD II [embossed in blue plastic connector body]	Applied	MA2
Z13	Ai11	Apple iPhone 11 Pro Max	Silver, 256GB	User Guide iOS 13	Apple	6/17/20	6/17/21	6/18/20	1728.90	USB & AB VISAs	FK1CF4Z1N70J		Active	L
Z14	MV_3	Murata DMS-20PC-8-DCM-C	Digital Panel Voltmeter 30.0 to 199.9V Red LED	20150819 Voltmeters - pc0-dcms.pdf	Mouser	12/29/20		1/1/21	53.63	USB VISA	14290C033C	DC VOLTAGE MONITOR; 7mA(MAX); GND -; +	Sold	L5
Z15	IRT_1	Fluke 62 MAX+	Infrared Thermometer, -22-1202⁰F, 12:1 DSR	20210831.1 Fluke 62 MAX+ Infrared Thermometer User Manual - 62max-62maxplus_manual.pdf	Test Equipment Depot	8/31/21	9/2/24	9/8/21	159.95	USB VISA	5086410MV	3M DROP; -30⁰ TO 650⁰ C; WATER/DUST RESISTANT IP54; Manufactured: Sep 2020; Country of origin Malaysia-L1	Available	L
Z16	EX_1	Extech 380947	True RMS AC/DC Mini Clamp Meter	20210925.1 Extech User Guide 380947 Revision A - 380947A_UM-en.pdf	Test Equipment Depot	9/25/21	10/1/22	10/4/21	276.20	USB VISA	A21240563	CAT II 600V; CAT III 300V; EN61010-2-032	Available	L
Z17	IT_1	ITECH IT8512A+	DC Electronic Load 150V/30A/300W	20210926.2 IT8500+ Series User Manual - IT8500_Series_Users_Manual.pdf	Circuit Specialists, Tempe, AZ	9/27/21	11/30/22	12/3/21	600.51	USB VISA	802143041767310328	IT8512A VER--1.53 [Info (Shift-7)]	Available	L
Z18	D2D_1	Dinico DIN-S-CF	Differential Temperature Controller with 2 Sensors	20211012 ThermoMart.com DIN-S-CF Manual (last version).pdf	ThermoMart	10/17/21		~10/22/21	46.85	USB VISA		AC110V; Temp Range -50⁰C - 110⁰C; Sensor NTC 25⁰C=10K B=3435; Relay Output Amp 5A/AC220V 10A/AC110V 10A/DC12V; [Sensor wire labels T1/T2]	Sold	L14
Z19	D2D_2	Dinico DIN-S-CF	Differential Temperature Controller with 2 Sensors	20211012 ThermoMart.com DIN-S-CF Manual (last version).pdf	ThermoMart	11/17/21		11/22/21	45.83	USB VISA		AC110V; Temp Range -50⁰C - 110⁰C; Sensor NTC 25⁰C=10K B=3435; Relay Output Amp 5A/AC220V 10A/AC110V 10A/DC12V; [Sensor wire labels T1/T2]	Sold	L
Z20	D2D_3	Dinico DIN-S-CF	Differential Temperature Controller with 2 Sensors	20211012 ThermoMart.com DIN-S-CF Manual (last version).pdf	ThermoMart	11/17/21		11/22/21	45.83	USB VISA		AC110V; Temp Range -50⁰C - 110⁰C; Sensor NTC 25⁰C=10K B=3435; Relay Output Amp 5A/AC220V 10A/AC110V 10A/DC12V; [Sensor wire labels T1/T2]	Sold	L17
Z21	MV_3	Murata DMR20-10-DCM-R-C	Digital Panel Voltmeter 6 to 75V Red LED, 1.2" Round Hole	20230211 Datasheet DMR20-10-DCM-R-C - dmr20-10-dcm.pdf	Murata	11/21/22		12/2/22	0.00		10772C131C	REV D	R&D	L	WP14
Z22	MV_4	Murata DMR20-10-DCM-R-C	Digital Panel Voltmeter 6 to 75V Red LED, 1.2" Round Hole	20230211 Datasheet DMR20-10-DCM-R-C - dmr20-10-dcm.pdf	Murata	11/21/22		12/8/22	0.00		10791C131C	REV D	R&D	L	WP15

## MobileApps
MobileApps		VAPS Mobile Applications

History	Short Name	Description		Vehicle			Current
		Man'f + Model No.	More Description	Year	Make	Model	Total Cost	Total Hours	Status	Batteries
MA1	HAPS	Honda Auxiliary Power System	VAPS Prototype #1; Battery on roof; MAIN-AUX contactor and analog meters controlled by dashboard switches	1985	Honda	Civic Wagon			Sold	Deep Cycle
MA2	SAPS	Subaru Auxiliary Power System	VAPS Prototype #2; Batteries on rear bumper; Wattmon based with manual and automatic control; Digital meters	2008	Subaru	Outback Wagon	$4635	574	Tabled	B8/11

	Locations	Location/Site Specific Information (Fixed Locations)

## Modules
Modules		Modbus devices (Wattmon Modules)

History	Name	Description		Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
			Model No.			Rec'd Date					Status	Location	Wattmon
M1	C252_1	25 Amp Dual Channel Current Sensor	C252	6/18/15	6/18/16	6/24/15	$100.91	C1 MC		C252 #1, Ordered 6/18/15, Rec'd 6/24/15, 1 year warranty expires 6/18/16 [as per photo shot onsite 6/16/16]	Applied	L	W10
M2	C252_2	25 Amp Dual Channel Current Sensor	C252	7/13/15	7/13/16	7/15/15	$100.91	C1 MC		#2 Ordered 7/13/15 Rec'd 7/15/15 1 year warranty; 9/18/15 Calibrated w/BK Precision on Wattmon #2. Two loops, each sensor, 0-12.5A.	Available	L	W10
M3	I3O2_1	Input and Output Module	I3O2	7/27/15	7/27/16	7/31/15	$65.59	C1 MC, JAK Ck#4003		I302 #1 (of 2) Ordered 7/27/15, Rec'd 7/31/15 Warranty Expires 7/27/16 $65.59 w/S&H, C1 & JAK Ck#4003	Available	L	W10
M4	I3O2_2	Input and Output Module	I3O2	7/27/15	7/27/16	7/31/15	$65.59	C1 MC, JAK Ck#4003		I302 #2 (of 2) Ordered 7/27/15, Rec'd 7/31/15 Warranty Expires 7/27/16 $65.59 w/S&H, C1 & JAK Ck#4003	Available	L	-
M5	C752_1	75 Amp Dual Channel Current Sensor	C752	8/16/15	8/16/16	8/24/15	$107.18	C1 MC		C752 #1 Ordered 8/16/15, Rec'd 8/24/15 1 Year Warranty Expires 8/16/16, 85.26 + 21.92 S&H = $107.18, C1	Assembly	MA2	-
M6	C252_3	25 Amp Dual Channel Current Sensor	C252	9/11/15	9/11/16	9/14/15	$78.43	C1 MC & DVS VISA	CS201508007	C252 #3, Ordered 9/11/15, Rec'd 9/14/15, 1 year warranty expires 9/11/16	Available	L	-
M7	C252_4	25 Amp Dual Channel Current Sensor	C252	9/11/15	9/11/16	9/14/15	$78.43	C1 MC & DVS VISA	CS201508006	C252 #4, Ordered 9/11/15, Rec'd 9/14/15, 1 year warranty expires 9/11/16; Ordered 9/11/15, Rec'd 9/14/15; Calibrated, 6/11/16, Loop1: 0-25A, Loop2: 0-12.5A (2 loops)	Available	L	W7
M8	I8O8_1	8-Channel Digital I/O Module with Relay Board and AC Adapter	I8O8	4/2/18	~4/12/19	4/12/18	$23.50	Website Work	IO8201712001	[All 3 parts] I8O8_1, (M8), Rec'd 4/12/18; [I8O8] INPUT OUTPUT MODULE, Rev 2.0; [Relay Board] www.probots.co.in, 8 Channel Relay Board; [AC Adapter] Foxlink, MODEL NO.:FA 1202000ST, INPUT:AC 90-265V 50/60 Hz, OUTPUT:12V 2A, S/N:114804792, P/N:19080027	Assembly	MA2	-
M9	A10_1	10-Channel ADC Module	A10-12V	4/2/18	~4/12/19	4/12/18	$21.50	Website Work	A10201708057	A10-12V, ANALOG MODULE, Rev 1.2	Applied	L	W10
M10	LCD_1	LCD Screen 20x4	WM-LCD	4/2/18	~4/12/19	4/12/18	$23.50	Website Work	LCD20160816	Rev. 1.0; JHD 204A; Cynergy 2013	Assembly	MA2	-

## OneWires
OneWires		OneWire Devices

History	Name	Description	Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Other Stickers and Man'f Labels	Current
		Model No. + Description					Status	Location	Wattmon
O1	T_1	DS18B20 (?) Digital Temperature Sensor		(Not Certain)	7/13/15		7/15/15	$0.00		T-Sensor #1	OK, Harness	L	-
O2	T_2	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	7/27/15	7/27/16	7/31/15	$4.00	JAK Ck# 4003 8/24/15	T-Sensor #2	OK, Harness	L	-
O3	T_3	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	7/27/15	7/27/16	7/31/15	$4.00	JAK Ck# 4003 8/24/15	T-Sensor #3	BAD	L	-
O4	T_4	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	7/27/15	7/27/16	7/31/15	$4.00	JAK Ck# 4003 8/24/15	T-Sensor #4	BAD	L	-
O5	T_5	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	7/27/15	7/27/16	7/31/15	$4.00	JAK Ck# 4003 8/24/15	T-Sensor #5	BAD	L	-
O6	T_6	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #6; Ordered 9/11/15, Rec'd 9/14/15	BAD	L	-
O7	T_7	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #7; Ordered 9/11/15, Rec'd 9/14/15	BAD	L	-
O8	T_8	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #8; Ordered 9/11/15, Rec'd 9/14/15	BAD	L	-
O9	T_9	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #9; Ordered 9/11/15, Rec'd 9/14/15	BAD	L	-
O10	T_10	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #10; Ordered 9/11/15, Rec'd 9/14/15	BAD, Cut Off	L	-
O11	T_11	DS18B20 Digital Temperature Sensor	20180422 Datasheet Maxim DS18B20.pdf	Wattmon.com	9/11/15	9/11/16	9/14/15	$3.92	C1 MC & DVS VISA	T-Sensor #11; Ordered 9/11/15, Rec'd 9/14/15	BAD	L	-
O12	T_12	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O12 (T_12) Rec'd 12/18/21	BAD?	L	-
O13	T_13	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O13 (T_13) Rec'd 12/18/21	BAD?	L	-
O14	T_14	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O14 (T_14) Rec'd 12/18/21	BAD?	L	-
O15	T_15	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O15 (T_15) Rec'd 12/18/21	Available	L
O16	T_16	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O16 (T_16) Rec'd 12/18/21	Available	L
O17	T_17	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O17 (T_17) Rec'd 12/18/21	Available	L
O18	T_18	SEN-11050 SparkFun Temperature Sensor (DS18B20)	20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf	DigiKey	12/15/21		12/18/21	$12.95	USB VISA	O18 (T_18) Rec'd 12/18/21	Available	L

## Panels
Panels		Solar Panels

History	Name	Description	Physical Size (LxWxT Inches)	Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Other Stickers and Man'f Labels	Current
		Man'f + Model No. + Description					Status	Location
P1	P_1	Fennel PWP-100W 100W 12V Polycrystalline	47.3 x 21.7 x 1.4		eBay.com Sollarfennel	4/22/15		4/28/15	$116.00	PSC	Man'f Model No. & technical data; Barcode sticker (s/n) 1405P100P002251; Panel #1	Available	L
P2	P_2	Fennel PWP-100W 100W 12V Polycrystalline	47.3 x 21.7 x 1.4		eBay.com Sollarfennel	7/8/15		7/15/17	$125.00	PSC	Man'f Model No. & technical data; Barcode sticker (s/n) 1405P100P001721; Panel #2	Available	L
P3	P_3	SunPower PowerFree AFP-100W-Mono 100W 12V Monocrystalline Semi-Flexible	41.8 x 21.4 x 0.13		AFP Power, St. Louis, MO	8/19/15		8/20/15	$212.99	PSC	Man'f Module Type & technical data; Panel #3	Available	L
P4	P_4	Renogy RNG-100D 100W 12V Monocrystalline	47.1 x 21.3 x 1.4		eBay.com RenogySolar	9/10/15		9/15/15	$135.00	PSC	Panel #4	Sold	L2
P5	P_5	Renogy RNG-100D 100W 12V Monocrystalline	47.1 x 21.3 x 1.4		eBay.com RenogySolar	9/10/15		9/15/15	$135.00	PSC	Panel #5	Sold	L2

## Supplies
Supplies		Power Supplies

History	Name	Description		Man'f Data	AC Input			DC Outputs	Output 1			Output 2		Output 3		Current Limiting	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	$.$$ Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description		V	A	W		V	A	W	V	A	V	A					Status	Location	WISPer
S1	HZ_1	Heathkit IP-2718	Tri-Power Supply (Heath/Zenith)	20180511 Heath Zenith Tri-Power Supply Model SP-2718.pdf	100-135 / 200-270	1.5	100	3	5	1.5		0-20	0.5	0-20	0.5	Yes	AK					120/240V, 1-1/2 AMP; EIA-416; 120/240VAC 50/60Hz; 90 WATTS	Needs R&R	L
S2	BK_1	BK Precision 9110	100W/60V/5A Multi Range DC Power Supply	20150804 9110_series_manual.pdf	99-121 / 198-242	3.2	300	1	0-60	0-5					CC/CW	Amazon.com	8/3/15	8/3/16	8/6/15	231.05	CA VISA	183E15135	LINE RATING 50/60Hz 300VA MAX; FUSE 3.15AT, LINE 100Vac 110Vac; FUSE 2.5AT, LINE 220Vac 240Vac	Available	L
S3	DE_1	Delta Electronics PMT-24V150W1AA	24V 150W Switching Power Supply	20180512 Datasheet_pmt-24v150w1aa-774709.pdf	90-132 / 180-264	3.0		1	22.8-27.6	6.5	156					Hiccup	MOU	2/17/18		3/2/18	35.38	AB VISA	P324150AA016215622	CAUTION! 120VAC [yellow]; INPUT AC 100-120V~3.0A 50-60 Hz 200-240V~2.0A; OUTPUT 24V 6.5A; REV.: 00	Available	L	-
S4	DE_2	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	MOU	3/5/18		3/11/18	43.87	AB VISA	P324200AM017320564	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A; Power Supply Status ...; Charge Controller Status LED: ...; Battery Type ...; W100 Load Ratings ...; CAUTION! 120 VAC [yellow]; WISPer W100 S/N : 2-180508 …	Sold	L	WP2
S5	DE_3	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	MOU	3/9/18		3/13/18	0.00		P324200AM017320562	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L1	WP3
S6	DE_4	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	6/12/19		6/14/19	49.13	USB VISA	P324200AM017440449	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L7	WP4
S7	DE_5	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	6/12/19		6/14/19	49.13	USB VISA	P324200AM017440448	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L10	WP5
S8	DE_6	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	5/26/20		5/29/20	48.43	USB VISA	P324200AM017440231	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L11	WP6
S9	DE_7	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	5/26/20		5/29/20	48.43	USB VISA	P324200AM017490309	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L3	WP7
S10	DE_8	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	5/26/20		5/29/20	48.43	USB VISA	P324200AM018100214	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L13	WP8
S11	DE_9	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	5/26/20		5/29/20	48.43	USB VISA	P324200AM018100219	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L14	WP9
S12	DE_10	Delta Electronics PMT-24V200W1AM	24V 200W Switching Power Supply	20180227 Datasheet_pmt-24v200w1am-774744.pdf	90-132 / 180-264	4.5		1	21.6-26.4	8.8	211.2					Hiccup	DKE	5/26/20		5/29/20	48.43	USB VISA	P324200AM018120213	INPUT 100-120V~4.5A 200-240V~2.5A 50-60Hz; OUTPUT 24V 8.8A	Sold	L15	WP10
S13	MW_1	Mean Well LRS-150F-48	48V 150W Switching Power Supply	20201220 LRS-150F Data Sheet.pdf	85-264	3.0		1	43.2~52.8	3.3	158.4					Hiccup	MOU	12/29/20	12/29/23	1/1/21	24.61	USB VISA	HC044O4794	INPUT 100-240V 3.0A 50/60Hz; OUTPUT 48V 3.3A	Available	L
S14	MW_2	Mean Well LRS-150F-48	48V 150W Switching Power Supply	20201220 LRS-150F Data Sheet.pdf	85-264	3.0		1	43.2~52.8	3.3	158.4					Hiccup	MOU	12/29/20	12/29/23	1/1/21	24.61	USB VISA	HC044O4809	INPUT 100-240V 3.0A 50/60Hz; OUTPUT 48V 3.3A	Available	L
S15	MW_3	Mean Well HRP-150N-48	48V 150W Switching Power Supply	20210105 HRP-150N Data Sheet.pdf	85-264	1.7		1	40.8-55.2	3.3	158.4					CC	MOU	1/5/21	1/5/26	1/7/21	62.53	USB VISA	EC082H7614	INPUT 100-240V 2.3A; 50/60Hz; OUTPUT 48V 3.3A	Sold	L5
S16	MW_4	Mean Well HRP-150N-48	48V 150W Switching Power Supply	20210105 HRP-150N Data Sheet.pdf	85-264	1.7		1	40.8-55.2	3.3	158.4					CC	MOU	1/5/21	1/5/26	1/7/21	62.53	USB VISA	EC082H7623	INPUT 100-240V 2.3A; 50/60Hz; OUTPUT 48V 3.3A	Sold	L5
S17	MW_5	Mean Well RSP-200-13.5	13.5V 200W Switching Power Supply	20220827 RSP-200 Series Data Sheet.pdf	88-264	2.5		1	12~15	14.9	201.15					Hiccup	DKE	8/27/22	8/27/25	8/31/22	65.56	AB VISA	SC216T4750	INPUT 100-240VAC 2.5A 50/60Hz; OUTPUT 13.5V 14.9A	Sold	L17	WP11
S18	MW_6	Mean Well RSP-200-13.5	13.5V 200W Switching Power Supply	20220827 RSP-200 Series Data Sheet.pdf	88-264	2.5		1	12~15	14.9	201.15					Hiccup	DKE	11/25/22	11/25/25	11/29/22	61.75	USB VISA	SC244K9448	INPUT 100-240VAC 2.5A 50/60Hz; OUTPUT 13.5V 14.9A	Sold	L18	WP12
S19	MW_7	Mean Well RSP-200-13.5	13.5V 200W Switching Power Supply	20220827 RSP-200 Series Data Sheet.pdf	88-264	2.5		1	12~15	14.9	201.15					Hiccup	DKE	11/25/22	11/25/25	11/29/22	61.75	USB VISA	SC244K9755	INPUT 100-240VAC 2.5A 50/60Hz; OUTPUT 13.5V 14.9A	Sold	L	WP13
S20	MW_8	Mean Well RSP-200-13.5	13.5V 200W Switching Power Supply	20220827 RSP-200 Series Data Sheet.pdf	88-264	2.5		1	12~15	14.9	201.15					Hiccup	SPSE	3/8/23	3/8/25	3/10/23	69.28	USB VISA	SC295F9903	INPUT 100-240VAC 2.5A 50/60Hz; OUTPUT 13.5V 14.9A	Assembly	L	WP14
S21	MW_9	Mean Well RSP-200-13.5	13.5V 200W Switching Power Supply	20220827 RSP-200 Series Data Sheet.pdf	88-264	2.5		1	12~15	14.9	201.15					Hiccup	SPSE	3/8/23	3/8/25	3/10/23	69.28	USB VISA	SC295F9904	INPUT 100-240VAC 2.5A 50/60Hz; OUTPUT 13.5V 14.9A	Assembly	L	WP15

## UPSs
UPSs		AC UPSs

History	Name	Description		Man'f Data	VA Rating	UPS Type	AC Input		DCV	AC Output			Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
		Man'f + Model No.	More Description				V	A		Wave Form	V	A					Status	Location	Batteries
A1	CP_1	CyberPower CP1500AVRLCD		20180504 CyberPower CP1500AVRLCD - see Warranties file for User's Manual.txt	1500	Bypass	90-140	15	24	Simulated Sine	120+-5%	12				<1/5/12			CPA9T2001352	Input: 125V~, 12A, 60Hz'; 'Model 1500VA: CP1500AVR / CP1500C'; 'Outlets: 125V~, 12A, 60HZ, 900W'; 'Total Output Current: 12A (Including Surge Outlets)	Discarded	-	-
A2	PS700_1	Liebert PS700MT-120	PowerSure Interactive 700	20180504 120v - 7002200_va.pdf	700	Bypass	90-148	10	24	Sine	120	5.8	NVD			<7/31/15	$6.80	Mileage		MODEL NO: PS700MT-120; INPUT: 120V~,50/60Hz, 7.0A; OUTPUT: 120V~,50/60Hz, 5.8A; VA/WATTS: 700VA/450W	Sold	L16	B27_28
A3	PS700_2	Liebert PS700MT-120	PowerSure Interactive 700	20180504 120v - 7002200_va.pdf	700	Bypass	90-148	10	24	Sine	120	5.8	NVD			<7/31/15	$6.80	Mileage	9930100162AD1C1	T1; 'Battery Test / Alarm Silence Button Press for >1/2 second'; 'Modified & Installed on B4-B7 5/17/19'; No Batteries 5/7/18; MODEL NO: PS700MT-120; INPUT: 120V~,50/60Hz, 7.0A; OUTPUT: 120V~,50/60Hz, 5.8A; VA/WATTS: 700VA/450W	Applied	L	B4-7
A4	PC_1	PowerCom KIN-1000AP	King Pro	20180505 User Manual - kingpro.pdf	1000	Bypass	90-150	15	24	Simulated Sine	120+-5%		NVD			<7/31/15	$6.80	Mileage	40085710701	T2; 'ON/OFF/TEST/SILENCE Button >2 seconds: ON/OFF <1 second: Self Test / Silence Alarm', 'Modified & Installed on B4-B7 5/16/19'; 'Batteries Replaced 5/5/18'; 'Batteries Replaced 8/6/15'; 'Input: AC 100-120V 50/60Hz 15A max.'; 'UPS Output: AC 120V 50/60Hz 600W / 1000VA'; 'Convenience Receptacle Output: AC 100-120V 50/60Hz 500VA'	Applied	L	B4-7
A5	GXT2_1	Liebert GXT2-2000RT120	UPStation GXT2U	20180505 liebert-gxt2u-120v-user-manual.pdf	2000	Online	60-140	20	48	Sine	100/110/115/120/127+-3%	20	NVD			<7/31/15	$6.80	Mileage		ON/OFF buttons > 1/2 sec; To Bypass: Press OFF once; To turn OFF: Bypass first, then press OFF twice; UPS ON LED means "Inverter On"; Batteries are charged whenever the unit has input AC, even if the UPS is not ON	Available	L	-
A6	GXT2_2	Liebert GXT2-1500RT120	UPStation GXT2U	20180505 liebert-gxt2u-120v-user-manual.pdf	1500	Online	60-140	15	48	Sine	100/110/115/120/127+-3%	15	NVD			<7/31/15	$6.80	Mileage		ON/OFF buttons > 1/2 sec; To Bypass: Press OFF once; To turn OFF: Bypass first, then press OFF twice; UPS ON LED means "Inverter On"; Batteries are charged whenever the unit has input AC, even if the UPS is not ON	Available	L	-
A7	TL6_1_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9532ALCPS584100099	8/21/15 #03 [cover, inside, front, rear]; 4 [front, rear]; Circuit Court of Jackson County, Asset, 100-02051	Available	L	-
A8	TL6_1_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9533ALCAC579400002	8/21/15 #01 [cover, inside, front, rear]; 4 [front, rear, AC input cable]	Available	L	-
A9	TL6_1_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9512ALCBP546300013	8/21/15 #02 [inside, rear, front]; 4 [front, rear]; Japanese, 03/05/20 [batteries]	Available	L	-
A10	TL6_2_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9509ALCPS482100090	8/21/15 #05 [rear, inside, front, cover]; 7 [front, rear]; Circuit Court of Jackson County, Asset, 100-02024 [front]; PCR 6/5/06 [rear]	Available	L	-
A11	TL6_2_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9508ALCAC514000036	8/21/15 #06 [inside, front, rear, cover]; 7 [front, rear, AC input cable]; PCR 6/5/06 [rear]	Available	L	-
A12	TL6_2_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9509ALCBP546300114	8/21/15 #04 [rear, front, inside on a battery]; 7 [front, rear]; PCR 6/5/06 [rear]	Available	L	-
A13	TL6_3_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9509ALCPS482100083	8/21/15 #08 [cover, inside, rear, front]; 6 [front, rear]; PCR 6/5/06 [rear]; Circuit Court of Jackson County, Asset, 100-02023	Available	L	-
A14	TL6_3_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9504ALCAC514000084	8/21/15 #09 [inside, front, rear, cover]; 6 [front, rear, AC input cable]; PCR 6/5/06 [rear]	Available	L	-
A15	TL6_3_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9509ALCBP546300034	8/21/15 #07 [rear, front, inside on a battery]; 6 [front, rear]; PCR 6/5/06 [rear]	Available	L	-
A16	TL6_4_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9508ALCPS482100050	8/21/15 #11 [inside, front, rear, cover]; 12 [front, rear]; PCR 6/5/06 [rear]; Circuit Court of Jackson County, Asset, 100-02055	Available	L	-
A17	TL6_4_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9508ALCAC514000023	8/21/15 #12 [rear, front, inside, cover]; 12 [front, rear, AC input cable]; PCR 6/5/06 [rear]	Available	L	-
A18	TL6_4_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9506ALCBP546300006	8/21/15 #10 [inside on a battery, rear, front]; 12 [front, rear]; PCR 6/5/06 [rear]	Available	L	-
A19	TL6_5_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9902DLCPS737100318	8/21/15 #14 [cover, inside, rear]; 3 [front]; Circuit Court of Jackson County, Asset, 100-02039; PO16598 [rear]; PC NATION 6/16/10 [rear]	Available	L	-
A20	TL6_5_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9902ALCAC579400012	8/21/15 #15 [cover, rear, front, inside]; 3 [front, AC input cable]	Available	L	-
A21	TL6_5_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9901BY0BP606800019	8/21/15 #13 [rear, front, inside on a battery]; 3 [front, AC input cable]	! DC Cable	L	-
A22	TL6_6_P	TrippLite SU6000RT3UPM	3U Power Module (controls)	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf	6000	Online					JC			8/15/15	$1.81	Mileage	9902DLCPS737100302	8/21/15 #17 [cover, inside, front, rear]; 8 [front, rear]; Circuit Court of Jackson County, Asset, 100-02034 [Isopropyl partially destroyed this label]; PO16598 [rear]; PC NATION [rear]	!Connector	L	-
A23	TL6_6_T	TrippLite SU6000XFMRRT3U	3U Transformer Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf			156-276	22.6		Sine	100/120/200/208/240V	30	JC			8/15/15	$1.81	Mileage	9902ALCAC579400046	8/21/15 #18 [cover, front, rear, inside]; 8 [front, AC input cable]	!L6-30	L	-
A24	TL6_6_B	TrippLite BP240V7RT3U	3U Battery Module	20160128 SmartOnline Single-Phase 5kVA-6kVA-10kVA 932407 (GOOD).pdf					240				JC			8/15/15	$1.81	Mileage	9915BY0BP606800063	8/21/15 #16 [rear, inside on a battery, front]; 8 [front, rear]	! DC Cable	L	-
A25	TL3_1	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	JC			8/15/15	$1.81	Mileage	9518AD0PS599700068	8/21/15 #19 [front]; 1 [front]; Circuit Court of Jackson County, Asset, 100-02040; PCR 6/1/06 [rear]; Japanese 12/23/2005 [battery pack, #02 & #05 battery]; JC1 #19 Battery #01-06 [individual batteries]; BATTERY TYPE AND QUANTITY: LEAD-ACID 12V,6PCS, NOMINAL VOLTAGE /CAPACITY OF BATTERY STRING: 72VDC/9Ah, CM-2 [battery pack]	!L5-30 !FP	L	-
A26	TL3_2	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	JC			8/15/15	$1.81	Mileage	9518AD0PS599700069	New batteries 12/12/17, Estimated runtime, Load 50% - 30 Minutes, Load 25% - 74 Minutes, (100%=2400 Watts); To turn output ON or OFF press and hold until beep; {labels which might have been covered or removed before delivery to RHS: 8/21/15 #20; 2 [front]; Circuit Court of Jackson County, Asset 100-02041; PCR 6/1/06 [rear]}	Sold	L5	B62-B67
A27	TL3_3	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	JC			8/15/15	$1.81	Mileage	9519AD0PS599700082	New batteries 12/12/17, Estimated runtime, Load 50% - 30 Minutes, Load 25% - 74 Minutes, (100%=2400 Watts); To turn output ON or OFF press and hold until beep; {labels which might have been covered or removed before delivery to RHS: 8/21/15 #21; 9 [front, rear]; Circuit Court of Jackson Count, Asset 100-02035; PCR 6/1/06 [rear]}	Sold	L5	B62-B67
A28	TL3_4	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	JC			8/15/15	$1.81	Mileage	9519AD0PS599700033	8/21/15 #22; 10 [front, rear]; Circuit Court of Jackson County, Asset 100-02036; PCR 6/1/06 [rear]	Available	L	-
A29	TL3_5	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	JC			8/15/15	$1.81	Mileage	9917ELCPS719400142	8/21/15 #23; ATTENTION! … [front, yellow]; Circuit Court of Jackson County, Asset 100-02084	Available	L	-
A30	TL3_6	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	NVD			~9/1/15	$17.01	Mileage	9519AD0PS599700085	NVD 2015 #24; UPS 4 [front, cord plug]; SVB-0552 [top]; 'US: DTLOT00BDRJ11-45' [top]; PCR 6/19/06 [rear]; Property of Jackson County, MO 014650 [rear]	Dead ! MOV	L	-
A31	TL3_7	TrippLite SU3000RTXL3U	3U (6) 12v Batteries	20161031 SU3000RTXL3U Data Sheet (1x battery).pdf	3000	Online	65-150	24	72	Sine	110/120	15	NVD			~9/1/15	$17.01	Mileage	9519AD0PS599700084	NVD 2015 #25; UPS 5 [front, cord plug]; SVB-0552 [top]; 'US: DTLOT00BDRJ11-45' [top]; PCR 6/19/06 [rear]; Property of Jackson County, MO 014649 [rear]	! 3/4 LED	L	-
A32	APC_1	APC BR500	Back-UPS RS 500	20190711 Manual ASTE-6Z7V7V_R0_EN.pdf	500	Bypass	78-150	10	12	Stepped Sine	120	10	KJ			7/9/19	$0.00		BB0537029474	Input: 120V~ 10A, 50/60Hz; UPS Outlets 500VA:120V~ 4.2A, 50/60Hz 300W; Surge Protected Outlets 120V~, 50/60Hz; Total Output Current: 10A	Available	L	-

## USBs
USBs		USB Devices (for Wattmons)

History	Name	Description	Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Serial Number	IMEI	Other Stickers and Man'f Labels	Current
		Man'f + Model No. + (Type)					Status	Location	Wattmon
U1	USB_1	Huawei E303s-65 (3G Modem)		eBay	7/11/15	8/11/15	7/15/15	$18.99	PSC		860874011326094	USB #1	Available	L
U2	USB_2	Huawei E303F (3G Modem)		Wattmon	9/11/15	9/11/16	9/14/15	$26.67	C1 MC & DVS VISA	B9CBY14C11007517	866168022585820	USB #2	Available	L	-
U3	USB_3	Huawei E303F (3G Modem)		Wattmon	9/11/15	9/11/16	9/14/15	$26.67	C1 MC & DVS VISA	B9CBY14B05002140	866168020409346	USB #3	Available	L

## Wattmons
Wattmons		Wattmons

History	Name	Description		Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Serial Number	Other Stickers and Man'f Labels	Current
		MAC Address	Model No.					Status	Location	IP Address	Module(s)
W1	Wattmon_1	D8-80-39-0C-B9-6F	WMPRO60	6/18/15	6/18/16	6/24/15	$232.04	C1 MC	[Unknown, unit was shipped back to India before this spreadsheet was created]		Returned	-	-	-
W2	Wattmon_2	D8-80-39-0C-BB-61	WMPRO60	7/13/15	7/13/16	7/15/15	$232.04	C1 MC	2015060028	#2, Ordered 7/13/15, Rec'd 7/15/15, 1 year warranty [2];12.133.21.146; 9/18/15 Vin/A1 and Current calibrated w/BK Precision & C252 #2. Two loops, each sensor, 0-12.5A	Returned	-	-	-
W3	Wattmon_3	D8-80-39-00-9D-1A	WMPRO60	7/27/15	6/18/16	7/31/15	$22.45	C1 MC	2015060076	#3, Warranty Replacement for Wattmon #1, Rec'd 7/31/15, 1 year warranty expires 6/18/16; 9/19/15 Vin/A1 and Current calibrated w/BK Precision & C252 #2. Two loops, each sensor, 0-12.5A; 12.133.21.141	Returned	-	-	-
W4	Wattmon_4	00-1E-C0-E3-0E-82	WMPRO60	9/11/15	9/11/16	9/14/15	$233.73	C1 MC & DVS VISA	201508082	Wattmon #4, Ordered 9/11/15, Rec'd 9/14/15, 1 year warranty expires 9/11/16; Ordered 9/11/15, Rec'd 9/14/15	Returned	-
W5	Wattmon_5	00-1E-C0-E3-64-B0	WMPRO60	9/11/15	9/11/16	9/14/15	$233.73	C1 MC & DVS VISA	201508064	Wattmon #5, Ordered 9/11/15, Rec'd 9/14/15, 1 year warranty expires 9/11/16; Ordered 9/11/15, Rec'd 9/14/15	Returned	-
W6	Wattmon_6	D8-80-39-0C-A9-E2	WMPRO60	4/27/16	7/31/16	5/5/16	$13.41	CA VISA		Wattmon #6, RMA replacement for #2, Rec'd 5/5/16, Warranty expires 7/31/16; Calibrated 6/1/16 With C252 #1	Available	L	12.133.21.146	-
W7	Wattmon_7	D8-80-39-0C-A0-34	WMPRO60	4/27/16	6/18/16	5/5/16	$13.41	CA VISA	201601038	Wattmon #7, RMA replacement for #3 & #1, Rec'd 5/5/16, 1 year warranty expires 6/18/16; A1/Vin Calibrated for 12v batteries ->NVRAM 6/11/16	Available	L	12.133.21.141	M7
W8	Wattmon_8	D8-80-39-0C-A9-A7	WMPRO60	4/27/16	9/11/16	5/5/16	$13.41	CA VISA	201601019	Wattmon #8, RMA replacement for #4, Rec'd 5/5/16, 1 year warranty expires 9/11/16; A1/Vin Calibrated for 12v batteries -->NVRAM 6/6/16	Available	L	90.0.0.108	M1
W9	Wattmon_9	D8-80-39-0C-9F-8D	WMPRO60	4/27/16	9/11/16	5/5/16	$13.41	CA VISA	201601051	Wattmon #9, RMA replacement for #5, Rec'd 5/5/16, 1 year warranty expires 9/11/16	Available	L	90.0.0.109	M3
W10	Wattmon_10	54-10-EC-8C-1C-D0	WMMEGA	2/19/18	~4/12/19	4/12/18	$81.50	Website Work	MG201803041	Rev. 1.0; Wattmon_10, Received 4/12/18	Available	L	DHCP 90.0.0.110	M9 M1

## WebRelays
WebRelays		IP Addressable Relays

History	Name	Description		Man'f Data	Source / Supplier	Order Date	Warranty Expires	Rec’d Date	Cost	Paid With	Stickers	Serial Number	Current
		Man'f + Model No.	More Description					Status	Location	IP Address	Wattmon
R1	R_1	Xytronix Research & Design X-WR-1R12-1I5-I	1 Relay 12A/240VAC/30VDC, 1 Digital Input 4-12VDC, 9-28VDC Supply	20160222 webrelay_users_manual.pdf	ControlByWeb.com	2/23/16	2/23/17	2/26/16	$118.26	C1 MC	Unit #1 of 2, Rec'd 2/26/16, C1; 12.133.21.143	00-0C-C8-03-6B-A5	Available	L	192.168.1.50	-
R2	R_2	Xytronix Research & Design X-WR-1R12-1I5-I	1 Relay 12A/240VAC/30VDC, 1 Digital Input 4-12VDC, 9-28VDC Supply	20160222 webrelay_users_manual.pdf	ControlByWeb.com	2/23/16	2/23/17	2/26/16	$118.26	C1 MC	Unit #2 of 2, Rec'd 2/26/16, C1; 12.133.21.157	00-0C-C8-03-6B-A6	Available	L	192.168.1.50

## WISPers
WISPers			WISPer DC UPSs Built/Sold					Current

History	Parts / BoM	Ordering & Inventory	Assembly	Model_ / Number	WISPer Generation	More Description	Order Date	Shipped / Installed Date	Warranty Expires	Serial Number	Contract Total	Total Cost	Total Hours	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
	Parts
WP1			WP1A	W50	1st Generation Prototype	WISPOWER#1; Dual 75w PS with Schottky Diode; 100AH SLA, Service	7/12/17	9/6/17	9/6/18		$1,140	$464	232	Sold	L18	B26
				WP1:	$1,140	$464	232				Net $/Hour:		$3
WP2			WP2A	W100_1	2nd Generation Prototype	Delta PS 24v/200w, Genasun, Fan, (2) T-105 Batteries	2/26/18	5/8/18	5/8/19	2-180508	$780	$561	448	Sold	L	-
WP3			WP3A	W100_2	1st Production Run	Delta PS 24v/200w, Genasun, Fan, 27TMX, Service Calls	5/7/18	8/13/18	8/13/19	3-180812	$688	$140	97	Sold	L1	B54
WP4			WP4A	W100_3	2nd Production Run	Delta PS 24v/200w, Genasun, Fan, 27TMX	6/4/19	7/9/19	7/9/20	4-190622	$797	$488	122	Sold	L7	B1
WP5			WP5A	W100_4	2nd Production Run	Delta PS 24v/200w, Genasun, Fan, 27TMX, Electrical Work (Outlets)	7/10/19	5/22/20	5/22/21	5-190622	$1,065	$547	287	Sold	L10	B56
				WP2-5:	$3,330	$1,735	955				Net $/Hour:		$2
WP6			WP6-10A	W100_5	3rd Production Run	Delta PS 24v/200w, Genasun, Fan	5/8/20	6/16/20	6/16/21	6-200612	$690	$392	24	Sold	L11	B57
WP7				W100_6	3rd Production Run	Delta PS 24v/200w, Genasun, Fan	5/8/20	6/16/20	6/16/21	7-200612	$680	$366	27	Sold	L3	B9-10
WP8				W100_7	3rd Production Run	Delta PS 24v/200w, Genasun, Fan	5/8/20	6/16/20	6/16/21	8-200612	$680	$366	26	Sold	L13	B59
WP9				W100_8	3rd Production Run	Delta PS 24v/200w, Genasun, Fan	6/8/20	7/6/20	7/6/21	9-200612	$680	$396	36	Sold	L14	B60
WP10				W100_9	3rd Production Run	Delta PS 24v/200w, Genasun, Fan	6/8/20	8/14/20	8/14/21	10-200612	$1,601	$731	76	Sold	L15	B61
				WP6-10:	$4,331	$2,252	189				Net $/Hour:		$11
WP11	WP11P		WP11A	W150_1	4th Generation Prototype	Dual Supply, Diode Isolation at Traco Input; Modular Assembly on Backplate; 52.8v Output	6/10/22	10/21/22	10/21/23	11-221007	$2,413	$542	48	Sold	L17	B58	BC9	S17	V11
				WP11:	$2,413	$542	48	R&D Hours:		267	Net $/Hour:		$6
WP12	WP12-13P		WP12-13A	W150_2	1st Production Run	As Prototype with Minor Changes including 1 Pole PCS	7/19/22	12/28/22	12/28/23	12-221214		$450	44	Sold	L18	B70-71	BC10	S18	V12
WP13				W150_3	1st Production Run	As Prototype with Minor Changes including 1 Pole PCS	10/13/22	1/30/23	1/30/24	13-230130		$450	44	Sold	L		BC11	S19	V13
				WP12-13:	$2,962	$901	88	R&D Hours:		239	Net $/Hour:		$6
WP14	WP14-15P	WP14-15O	WP14-15A	W150_4	2nd Production Run	Major Changes including elimination of PCS and addition of Meter Assembly				14-23????		#REF!	18	R&D	L		BC12	S20	V14	Z21
WP15				W150_5	2nd Production Run	Major Changes including elimination of PCS and addition of Meter Assembly				15-23????		#REF!	18	R&D	L		BC13	S21	V15	Z22
				WP14-15:		#REF!	35	R&D Hours:			Net $/Hour:		#REF!
WP16				W150_6	3rd Production Run	To Be Determined				16-23????				R&D	L				V16
WP17				W150_7	3rd Production Run	To Be Determined				17-23????				R&D
WP18				W150_8	3rd Production Run	To Be Determined				18-23????				R&D

## A1
UPSs: A1	A					CP_1: CyberPower CP1500AVRLCD

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Discarded	-	-
?	?	?					Ordered and received (unknown dates, but it had to be before 1/5/12 when it was attached to the NAS)		Available	L	From Man'f	?MM?
?	?	?					Installed in rear room to provide backup power to the network (unknown date)		Applied			?MM?
2012	Jan	12					Attached USB connection to QNAP NAS (as per NAS Setup Notes)					20120112
2018	May	3	Th					Tested: disconnected input power for about 10mins (to watch NAS shutdown). Battery capacity is a whole lot less than it was in early 2012 when it was first setup with the NAS (see NAS Setup Notes). With the NAS on, it probably won't keep the network going for more than about 15 mins. However, once the NAS shuts down (~7 mins) it could probably keep going to 15-30 mins total. Useable, but batteries are close to needing replacement. (I remember when it was new that it would predict that it could keep the NAS and the network going for over an hour.)					20180503
		4	Fr					Created this history sheet. Searched for further records, none found in emails, but found the User Manual in the Warranties/Manuals/Bills of Sale paper file. From memory I don't think the batteries have ever been replaced (now more than 6 years old). The only reason these batteries are still useable is because the UPS is being operated at less than 10% of load capacity.	IMG WMBS				20180504
		12	Sa		08:24		09:31	Power outage in Wood Heights area including Rayville, 1 hr 7 mins; CP_1 is now plugged into the T1 UPS circuit (GXT2_2) because it was very close to death almost immediately (although NAS did shut down OK after ~7 mins)	A6			Weak Batteries	20180512
	Aug	31	Fr	~	01:30			I woke to find CP_1 inoperative, flashing front panel power light; Turned off, and power to network bypassed		OFF			20180831
				Removed from high shelf in rear room; Removed front panel and pulled batteries (2); B.B. Battery HR1234W "12V,34WPC/15min./1.30VPC/25⁰C" (whatever that means), shrink wrapped pack with battery leads in between (see photos); Total pack 3.5v (1.75v average for each of (2) 12v batteries); They aren't swollen and bulging, these are good quality batteries, more than 6 years service life, will try to buy	IMG	Needs Batteries	L0	Salvage	20180831
	Sep	1	Sa					B&B Brand is hard to find, and >$30 each for 7AH; Will try to find better quality than Sigmas Tek but B&B may not be easy to find					20180901
2019	Mar	29	Fr					Drilled hole in front panel		Assembly			20190329
		30	Sa					Attached to 20150808_1/2, 20150808_2/2, 20150910_1/2, 20150910_2/2; Very slow charger for this size battery bank (probably only ~1 Amp); Charges whenever plugged in even if output is off; Battery Capacity ~50% and Estimated Run Time ~30 Minutes are in error (150 W load should be ~36 hours); I doubt if these calculations will be accurate as they are assuming we have a 7 AH battery, but we've got 225 AH; Nevertheless, it should keep running until battery voltage under load drops below some internally decided point, probably about 10.6 vdc	IMG	Testing		B4-B7	20190330
		31	Su					"Fully charged" float is 27.3 vdc (Fluke, 13.65x2); Installed on high shelf in rear room; All circuits I need right now is about 600w or 66% of total load capacity; Tested for several hours @ ~50% load capacity (300+w) and some 'burn smell' but this could be dust burning off the heat sinks on the inverter; Original Man'f B&B Brand batteries --> Salvage		Applied	L		20190331
2019	Apr	22	Mo	~	09:15	~	11:35	Accidently plugged compressor into T1 circuit, which ran for about 30 seconds before UPS shut itself off due to overload (entire network went down except for T400s and T450s) …; Came back from Richmond and discovered network power was down and CP_1 was beeping; Reset					20190422
		27	Sa		14:38		15:55	Power outage including entire area (Wood Heights, Lawson, Excelsior Springs); Reduced load to about 250 watts and left for town; No problems; Probably used about 12.5 AH (~5% of battery capacity) during 1-1/4 hour outage					20190427
		28	Su	~	14:20	~	14:35	During Absorption/Equalize on BK_1 voltage went somewhere above 30.00 vdc and UPS shut itself off, I suspect due to battery overvoltage protection …; I started it back up (without BK_1); Revised Absorption/Equalization route for 30.00vdc maximum	S2				20190428
	May	15	We		08:38		09:28	Power outage including Rayville, Wood Heights …; Power restored after 50 minutes; Load during this time was about 385 Watts/~16 Amps (T400s being used during entire time); Therefore batteries discharged to ~94 %SoC					20190515
				Once again, some burning smell from CyberPower (I've got it on my TODO list to disassemble it and check for hot spots)					20190515
		16	Th					DE_1 installed in parallel, adjusted to 27.0vdc to speed return to float after a power failure	S3				20190516
				Bypassed T1/T2 and removed UPS from shelf in rear room; Case is melted/deformed on the bottom; Disassembly more difficult than it s/b because the plastic is deformed; The hottest area appears to be around the transformer, which has melted its way down into the bottom of the case; It doesn't appear to be a bad high current connection as I can see where the two battery wires attach in and there is no sign of heat there; Possibly bad 12vdc fan (but this is very small, and it spins freely); Possibly bad capacitor (likely cause); Also possibly a bad crimp connection just inside the transformer (the positive battery connection goes straight into the transformer near the small fan); And to top it all off, if this thing self-destructed when it wasn't being abused then I can't rely on it even if I can find the problem and fix it.					20190516
				Decision made to scrap, part out and dispose of CP_1 (A1)	A4	Discarded	-	-	20190516

## A2
UPSs: A2	A					PS700_1: Liebert PS700MT-120

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L16	B27_28
2015	?	?					[A2-6] Acquired from NVD (Nathan Van Duyn) sometime before 7/31/15 (probably no more than a month or so); [A2] 'L_1 from NVD'		Available	L	Dead	2015MM?
	Jul	31					[A2-6] Replacement batteries ordered from BatterySharks.com	EML		L0		20150731
	Aug	5					[A2-6] Batteries received					20150805
		6					Batteries installed and UPS placed in service in the garage (light over bench)		Applied	L	B12_13	20150806
2017	Oct ?	?					The batteries went dead (they self-destructed, melted, deformed); It is sometimes very hot in the garage, so I'm not surprised, because the SigmasTek datasheet says the long term float life is ~2-4 years at 86⁰F / Batteries added to pile in W side storage for recycling.		Available		-	2017MM?
	Aug	31					Meeting with Mark and Keith at TurboNet Lexington office (see yellow sheet notes): / They wanted an installed quote on a UPS system for the fiber setup in the basement there, and at first we were talking about installing one of the JC TrippLite 3kVA units with 12 new batteries / I shot photos of the equipment and looked at maximum power ratings (4A and 2A, or 720w) and we talked about it being more like 350w	TA1 IMG				20170831
	Sep	1					I sent Mark and Keith a quote for the Tripp-Lite with 12 new batteries 20170901 Fiber UPS Quote.pdf / This didn't go anywhere for quite a while, and in the meanwhile I got to thinking that it would be wiser to install a smaller inverter in order to maximize battery runtime, and the Tripp-Lite requires a 30A supply circuit which they don't have	DBT TA1				20170901
	Oct	24					I sent Mark and Keith another installed quote for $850: "UPS for fiber setup in Lexington - Longer runtime option" 20171024 Fiber UPS Quote 2.pdf / This quote for Liebert PS700MT-120 and (2) 100AH SLA batteries; "Bench testing suggests that with a 100 Watt load the system should run for 8 to 16 hours."					20171024
	Nov	2					Rec'd advance Payment of $425 less $12.63 Paypal fee (net $412.37)	EML TA1				20171102
		6					Batteries ordered from BatterySharks.com (as needed for TurboNet fiber setup in Lexington office, 2x100AH)			L0		20171106
		8					Batteries received and installed (UPS modified for external battery bank); Testing notes (white sheet) / 20171109 Fiber UPS Final Invoice.pdf (sent via email, "The system is ready to go …")	TA1 DBT EML WS	Testing		B27_28	20171108
		9					UPS and batteries installed on fiber setup in TurboNet Lexington office basement (final payment of $437.63 rec'd from TurboNet)	TA1	Sold	L4		20171109
2018	May	8					I was in Lexington (to install WISPer #2 W100 at WWT): Fiber setup is running somewhere between 113-225 watts (2 bars out of 4 is 450/2 = ~225 watts); I told Keith it would probably only go about 8 hours at that load					20180508
2020	May	8	Fr					Onsite at TL (to deliver WP5/B56 to LWT and discuss other spinoffs): Inspected; 27.45v Fluke; No heat, no bulging, no cracks; Mark and Keith reported a 30 min outage a few weeks ago and no problems	L4				20200508
	Aug	11	Tu	~	12:05	~	13:45	While with Keith onsite at Swafford tower he related that he had just gotten the fiber setup with UPS moved to the New Building (A2/B27_28 L4->L16)	L4		L16	B27_28	20200811
2021	Mar	14	Su	~	12:20	~	13:30	Onsite at TLNB for the Backup Power Supply Maintenance Program; See L16 for details	DBT TM21S SMS				20210314
	Aug	13					Lexington office discussion with Keith (MikroTik) / [Note added 12/27/21 (during .ods General Review): I remember checking on the server room and found that they had installed an air conditioner to lower the ambient / It was about 75⁰F (Keith had a thermostat reading this) and I recommended he set it to 68⁰F (which I saw him do)]	TM21F		L16		20210813
	Sep	22					Lexington Meeting with Keith and Mark (MikroTik) / [Note added 12/27/21 (during .ods General Review): I remember checking on the server room and it was nice and cool (I had asked Keith to set the A/C thermostat at 68⁰F)]					20210922
2022	Mar	9	We	~	14:06			SMS from Mark "I think we need this at the Lexington tower" and photo of Liebert UPS and batteries on fiber backbone / Images\DC\20220307;09DC MO, Lexington, From Mark Webb, TurboNet; LWT Power Outage, TLNB Server Room [O]\20220309 1503 From Mark Webb, MMS, TLNB Server Room IMG_0039.heic and .jpeg	TM22 SMS IMG		L16		20220309
	Jul	5	Tu					Lexington Power Failure: While travelling in CO I rec'd MMS/SMS from Keith; "Should this be all the way up at the shop" / Photo of Liebert at TLNB: G:\Images\DC\20220705DC MO, Lexington, From Keith Jones, TurboNet; Liebert at TLNB [O]\20220705 1113 IMG_3488.jpeg / Call to Keith: Power loss for several hours in Lexington; He had to reset the fiber stuff; I explained to him how the 4 bar indicator on the Liebert works (photo shows load is 1/4 bars, as it was 3/14/21, ~56w)			L16		20220705
		22	Fr					Lexington Power Failure: Keith notified me of this when he was here at the shop to pickup the power cable for CFS / When he left the Lexington shop at about 11:00 the power had been off for about 30m and the Liebert was showing 4/4 bars battery remaining; I didn't hear about when the power was restored	T48-4 TM22				20220722

## A3
UPSs: A3	A					PS700_2: Liebert PS700MT-120

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	B4-7
2015	?	?					A2-6; A3 is 'L_2 from NVD'		Available	L	Dead	2015MM?
	Jul	31					A2-6	EML		L0		20150731
	Aug	5					20150805
		6					Batteries installed, plugged in but not placed in service			L	B16_17	20150806
				Installed UPS at Mark Hall residence on SERVANT2 (date of installation unknown, but probably within a month after I installed the batteries)		Applied	Hall Bsmt		20150806
2017	Jul					Mark died, and they shut down SERVANT2, and may have also unplugged the UPS		Unknown			20170706
2018	May	7	Mo					I visited Sheila and Isaac and it does not look like it had been plugged in (dead when pressing front power button); Returned unit to shop; Batteries are deformed, melted, 1.26v total for both batteries in series (Salvage) / Tested UPS with BK Precision 9110 (28v, 5.1amps) and UPS is operational, I did not think to test inverter but probably OK as unit passes self-test, charger 27.6v (13.8v x 2); Stickers applied; Photos / Placed under bench (waiting application or available funds for batteries)	IMG	No Batteries	L	-	20180507
2019	May	17	Fr					Drilled hole in front panel; Extended battery wires; Attached to (4) T-105s in series (20150808_1/2, 20150808_2/2, 20150910_1/2, 20150910_2/2); Float is 27.5vdc		Assembly	L0	B4-B7	20190517
				~	05:00			[A3-4] In parallel with PC_1 and DE_1	S3	Applied	L		20190517
				Loads rearranged: powering Network (switches, NAS, etc.), T1 circuit (S Bench) and Fluke (when used to monitor B4-B7 voltage)					20190517
				Stickers applied: T1; 'Battery Test / Alarm Silence Button Press for >1/2 second'; 'Modified & Installed on B4-B7 5/17/19'					20190517
				06:10		06:40	[A3-4] Simulated power failure test with near maximum loads on Liebert and PowerCom (T400s/T450s, monitors, emergency lights, Trace/SAPS in Subaru, anything I could easily set up, kept it going) / Tried to turn on JAK2, but PowerCom cannot handle JAK2 starting up with everything else on / Turned off some unessential stuff to try starting JAK2 again, but PowerCom cannot handle JAK2 startup / (it probably would handle JAK2 except for the inrush power, which is greater than the ~155 watts I see when it is up and running) / ... at 30 minutes 24.5vdc, Liebert says ~75% battery remains (3 bars out of 4, but it said this a few minutes after starting the test), very slight "hot" smell but probably just dust/dirt on the heat sinks / Estimated <5% of battery capacity used; Power restored					20190517
		20	Mo					[A3-4] Corrected/improved inventory sticker applied (over the top of the old one)					20190520
		23					[A3-4] Network UPSs on high shelf in rear room: PowerCom, Liebert, Delta, Trojan T-105s	IMG				20190523
	Jun	29	Sa	~	08:15	~	08:45	[A3-4] T1 Bypassed; Network loads moved to T2 (PowerCom); T2 Bypassed; Liebert removed; T2 Not Bypassed; Liebert installed in W100 Series Test setup (temporary, for a few days)	WRD	W100 Test	L0	B1 & B54	20190629
				Note that no load idle power on the Liebert is 39-45 Watts, it has a fan, and that's what it takes with no load on it at all					20190629
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG				20190708
		9	Tu	~	12:45			W100 Series Test setup disassembled	WRD	Available	L	-	20190709
		10	We	~	07:30	~	08:10	[A3-4] Liebert moved back to rear room for Network and N Desk; T2 bypass; A3 connected to batteries; T1 and T2 bypass NOT; Network and N Desk brought down and moved to T1; T450s (R)		Applied		B4-B7	20190710
	Oct	5					Equalization with BK @ 30 v caused Liebert to beep and display flashing LED (error), but it kept functioning / After equalization was completed I had to power down the Liebert (network down briefly) and restart, after which error was cleared	S2				20191005
2019	Dec	19		~	09:00	~	11:45	[A3-4] Power failure, 758 customers					20191219
2020	Mar	10		~	22:12	~	02:14	[A3-4] Power failure, 750+ customers, 4 hours (I worked at T400s for the last ~3 hours)					20200310
				20200310
2021	Jan	12	Tu					[A3-4] Shelf above door to network room rearranged (see B4-B7 for details); Photos of PC_1, PS700_2, BK_1 and B4-B7 / Photos also include TurboNet/RHS project with B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	IMG			B4-B7	20210112
		14	We					[A3-4] Photos: Network UPSs AC Power Distribution T1 and T2 (Rear Room); This photo and the photos from Tu1/12 and Mo1/8 (RHS project) were posted on my Facebook timeline					20210114
	Dec	25	Sa	~	08:17	~	10:38	[A3-4] T2 (A4) and T1 (A3) bypassed and off for service on B4-B7; Remained attached to batteries during BK Equalization (set 30.50v/3.278a), A3 and/or A4 loads BK slightly and Liebert cooling fan is on / A4 and A3 OFF still loads BK but not as much ...; A3 and A4 ON; Bypass removed	S2			B4-B7	20211225
2022	Aug	1	Mo					[A3-4] T2 (A4) and T1 (A3) bypassed and off for service on B4-B7; Remained attached to batteries during BK Equalization (set 29.2v/3.424a) ...	S2		L0		20220801
		2	Tu	~	08:15	~	08:54	[A3-4] Plugged in Liebert (A3) and PowerCom (A4) to recover charge lost in aborted ITECH Battery Test ... unplugged (still bypassed and off)					20220802
				~	08:54	~	15:26	[A3-4] ITECH Battery Test (11.25a, Stop 20v) ...; 23,525s (6.5h) 73.511 AH (32.7% of new capacity) / CONCLUSION: B4-B7 are still very useable for this application, the C/20 capacity runtime of 6.5h is plenty for what I need them for					20220802
				~	19:25	~	19:35	[A3-4] UPSs ON; Liebert (A3) shows battery status 2/4 bars; UPSs plugged in (charging, both UPSs ~2.7aE); At this low charge rate it will take at least 27h to recover; Bypass removed			L		20220802
2023	May	18	Th					[A3-4] After discovering B4-7 very dry with exposed plates I installed a Window A/C which has reduced room temperature as low as it can go (room air ~20⁰C); Batteries are still above 27⁰C (batteries are heating themselves) / I have an idea that should work to reduced the battery float voltage: Dual diodes back to back, with suppression contactor to extend run time & max power capacity / I call this a Float Reducer and it should drop the charging voltage to <27v but allow bidirectional operation (with or without contactor) / Soon after this day I started bypassing and unplugging both UPSs at night, and I also don't run the Liebert at all (T1) as it has a higher Float than the PowerCom (T2) which is charging only during the work day	WS SSC LIB			B4-7	20230518

## A4
UPSs: A4	A					PC_1: PowerCom KIN-1000AP

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	B4-7
2015	?	?					A2-6; A4 is 'PC_1 from NVD'		Available	L	Dead	2015MM?
	Jul	31					A2-6	EML		L0		20150731
	Aug	5					20150805
		6					Batteries installed and placed in service in front room (reading lights)			L	B14_15	20150806
2018	May	1		~	18:00	~	18:30	UPS dead …; Very warm		Inop	L0		20180501
		3					Opened UPS and found batteries to be 'toast', one of them deformed. UPS OK. Batteries were in service 2 years 9 months / I'm not surprised, because the SigmasTek datasheet says the long term float life is ~2-4 years at 86⁰F; Batteries added to pile in W side storage for recycling	IMG	Available		Salvage	20180503
				Attached #01 and #02 batteries from JC12 #10 (A18, TL6_4_B); batteries do not pass self-test; Will charge for >16 hrs and test again …	A18			(2) from A18	20180503
		4		~	07:00			Batteries have been charged for ~16 hrs, now 27.4v (13.7v each); Self-test OK, UPS operational					20180504
		5					Reassembled and installed in front room on (3) compact flourescents (50-75w total) / When AC input is removed the UPS shuts down immediately, and it will not pass self-test with only one of the three compact flourescents		Applied			20180505
				Not useable until I can buy some batteries / Stored under the bench (plugged in, floating); Stickers	IMG	Weak Batteries	L		20180505
2019	May	16	Th					Batteries discarded (salvage); Battery wires extended (used wires from CP_1); Drilled hole in front panel	A18 A1	Assembly	L0	-	20190516
				~	23:45			Attached to (4) T-105s in series (20150808_1/2, 20150808_2/2, 20150910_1/2, 20150910_2/2); Float is 27.3 to 27.4vdc				B4-B7	20190516
		17	Fr	~	00:00			Powered from and powering T2 circuit (main bench N); Also powering network center equipment (temporary)		Applied	L		20190517
				Stickers applied 'Modified & Installed on B4-B7 5/16/19', 'T2', 'ON/OFF/TEST/SILENCE Button >2 seconds: ON/OFF <1 second: Self Test / Silence Alarm'					20190517
				~	05:00			A3-4	S3				20190517
				Loads rearranged: powering T2 circuit (main bench N, currently T400s and etc.) and N Desk (currently T450s and etc.)					20190517
				06:10		06:40	A3-4					20190517
		20	Mo					20190520
		23					IMG				20190523
	Jun	29	Sa	~	08:15	~	08:45					20190629
	Jul	10	We	~	07:30	~	08:10	A3-4; PC_1 will be used for bench T2 circuit only					20190710
2019	Dec	19		~	09:00	~	11:45	A3-4					20191219
2020	Mar	10		~	22:12	~	02:14					20200310
2021	Jan	12	Tu					IMG			B4-B7	20210112
		14	We					20210114
	Dec	25	Sa	~	08:17	~	10:38		S2			B4-B7	20211225
2022	Aug	1	Mo					S2		L0		20220801
		2	Tu	~	08:15	~	08:54					20220802
				~	08:54	~	15:26					20220802
				~	19:25	~	19:35				L		20220802
2023	Jan	4	We	~	17:29	~	17:33	While working at T400s PC_1 shut itself OFF (dumped T400s) ...; Pressed ON several times and it came back up; Not sure what's going on but whatever it is it's not good; Watch and wait					20230104
	May	18	Th					A3-4	WS SSC LIB			B4-7	20230518

## A5
UPSs: A5	A					GXT2_1: Liebert GXT2-2000RT120

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2015	?	?					A2-6; A5 is 'L_3 from NVD'		Available	L	Dead	2015MM?
	Aug	8					A2-6 (4x18AH to be attached externally)	EML		L0		20150808
		5					A2-6					20150805
		13					[A5-6] Batteries attached externally and UPS placed in service in rear room (exact date unknown, but labels for installation in rear room were printed 8/12/15); A5 on T2 shop circuit		Applied	L	B22_25	20150813
2016	Jan	20					[A5-6] Part of the rear room shop circuit stuff (installed ~8/12/15)	IMG				20160120
2018	May	3					[A5-6] 20150805_18 (B18_21) and 20150813 (B22_25) batteries					20180503
		5					[A5-6] UPSs: GXT2_1, GXT2_2, 20150805_18 and 20150813 batteries					20180505
		6					[A5-6] 20150805_18 (B18_21) and 20150813 (B22_25) batteries; 'Liebert UPSs Battery Test' (videos, AED) / Both GXT2_1 and GXT2_2 UPSs and batteries are good for >1 hour operation with typical loads on shop circuits T1 and T2	IMG AED				20180506
		12	Sa		08:24		09:31	[A5-6] Power outage in Wood Heights area including Rayville, 1 hr 7 mins: / I continued working at T400s with some careful use of power on the T1 and T2 circuits (and it looked like I would have had another 30 mins of backup power if it had been needed)					20180512
	Jun	2	Sa	~	05:30			[A5-6] Brownouts: T2 circuit was dropped briefly (there was a pretty good load at the time, as I was using T400s and both monitors); But this could be an indication that the batteries are close to 'end of life'					20180602
				~	05:48	~	12:24	[A5-6] Power outage, 6-1/2 hours; I minimized the loads and kept GXT2_2 (T1) and GXT2_1 (T2) going; T1 died completely at ~08:35; T2 died completely at ~11:55; Power restored at ~12:24					20180602
		30	Sa	~	11:40			Beeping, red "Fault Indicator" light is lit, A&C LEDs (UPS failed battery test, long beep every minute): This is while I was using T400s with both monitors on; T2 battery pack is very warm (20150813, B22_25) / Pressed On for > 1sec which silenced beeping, but Fault Indicator remains on (red); CONCLUSION: batteries are toast				Weak	20180630
	Aug	31	Fr	~	06:15			Brief power failure (thunderstorm), beeping and error indications, no output; Disconnected input power and turned OFF; Power to T2 circuit bypassed		OFF		Dead	20180831
2019	Mar	31	Su					[A5-6] Batteries --> Salvage		Available		-	20190331
	May	20	Mo					[A5-6] Corrected/improved inventory sticker applied (over the top of the old one)					20190520
		23					[A5-6] Network UPSs on high shelf in rear room: PowerCom, Liebert, Delta, Trojan T-105s (A6 shown cut off on right)	IMG				20190523
2021	Jan	12	Tu					[A5-6] Moved GXT2_1 and GXT2_2 from above the door in the network room to West side storage on the pallets	B4-B7				20210112

## A6
UPSs: A6	A					GXT2_2: Liebert GXT2-1500RT120

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2015	?	?					A2-6; A6 is 'L_4 from NVD'		Available	L	Dead	2015MM?
	Jul	31					A2-6 (4x18AH to be attached externally)	EML		L0		20150731
	Aug	5					A2-6					20150805
		13					A5-6; A6 on T1 shop circuit		Applied	L	B18_21	20150813
2016	Jan	20					A5-6	IMG				20160120
2018	May	3					20180503
		5					20180505
		6					IMG AED				20180506
		12	Sa		08:24		09:31					20180512
	Jun	2	Sa	~	05:30			A5-6: A6 on T1 circuit kept going OK					20180602
				~	05:48	~	12:24	A5-6					20180602
2019	Mar	?					Brief power outage and T1 circuit not kept up (1-2 secs)		Bad Batteries		Dead	201903?
		31					Bypassed and OFF; A5-6		Available		-	20190331
	May	20	Mo					A5-6					20190520
		23					IMG				20190523
2021	Jan	12	Tu					B47-7				20210112

## A7
UPSs: A7	A					TL6_1_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/27/16	2/26/17	10/27/16	10/27/16
2015	Aug	15		~	00:15			[A7-29] 23 UPS units picked up at Johnson County data center (~2,500 lbs); (6) 6kVA sets (3 units each) and (5) 3kVA units; Subaru and Triton Trailer	IMG	Available	Triton Trailer	A9					20150815
		21					[A7-29] Initial cleaning, labelling, photographs and stacking (w/Sasha Howard); No testing			L					20150821

2016	Feb	4	Fr					[A7-9 A22-24] Cleaning, quality photographs, testing					2/4/16				20160204
		9	Tu		09:56			[A7-9] Charging…			L0					20160209
				11:04		11:14	[A7-9] No load battery test, 259 (13.0) … 251 (12.6) VDC @ 10 mins					2/9/16		20160209
				11:14		11:19	[A7-9] Heater load test battery, 231 (11.6) … 222 (11.1) VDC @ 5 mins					2/9/16	20160209
				11:20		11:45	[A7-9] Charging …; Charging concluded @ 25 mins, batteries used to test JC3 (TL6_5, A19-21, OK) / Moved to N stack on floor and noticed that one of the two battery connector posts is broken and needs extraction and replacement			L					20160209
		11	Th				18:04	[A7-9] Battery connector posts r/w (2) from JC8 (TL6_6, A22-24, another one broke), but now unit is ready for final charging and test, moved to S stack 2nd / Battery used to test JC4 (TL6_1, A7-9), charged some & heater test ...; Economy mode, charging…			L0					20160211
		17	We		09:42			[A7-9] End charging (5 days 15hrs 38mins)			L			2/17/16			20160217
	Mar	14	Mo		12:00			[A7-9] 270 VDC before charging. Begin charging for final test (want 72 hours)…			L0					20160314
	Jun	13	Mo	~	20:45			[A7-9] Unplugged to save electricity, has been floating for 3 months (I did not have time for the final test)			L			6/13/16			20160613
	Oct	23	Su		08:53		09:03	[A7-9] Plugged in; Battery is charging for final test (want 72 hours); A minute later: 94%/261 (13.1) VDC … / AC Output Breaker ON (but no load); Battery 100%/270 (13.5) VDC …			L0					20161023
		27	Th					[A7-9] Battery 274 (13.7) VDC; Heater plugged in (Bypass Mode), Load 88-89% 3.7KW; ON (Economy Mode)					20161027
				08:15		09:15	[A7-9] Online Mode (Economy Mode OFF), Load 87-88% 3.7KW …; Has been floating for 4 days: AC Input Breaker OFF …					10/27/16	10/27/16			20161027
				09:16		09:17	[A7-9] Battery 55% 235 (11.75) VDC …; Battery 53% 233 (11.65) VDC …					20161027
				09:18		09:19	[A7-9] Battery 50% 231 (11.55) VDC …; Battery 46% 229 (11.45) VDC …					20161027
				09:20		09:25	[A7-9] Battery 43% 227 (11.35) VDC; Removed heater load …; Battery 79% 249 (12.45) VDC; AC Input Breaker ON; FINAL TEST PASSED; Bypass Mode; Charging …					10/27/16	10/27/16	20161027
		30	Su		11:15			[A7-9] Has been floating for 3+ days: Unplugged			L			10/30/16			20161030
2017	Feb	24	Fr		09:40			[A7-9] Power applied (charging, Bypass Mode) …			L0					20170224
		26	Su		09:40			[A7-9] Unplugged			L			2/26/17			20170226
	Dec	8			04:27			[A7-9] Plugged in					20171208
		9					03:20	[A7-9] Unplugged					20171209
2018	May	18					[A7-31] Data on JC UPSs transferred here from UFS (see for further details not considered important here)	UFS					20180518
2019	May	20	Mo					[A7-25 A28-31] New inventory sticker applied [front]					20190520
				[A7-18] Batteries pulled for salvage				-					20190520
		23					[A7-25 A28-31] Photo of UPS stack, W Storage	IMG					20190523

## A8
UPSs: A8	A					TL6_1_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/27/16	2/26/17	10/27/16	10/27/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A9					20150815
		21					L					20150821
2016	Feb	2					[A8/11/14/17/20/23] Photo of 20v sockets (needed to buy a male plug for the heater); Photo of Dayton "Fan Forced Heater" sticker (ratings)					20160202
		4	Fr					A7-9 A22-24					2/4/16				20160204
		9	Tu		09:56			A7-9			L0					20160209
				11:04		11:14					2/9/16		20160209
				11:14		11:19					2/9/16	20160209
				11:20		11:45				L					20160209
		11	Th				18:04				L0					20160211
		17	We		09:42					L			2/17/16			20160217
	Mar	14	Mo		12:00					L0					20160314
	Jun	13	Mo	~	20:45					L			6/13/16			20160613
	Oct	23	Su		08:53		09:03				L0					20161023
		27	Th					20161027
				08:15		09:15					10/27/16	10/27/16			20161027
				09:16		09:17					20161027
				09:18		09:19					20161027
				09:20		09:25					10/27/16	10/27/16	20161027
		30	Su		11:15					L			10/30/16			20161030
2017	Feb	24	Fr		09:40					L0					20170224
		26	Su		09:40					L			2/26/17			20170226
	Dec	8			04:27					20171208
		9					03:20					20171209
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A9
UPSs: A9	A					TL6_1_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/27/16	2/26/17	10/27/16	10/27/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A9					20150815
		21					L					20150821

2016	Feb	4	Fr					A7-9 A22-24					2/4/16				20160204
		9	Tu		09:56			A7-9			L0					20160209
				11:04		11:14					2/9/16		20160209
				11:14		11:19					2/9/16	20160209
				11:20		11:45				L					20160209
		11	Th				18:04				L0					20160211
		17	We		09:42					L			2/17/16			20160217
	Mar	14	Mo		12:00					L0					20160314
	Jun	13	Mo	~	20:45					L			6/13/16			20160613
	Oct	23	Su		08:53		09:03				L0					20161023
		27	Th					20161027
				08:15		09:15					10/27/16	10/27/16			20161027
				09:16		09:17					20161027
				09:18		09:19					20161027
				09:20		09:25			Weak Batteries					10/27/16	10/27/16	20161027
		30	Su		11:15					L			10/30/16			20161030
2017	Feb	24	Fr		09:40					L0					20170224
		26	Su		09:40					L			2/26/17			20170226
	Dec	8			04:27					20171208
		9					03:20					20171209
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18		Available		-					20190520
		23					A7-25 A28-31	IMG					20190523

## A10
UPSs: A10	A					TL6_2_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	1/29/16	2/26/17	2/9/16	3/14/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A12					20150815
		21					L					20150821

2016	Jan	29	Fr					[A10-12] Cleaning, quality photographs, testing					1/29/16				20160129
	Feb	9	Tu		12:38		13:02	[A10-12] Quality photographs completed; Load test battery, 0% load, 254 (12.7) VDC …; 22 mins to 251 (12.6) VDC @ 24 mins …; Charging			L0			2/9/16	2/9/16		20160209
				13:34		13:39	[A10-12] Heater load test battery, 232 (11.6) ...; 222 (11.1) VDC @ 5 mins; Charging					2/9/16	20160209
				14:50			[A10-12] Moved to S Stack 1st, charging…					20160209
		11	Th		17:56			[A10-12] End charging (51 hrs)			L			2/11/16			20160211
		23	Tu		09:57			[A10-12] Start charging…			L0					20160223
	Mar	14	Mo		11:17		11:22	[A10-12] Has been charging for 2 weeks 6 days; 274 VDC …; Final Test, Heater Load: 234 (11.7) 54%, 233 (11.7) 53%, 231 (11.6) 50%, 229 (11.5) 46%, 227 (11.4) 43%					3/14/16		3/14/16	20160314
				11:27			[A10-12] Start charging...					20160314
	Jun	13	Mo	~	20:45			[A10-12] Has been floating for 3 months; Unplugged to save electricity			L			6/13/16			20160613
	Oct	23	Su		09:40		09:52	[A10-12] Battery 247 (12.4) VDC before plugging in (Fluke 8000A); Power applied (charging, Bypass Mode); Initial Battery 68%/248 (12.4) VDC … / Battery 100%/270 (13.5) VDC			L0					20161023
	Oct	24	Mo		10:20			[A10-12] Has been charging for 12 hrs 40 mins; 274 (13.7) VDC; Unplugged			L					20161024
2017	Feb	24	Fr		09:30			[A10-12] Power applied (charging, Bypass Mode) …			L0					20170224
		26	Su				09:40	[A10-12] Has been charging for 48 hrs +; Unplugged			L			2/26/17			20170226
	Dec	8			04:23			[A10-12] Plugged in: Charger failure! (Battery = 0%); Unplugged					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A11
UPSs: A11	A					TL6_2_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	1/29/16	2/26/17	2/9/16	3/14/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A12					20150815
		21					L					20150821
2016	Jan	29	Fr					A10-12					1/29/16				20160129
	Feb	2					A8/11/14/17/20/23					20160202
		9	Tu		12:38		13:02	A10-12			L0			2/9/16	2/9/16		20160209
				13:34		13:39					2/9/16	20160209
				14:50					20160209
		11	Th		17:56					L			2/11/16			20160211
		23	Tu		09:57					L0					20160223
	Mar	14	Mo		11:17		11:22					3/14/16		3/14/16	20160314
				11:27					20160314
	Jun	13	Mo	~	20:45					L			6/13/16			20160613
	Oct	23	Su		09:40		09:52				L0					20161023
	Oct	24	Mo		10:20					L					20161024
2017	Feb	24	Fr		09:30					L0					20170224
		26	Su				09:40				L			2/26/17			20170226
	Dec	8			04:23					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A12
UPSs: A12	A					TL6_2_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	1/29/16	2/26/17	2/9/16	3/14/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A12					20150815
		21					L					20150821

2016	Jan	29	Fr					A10-12					1/29/16				20160129
	Feb	9	Tu		12:38		13:02	A10-12			L0			2/9/16	2/9/16		20160209
				13:34		13:39			Weak Batteries					2/9/16	20160209
				14:50					20160209
		11	Th		17:56					L			2/11/16			20160211
		23	Tu		09:57					L0					20160223
	Mar	14	Mo		11:17		11:22					3/14/16		3/14/16	20160314
				11:27					20160314
	Jun	13	Mo	~	20:45					L			6/13/16			20160613
	Oct	23	Su		09:40		09:52				L0					20161023
	Oct	24	Mo		10:20					L					20161024
2017	Feb	24	Fr		09:30					L0					20170224
		26	Su				09:40				L			2/26/17			20170226
	Dec	8			04:23					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18		Available		-					20190520
		23					A7-25 A28-31	IMG					20190523

## A13
UPSs: A13	A					TL6_3_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	2/25/16	2/27/17	2/25/16	2/25/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A15					20150815
		21					L					20150821

2016	Feb	12	Fr					[A13-15] Cleaned					20160212
		17	We				09:47	[A13-15] Quality photographs; 245 VDC battery (before testing). Set 240 VAC Input & Output (switch and Setup) …; Online for inverter test (no load)	IMG		L0					20160217
				10:32		10:37	[A13-15] At 45 minutes into "no load" test I added the heater load (still online) …; At 50 minutes into test: heater load (battery), 267 VDC dropping rapidly					20160217
				10:38		10:39	[A13-15] Warning: "Shutdown imminent", I put it back on AC input at about 20 seconds into heater test …; 257 VDC; set Economy Mode					20160217
				10:45		11:32	[A13-15] Moved to S stack 4th …; Charging …					20160217
		25	Th		08:45		08:46	[A13-15] Has been floating for 7 days 21 hrs; Battery 274 VDC …; Online Mode					2/25/16			20160225
				08:48		08:56	[A13-15] Heater attached: load 85-86% … / AC Input OFF, at (0,1,2,3,4,5 mins) battery VDC: 231 (11.6), 232 (11.6), 230 (11.5), 228 (11.4), 226 (11.3), 224 (11.2), at 5mins AC Input ON					2/25/16	20160225
				09:03		09:45	[A13-15] Heater load removed, Economy Mode, battery 254 VDC and climbing …; Battery 265 VDC, AC Input OFF, 0% Load					20160225
				09:50		09:52	[A13-15] Battery 256 VDC (90%), AC Input ON …; Online Mode with heater 86% load …					2/25/16		20160225
				10:53			[A13-15] Heater load removed, Economy Mode, Charging…					2/25/16				20160225
	Mar	14	Mo		11:57			[A13-15] End charging (2 weeks 4 days)			L			3/14/16			20160314
	Jun	13	Mo	~	20:50			[A13-15] Charging, economy mode			L0					20160613
		15	We	~	11:55			[A13-15] Charging ended and shut down (1 day 15 hours)			L			6/15/16			20160615
	Oct	23	Su					[A13-15] Moved to S stack 3rd					20161023
		24	Mo		10:47			[A13-15] Battery 244 (12.2) VDC before plugging in (Fluke 8000A); Power applied (charging, Bypass Mode); Initial Battery 64%/246 (12.3) VDC			L0					20161024
		25	Tu		11:23			[A13-15] Battery 274 (13.7) VDC; Unplugged (24 hrs 36 mins)			L			10/25/16			20161025
2017	Feb	26	Su		10:15			[A13-15] Plugged in (charging, Bypass Mode)			L0					20170226
		27	Mo		11:53			[A13-15] Unplugged (25 hrs +)			L			2/27/17			20170227
	Dec	8			04:30			[A13-15] Plugged in: but no front panel (bypass mode); Probably very dead batteries; Unplugged					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A14
UPSs: A14	A					TL6_3_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	2/25/16	2/27/17	2/25/16	2/25/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A15					20150815
		21					L					20150821
2016	Feb	2					A8/11/14/17/20/23					20160202
		12	Fr					A13-15					20160212
		17	We				09:47		IMG		L0					20160217
				10:32		10:37					20160217
				10:38		10:39					20160217
				10:45		11:32					20160217
		25	Th		08:45		08:46					2/25/16			20160225
				08:48		08:56					2/25/16	20160225
				09:03		09:45					20160225
				09:50		09:52					2/25/16		20160225
				10:53					2/25/16				20160225
	Mar	14	Mo		11:57					L			3/14/16			20160314
	Jun	13	Mo	~	20:50					L0					20160613
		15	We	~	11:55					L			6/15/16			20160615
	Oct	23	Su					20161023
		24	Mo		10:47					L0					20161024
		25	Tu		11:23					L			10/25/16			20161025
2017	Feb	26	Su		10:15					L0					20170226
		27	Mo		11:53					L			2/27/17			20170227
	Dec	8			04:30					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A15
UPSs: A15	A					TL6_3_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	2/25/16	2/27/17	2/25/16	2/25/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A15					20150815
		21					L					20150821

2016	Feb	12	Fr					A13-15					20160212
		17	We				09:47		IMG		L0					20160217
				10:32		10:37					20160217
				10:38		10:39					20160217
				10:45		11:32					20160217
		25	Th		08:45		08:46					2/25/16			20160225
				08:48		08:56			Weak Batteries					2/25/16	20160225
				09:03		09:45					20160225
				09:50		09:52					2/25/16		20160225
				10:53					2/25/16				20160225
	Mar	14	Mo		11:57					L			3/14/16			20160314
	Jun	13	Mo	~	20:50					L0					20160613
		15	We	~	11:55					L			6/15/16			20160615
	Oct	23	Su					20161023
		24	Mo		10:47					L0					20161024
		25	Tu		11:23					L			10/25/16			20161025
2017	Feb	26	Su		10:15					L0					20170226
		27	Mo		11:53					L			2/27/17			20170227
	Dec	8			04:30					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18		Available		-					20190520
		23					A7-25 A28-31	IMG					20190523

## A16
UPSs: A16	A					TL6_4_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/29/16	11/6/16	10/29/16	10/29/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A18					20150815
		21					L					20150821

2016	Feb	11	Th		16:42		17:42	[A16-18] Cleaned, quality photographs; Initial test: won't power up; Battery 81.7 VDC; JC4 (TL6_1, A7-9) #02 batteries (TL6_1_B, A9) used for initial test: / OK, set 240 (Switch & Setup), Economy Mode NO; Heater test (with TL6_1_B) (online) … ; Online w/heater for 1 hour (TL6_1_B). Started heater test on battery …			L0	A9	2/11/16				20160211
				17:44			[A16-18] Heater test (with battery TL6_1_B, A9) concluded @ 2 mins because TL6_1_B batteries are low; Moved to main shop (for TL6_4_B battery rejuvenation)			L	A18					20160211

		25	Tu				13:51	[A16-18] All batteries are probably useable; Moved to N stack 1st and assembled battery bank, 250 (12.5) VDC (Fluke 8000A) … / Power applied, battery 75%/255 (12.75) VDC, charging …			L0					20160225
		29	Sa		03:45		03:50	[A16-18] Battery Temperatures are Good: All 81-86⁰F, #10 and #11 are the only two batteries above 85⁰F; Battery 274 (13.7) VDC / Heater plugged in (Bypass Mode), Load 89% 3.7KW; ON (Economy Mode) …; Online Mode (Economy Mode OFF), Load 86-87% 3.6KW; Battery 275 (13.75) VDC					20160229
				04:50		04:51	[A16-18] Has been charging for 3 days 15 hrs; AC Input Breaker OFF …; Battery 41% 227 (11.35) VDC					10/29/16	10/29/16			20160229
				04:52		04:53	[A16-18] Battery 33% 221 (11.05) VDC …; "Shutdown Imminent" (can't read battery V/%)					20160229
				04:54		04:55	[A16-18] "Shutdown Imminent" (can't read battery V/%) …; "Shutdown Imminent" (can't read battery V/%); Removed heater load					10/29/16	20160229
				05:00			[A16-18] Battery 70% 244 (12.20) VDC; AC Input Breaker ON; FINAL TEST PASSED; Bypass Mode; Charging …					10/29/16		20160229
	Nov	1	Tu		10:15			[A16-18] Battery has been charging >72 Hrs; Total (FP/Fluke) 274/275 VDC / Temperatures ⁰F, #1-20, 82,82,82,82,82,82,82,82,83,86,84,83,85,85,84,85,83,84,86,85 (#10 & #19) / DCV (Fluke) #1-20, 14.4,14.6,14.3,12.5,14.2,13.0,12.8,14.3,13.2,14.2,13.3,13.2,13.5,14.1,13.5,13.7,14.2,14.2,13.1,13.8 (#1 & #2) / Decided that I should replace (4) batteries: #1,2,10,19					20161101
				10:50			[A16-18] Batteries have been floating for 3 days 6 hrs; Unplugged (to replace 4 batteries)					11/1/16			20161101

		6	Su	~	05:05			[A16-18] (DST back 1 Hr); Has been charging since Tu11/1 12:05; Total (FP/Fluke) 274/276 (13.7/13.8) VDC / Temperatures ⁰F, #1-20, 79,79,78,78,77,78,78,78,79,83, 79,78,79,78,78,79,78,79,81,79 (#10,#19) / DCV (Fluke) #1-20, 14.2,15.0,14.2,12.7,12.9,13.9,13.8,14.2,13.0,14.9,13.4,13.1,13.4,13.9,13.4,13.4,13.5,13.9,15.2,13.6 (#2,#10,#19)				A18(16) A21(4)					20161106
				~	05:50	~	05:52	[A16-18] Heater load 87%/3.7KW …; Online 86-87%/3.6-3.7KW					20161106
				05:56		05:57	[A16-18] Batteries have been floating for 4 days 19 hrs; AC input OFF … ; 32% 220 (11.0) VDC					11/6/16			20161106
				05:58		06:00	[A16-18] "Shutdown Imminent" (can't read battery V/%) …; It shut itself off @ 3'40"; AC input ON (Test Fail "Battery 5 mins >80% Load")					20161106
				~	06:02	~	06:08	[A16-18] Heater load removed …; Small heater load 33%/1.4KW; Battery 84% 259 (12.95) VDC					20161106
				06:10		06:11	[A16-18] AC input OFF … ; 79% 250 (12.5) VDC …; Battery total Fluke 249 (12.45) VDC …; DCV (Fluke) 12.8,13.0,12.6,10.2,12.4,12.6,12.6,12.4,12.4,12.9,12.4,12.4,12.5,12.6,12.5,12.5,12.5,12.2,12.9,12.5; Battery total Fluke 248 (12.4) VDC / [test was at ~5.6A discharge] …					20161106
				~	06:19	~	06:48	[A16-18] Battery 77% 247-248 (12.35-12.4) VDC; AC input ON; Small heater load OFF; Should replace (by load test) 4,5,8,9,11,12,18; Should replace (by high T) 10,19 / I don't have enough "good" batteries (2 with load test >12.0v@5'/7-8A); Charging until FP 100% … ; OFF (Online->Bypass) Battery 90%					20161106
				~	07:48	~	08:01	[A16-18] Battery 97% … ; Battery 100%; AC input removed (UPS OFF)			L					20161106
2017	Feb	26	Su		10:21		16:55	[A16-18] Plugged in (charging, Bypass Mode) … ; Unplugged					20170226
	Dec	8		~	04:30			[A16-18] Plugged in: but no front panel (flickering display backlight, bypass mode, probably very dead batteries); Unplugged					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A17
UPSs: A17	A					TL6_4_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/29/16	11/6/16	10/29/16	10/29/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A18					20150815
		21					L					20150821
2016	Feb	2					A8/11/14/17/20/23					20160202
		11	Th		16:42		17:42	A16-18			L0	A9	2/11/16				20160211
				17:44					L	A18					20160211

		25	Tu				13:51				L0					20160225
		29	Sa		03:45		03:50					20160229
				04:50		04:51					10/29/16	10/29/16			20160229
				04:52		04:53					20160229
				04:54		04:55					10/29/16	20160229
				05:00					10/29/16		20160229
	Nov	1	Tu		10:15					20161101
				10:50					11/1/16			20161101

		6	Su	~	05:05					A18(16) A21(4)					20161106
				~	05:50	~	05:52					20161106
				05:56		05:57					11/6/16			20161106
				05:58		06:00					20161106
				~	06:02	~	06:08					20161106
				06:10		06:11					20161106
				~	06:19	~	06:48					20161106
				~	07:48	~	08:01				L					20161106
2017	Feb	26	Su		10:21		16:55					20170226
	Dec	8		~	04:30					20171208
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				A7-18				-					20190520
		23					A7-25 A28-31	IMG					20190523

## A18
UPSs: A18	A					TL6_4_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	10/29/16	11/6/16	10/29/16	10/29/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A18					20150815
		21					L					20150821

2016	Feb	11	Th		16:42		17:42	A16-18		Weak Batteries	L0	A9	2/11/16				20160211
				17:44					L	A18					20160211
		13	Sa	~	13:20	~	14:00	Removed cover and tape over batteries; #10 battery voltages, low to high: 3.7, 5.4, 3.8, 3.0; 3.7, 4.3, 3.8, 3.8; 5.4, 3.1, 4.7, 4.5; 5.4, 4.6, 5.3, 5.4; 5.4, 3.8, 5.4, 3.7 / Calculated total: 88.2 VDC (agrees OK with 81.7 VDC measured 2/11, when considering roundoff errors and different temperature) ... / Finished breaking into 5 strings of 4 batteries each, before parallel connection: 15.6, 15.4, 17.3, 20.6, 18.0			L0					20160213
				14:03		14:09	Paralleled total 18.0 VDC dropping …; BK 48.0 VDC CV @ 0.84 A climbing					20160213
				14:20	~	14:25	1.02 A steady … / 0.93 A dropping, individual voltages: 12.4, 10.2, 12.3, 12.5; 12.6, 11.6, 12.4, 11.1; 11.4, 11.3, 12.6, 12.1; 11.5, 11.7, 12.9, 11.4; 11.5, 11.2, 11.6, 13.1 / Adjusted BK, watching battery #20, to keep @ <=14.3 VDC					20160213
				14:32		16:03	BK 54.4 VDC CV @ 1.58 A climbing, battery #20 14.2 VDC …; 48.2 VDC @ 1.85 A CC					20160213
				16:04	~	16:08	Battery #20 12.1 VDC …; Measured individual batteries, all are balanced (see white sheet), will continue BK setting "float" (54.40v)	WS					20160213
				16:15		17:10	48.3 VDC @ 1.83 A CC …; 48.0 VDC @ 1.83 A CC, temperatures are even, all about 23-24 deg C (still not concerned about setting for the night)					20160213
				17:39			48.2 VDC @ 1.83 A CC					20160213
		14	Su		04:40		07:55	51.9 VDC @ 1.83 A CC, batteries are all 12.7 to 12.8 VDC …; 52.7 VDC @ 1.83 A CC, batteries are all 12.9 to 13.0 VDC					20160214
				~	20:00			54.4 VDC @ 0.38 A CV, dropping rapidly; All looks good, float charge is proceeding normally; Individual voltages from 13.2 to 14.0 VDC; Battery #6 is 14.0 VDC					20160214
		15	Mo		07:55		18:00	54.4 VDC @ 0.16 A CV; Battery #6 is 14.0 VDC …; 54.4 VDC @ 0.15 A CV; Battery #6 is 14.0 VDC; Watching to see if charging current drops to less than 100 mA					20160215
				18:27			54.4 VDC @ 0.16 A CV; I don't know why it is not dropping, except to say, the "lagging batteries" are finally taking a charge; Watch and wait					20160215
		16	Tu		08:15		15:56	54.4 VDC @ 0.19 ±0.01 A CV (somewhat erratic), batteries are all 13.1 to 13.8 VDC ...; 54.4 VDC @ 0.23 A CV					20160216
		17	We		08:30		08:33	54.4 VDC @ 0.26 A CV …; Batteries are all 13.2 to 13.9 VDC, #8 battery is 13.9 VDC					20160217
				08:35		09:02	Equalization: raised BK to 57.0 (14.25) VDC, initial current is 0.73 A, and battery #8 is 14.5 VDC … / Battery #8 is 14.5 VDC; Reduced BK to 55.0 (13.75) VDC to avoid outgassing #8					20160217
				09:06		10:53	Battery #8 is 14.0 VDC; will leave BK @ 55.0 VDC (now 0.36 A) … ; 55.0 VDC @ 0.33 A, #5 13.2, #8 14.0 VDC					20160217
				11:46		15:52	55.0 VDC @ 0.32 A; #5 13.3, #8 14.0 VDC; OK, will leave at this float voltage (13.75 VDC per battery unit) …; 55.0 VDC @ 0.35 A					20160217
		19	Fr		04:10		04:23	55.0 VDC @ 0.41 A rising very slowly, batteries are all between 13.2 (#5) to 14.2 (#8) VDC … / 55.0 VDC @ 0.43 A, contact resistance appears to be playing a part as moving leads causes changes, battery #8 is 14.3 VDC					20160219
				04:38		05:10	55.0 VDC @ 0.45 A …; 55.0 VDC @ 0.46 A; Erratic if clip lead touched (changed clip lead from BK)					20160219
				05:19		05:27	55.0 VDC @ 0.46 A …; 55.0 VDC @ 0.47 A					20160219
				05:36		05:57	55.0 VDC @ 0.48 A …; 55.0 VDC @ 0.49 A					20160219
		20	Sa	~	07:15		07:30	55.0 VDC @ 0.55 A, #5 13.2, #8 14.4, #10 14.5 VDC, BK adjusted down, 54.0 VDC @ 0.40 A, #10 battery is cracked and has been outgassing heavily along the seam … / 54.0 VDC @ 0.43 A, #10 14.0 VDC					20160220
				~	09:28		09:47	54.0 VDC @ 0.41 A, #10 14.3 VDC, BK adjusted down to 53.5 VDC @ 0.33 A initially …; 53.5 VDC @ 0.35 A			L					20160220
		24	Mo					Disassembled battery bank (#10); Testing individual batteries …			L0					20160224
		25	Tu				13:51	A16-18					20160225
		29	Sa		03:45		03:50					20160229
				04:50		04:51					10/29/16	10/29/16			20160229
				04:52		04:53					20160229
				04:54		04:55					10/29/16	20160229
				05:00					10/29/16		20160229
	Nov	1	Tu		10:15					20161101
				10:50					11/1/16			20161101
				12:05	Batteries replaced with ones from JC3#13 (TL6_5_B, A21): #1 r/w B#01; #2 r/w B#10; #10 r/w B#11; #19 r/w B#19 / All four of the batteries from TL6_5 were charged and load tested AOK, then charged again for several days (see post-its on reverse of white sheet notes for details) / I'm really not sure they are any better than what was there to begin with, but I want to try and see. ...; Plugged in and charging …	WS			A18(16) A21(4)					20161101
				Discharge test on (4) original batteries (TL6_4_B): #1, 13.0->12.1; #2, 13.0->12.2; #10, 12.8->10.8; #19, 12.8->12.1 (VDC under 7-8A Load @ 5mins)					20161101
				14:25		17:05	Original batteries (TL6_4_B): Removed and on BK float … / End float: Scrapped #10 (load test dropped to 10.8 @ 5'); Scrapped #19 (load test OK, but high current on charge); #1 & #2 kept (load test good)					20161101
		6	Su	~	05:05			A16-18					20161106
				~	05:50	~	05:52					20161106
				05:56		05:57					11/6/16			20161106
				05:58		06:00					20161106
				~	06:02	~	06:08					20161106
				06:10		06:11					20161106
				~	06:19	~	06:48					20161106
				~	07:48	~	08:01				L					20161106
2017	Feb	26	Su		10:21		16:55					20170226
	Dec	8		~	04:30					20171208
2018	May	3					Original TL6_4_B #01 and #02 batteries installed in PowerCom UPS (PC_1/A4)	A4					20180503
		18					A7-31					20180518
2019	May	16	Th					Original TL6_4_B #01 and #02 batteries discarded (they were installed in PowerCom UPS (PC_1/A4) --> salvage	A4					20190516
		20	Mo					A7-25 A28-31					20190520
				A7-18		Available		-					20190520
		23					A7-25 A28-31	IMG					20190523

## A19
UPSs: A19	A					TL6_5_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	2/8/16	2/23/16		2/9/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A21					20150815
		21					L					20150821

2016	Feb	6	Sa					[A19-21] Cleaning, straightened bent cover on #15 (TL6_5_T, A20, Transformer Module), quality photographs, initial testing, Economy Mode charging …			L0		2/6/16				20160206
		7	Su					[A19-21] OK, still charging …					20160207
		8	Mo	~	07:30	~	08:30	[A19-21] Early AM short power failures; "O/P Short" error …; Restarted 1 hour test (Online Mode)					2/8/16			20160208
				~	10:00	~	10:50	[A19-21] 1 hour test OK (~90 mins), back to Economy Mode …; Pulled input plug (no load). Unit almost immediately shut down: "Battery Low"					2/8/16				20160208
				~	11:00		11:02	[A19-21] Pulled input plug again (no load): "Output S/C", "Output Failure", "CALL FOR SERVICE"; Turned set OFF …; Restarted, Economy Mode, charging …					20160208
		9	Tu		09:40		09:46	[A19-21] No load, Economy, transfer to battery (#13, A21, TL6_5_B): "O/P Short" then "On Battery" / 225 VDC … 224 … 223 (11.5) … 222 (11.1) @ 5 mins and heater load shut down …; Economy, charging …					2/9/16	20160209
				09:47			[A19-21] Shut down; Tested with JC8 #16 battery (TL6_6_B, A24) and won't power up (just like JC 8, TL6_6, A22-24) [2/13/16: TL6_6_B battery is bad]				A24					20160209
				~	12:00		12:03	[A19-21] Battery TL6_1_B used to test …; Economy --> Battery (no load), @ 5 mins 254 VDC (12.7)				A9					20160209
				12:08		12:12	[A19-21] Heater load, initially 235 VDC (11.8) …; Unit shut itself down at ~4.5 mins (battery under voltage) / [And this is OK, because TL6_1_B battery was not very well charged at this point]					20160209
		11	Th				19:31	[A19-21] Moved to S stack 3rd …; Economy, Charging (want 72 hours) …				A21					20160211
		23	Tu		08:52		09:00	[A19-21] Has been charging for almost 12 days; Battery voltage is 276 VDC …; Heater plugged in (now 85-86% load); Set Online Mode (87% load)					2/23/16			20160223
				09:07		09:08	[A19-21] Battery 275 VDC, handling heater load OK (Online Mode) … / AC Input Breaker OFF and on battery: immediate "Inverter Failure, Call for Service" and unit turned itself OFF					20160223
				09:09		09:12	[A19-21] No Load, ON, diagnostics report "Bad Battery, Call for Service" …; OFF, waited, restored AC, front panel flashing (battery bank is probably too low to start it up)					20160223
				09:13			[A19-21] OFF, waited, restored AC, front panel dead (but LED for "Bypass" is on): Once again, symptom is for battery bank too low to start it up					20160223
	Oct	23	Su					[A19-21] Moved to Main Shop 3rd (to test batteries)			L					20161023

		29					[A19-20] Batteries for this set scrapped				-					20161029
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523

## A20
UPSs: A20	A					TL6_5_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	2/8/16	2/23/16		2/9/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A21					20150815
		21					L					20150821
2016	Feb	2					A8/11/14/17/20/23					20160202
		6	Sa					A19-21			L0		2/6/16				20160206
		7	Su					20160207
		8	Mo	~	07:30	~	08:30					2/8/16			20160208
				~	10:00	~	10:50					2/8/16				20160208
				~	11:00		11:02					20160208
		9	Tu		09:40		09:46					2/9/16	20160209
				09:47					A24					20160209
				~	12:00		12:03					A9					20160209
				12:08		12:12					20160209
		11	Th				19:31					A21					20160211
		23	Tu		08:52		09:00					2/23/16			20160223
				09:07		09:08					20160223
				09:09		09:12					20160223
				09:13					20160223
	Oct	23	Su					L					20161023

		29					A19-20				-					20161029
2018	May	18					A7-31	UFS					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523

## A21
UPSs: A21	A					TL6_5_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				! DC Cable	L	-	2/8/16	2/23/16		2/9/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A21					20150815
		21					L					20150821

2016	Feb	6	Sa					A19-21			L0		2/6/16				20160206
		7	Su					20160207
		8	Mo	~	07:30	~	08:30					2/8/16			20160208
				~	10:00	~	10:50					2/8/16				20160208
				~	11:00		11:02					20160208
		9	Tu		09:40		09:46			Weak Batteries					2/9/16	20160209
				09:47					A24					20160209
				~	12:00		12:03					A9					20160209
				12:08		12:12					20160209
		11	Th				19:31					A21					20160211
		23	Tu		08:52		09:00					2/23/16			20160223
				09:07		09:08					20160223
				09:09		09:12					20160223
				09:13					Dead Batteries					20160223
	Oct	23	Su					20161023
		25	Tu					Bank 160 (8.0) VDC; Charged in 5 strings of 4, but aborted this after only about 12 Mins (too much imbalance); Disassembled, and there's a screw to drill out and tap in the middle battery bar; Individual tests (5 at a time on BK @ 13.6 VDC)		Drill & Tap					20161025
		29	Sa					(15) batteries scrapped, (5) batteries useable (all passed 5min Load Test), float charging under bench …			L	-					20161029
2018	May	18					A7-31					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
				(4) Original JC3 #13 (A21/TL6_5_B) batteries scrapped (#01, #10, #11, #19; they were in A18) / One remains more or less permanently on the bench (powering Wattmon_9, charged with Heathkit)					20190520
		23					A7-25 A28-31	IMG					20190523
2021	Jan	14	Th					Removed (2) DC cables from battery modules TL6_5_B (A21) and TL6_6_B (A24) for use on RHS/TurboNet contract	L5	! DC Cable					20210114

## A22
UPSs: A22	A					TL6_6_P: TrippLite SU6000RT3UPM					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				!Connector	L	-
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A24					20150815
		21	Fr					L					20150821

2016	Feb	4	Fr					A7-9 A22-24 ...			L0					20160204
		6	Sa					[A22-24] Cleaning, photographs, testing completed / Won't power up (probably dead battery bank, as discovered 2/9/16 when using this battery bank (TL6_6_B, A24) to test JC3 (TL6_5) (same symptom there) / Moved to main shop to test batteries.			L					20160206
		11	Th					Battery connector posts removed for use on JC4 (TL6_1_P, A7)		!Connector					20160211

	Oct	26	We					Batteries for this set scrapped				-					20161026
2018	May	18					A7-31					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523

## A23
UPSs: A23	A					TL6_6_T: TrippLite SU6000XFMRRT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				!L6-30	L	-
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A24					20150815
		21	Fr					L					20150821
2016	Feb	2					A8/11/14/17/20/23					20160202
		4	Fr					A7-9 A22-24 ...			L0					20160204
		6	Sa					A22-24			L					20160206

	Oct	26	We					Batteries for this set scrapped				-					20161026
	Nov	22	Tu					Removed one of three L6-30 sockets (for use on Aube heater controller); See photos	IMG	!L6-30					20161122
2018	May	18					A7-31					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523

## A24
UPSs: A24	A					TL6_6_B: TrippLite BP240V7RT3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				! DC Cable	L	-
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A24					20150815
		21	Fr					L					20150821

2016	Feb	4	Fr					A7-9 A22-24 ...			L0					20160204
		6	Sa					A22-24		Dead Batteries	L					20160206
		9	Tu					Battery TL6_6_B used to test JC3 (TL6_5, A19-20): Same symptom there (won't power up) but later JC3 did power up with #02 batteries (TL6_1_B, A9), so evidently this battery bank is dead or too low a voltage to start the unit			L0					20160209
		10	We		18:25		20:56	Measured battery bank voltage (#16, A24, TL6_6_B)… 50.7 VDC (obviously dead, this is 2.5 VDC per 12 V battery) / Opened cover to rig charge using BK Precision (5 strings of 4 batteries each @ initial charge of 14.9 VDC per battery = 59.60 VDC)… / String voltages, 1st string (from Negative connection upwards) to 5th string: 7.8, 0.4, 18.1, 11.3, 12.0 / After parallel connections made: 7.9 VDC ... (a whole bunch of irrelevant charging data omitted) ...; BK programmed for Absorption (52.90v) for the night					20160210
		11	Th		08:00		23:50	1.672 A @ 52.56 VDC climbing slowly; String T (deg C): 22, 27, 25, 25, 24 ... (a whole bunch of irrelevant charging data omitted) ... / Reduced BK target (53.0v) and left overnight					20160211
		12	Fr		10:07		18:20	1.66 A @ 53.0 VDC, CV, Measured deg C and battery voltages; There are (8) batteries that will not come up to intrinsic voltage, with one or two per string that are bad / The other batteries are being driven above gassing voltage ... (a whole bunch of irrelevant charging data omitted) ...; BK at 50.0v					20160212
		13	Sa		06:30		06:45	1.8 A @ 51.9 VDC, CC (battery #18 7.9 VDC) (raised BK maximum to 54.5 VDC) …; 0.6 A @ 46.9 VDC, CV (lowered BK max to 46.9 VDC)					20160213
				07:00			CONCLUSIONS: There are (12) batteries that may be useable, but (8) must be discarded (see white sheets) / Battery #14 is obviously dry and has acid flakes at terminal, but it is one of the dead ones; Dead: #1, 7, 8, 9, 12, 14, 16, 18 / Maybe useable: #2, 3, 4, 5, 6, 10, 11, 13, 15, 17, 19, 20 (but these have been outgassed dry by my attempts / KEEP to borrow spares in rejuvenating JC 12 (TL6_4_B) or others	WS		L					20160213
	Oct	24	Mo					Disassembled and labeled battery bank (#16); Testing individual batteries …			L0					20161024
		25	Tu					(19) batteries scrapped; (1) hopeful on Trace …				-					20161025
		26	We					Hopeful scrapped (all 20 batteries have been sent to the scrapper); Waiting procurement or spares		Available	L					20161026

2018	May	18					A7-31					20180518
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523
2021	Jan	14	Th					Removed (2) DC cables from battery modules TL6_5_B (A21) and TL6_6_B (A24) for use on RHS/TurboNet contract	L5	! DC Cable					20210114

## A25
UPSs: A25	A					TL3_1: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				!L5-30 !FP	L	-		11/1/16
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A25					20150815
		21					L					20150821
2016					[A25-31] Stickers applied, cover removed, cleaned inside with compressor (unknown date, but probably 2016, brown table W side)					20160821
	Oct	31	Mo					Moved to main shop; Photos; removed front cover and battery unit (6x12v); Battery stickers applied	IMG		L0					20161031
				14:10		14:20	OC total bank 69.8 VDC [good], DCV 9.9,12.0,12.0,12.0,12.0,12.0 (#1-#6) …; Float charging on BK (6x12v singles, 13.6vdc)					20161031
	Nov	1	Tu		14:15		14:25	Removed from float after observing charge mA for individuals: ~95,40,?*,10,10,10 (*I accidently shorted it, so don't know) / #1 is the weakest battery, taking a long time to come up to full charge …; Topping charge for #3 (which I accidently shorted)					11/1/16			20161101
				15:07		15:15	Topping charge for #3 ended …; DCV (Fluke): 10.8,13.0,13.2,13.1,13.1,13.1; Decided to break the brick apart, discharge test, and probably will scrap #1 (photos)	IMG					20161101
				16:30			Discharge tests complete (VDC under 7-8A Load at 5 mins unless noted): #01, 10.8->~2.0 @ 0 Secs (scrapped); #02, 13.0->11.7 (OK but weak, on float...) / #03, 13.1->11.9 (OK but weak, on float...); #04, 13.1->11.8 (OK but weak, will float); #05, 13.1->11.9 (OK but weak, will float) / #06, 13.0->11.9 @ 18 Mins (oops!, strong enough, will float)				A25 #02-06					20161101
				Assembled a six pack from identical UB1280 batteries / These were probably purchased for the Deltec in Spring 2015 (after return from Ukraine), but the Deltec died soon after that / They've been kept floating under the bench ever since then / 10/29/16 load tests were all good, 12.1v @ 5' (but two of the eight batteries in the set were scrapped, leaving these six) / Floated for more than 2 days since the load tests, down to ~10mA per battery				UB1280 from Deltec					20161101
				Removed the rear panel NEMA L5-30 female socket (for making a cord I can use to plug these in)	IMG	No L5-30					20161101
				Moved to W side: N stack #1 (waiting assembly of test cord for plugging it in)			L					20161101
2017	Feb	26	Su		10:33		10:44	Plugged in; Within 1 minute LINE, FAULT, 100% (beeps); Unplugged; Plugged in: Within 1 minute (same, beeps) ...; Unplugged				Dead (UB1280/Deltec)					20170226
2018	May	18					A7-31	UFS					20180518
2019	May	19	Su					Original TL3_1 batteries #02-06 scrapped					20190519
				Battery six pack (UB1280/Deltec) is 5.3 vdc total --> Salvage				-					20190519
		20	Mo					A7-25 A28-31; Also missing one front panel screw		!L5-30 !FP					20190520
		23					A7-25 A28-31	IMG					20190523

## A26
UPSs: A26	A					TL3_2: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr ~50% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 30-60 mins ~50% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L5	B62-B67	~12/15/17	Continuous	~12/15/17	~12/15/17
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A26					20150815
		21					L					20150821
2016					A25-31					20160821
	Nov	1	Tu					Moved to main shop; Battery total 72.0 VDC (very good) 12.0,12.0,12.0,12.0,12.0,12.0; Will not remove batteries to test charge; Moved back to W side (tool cart)					20161101
2017	Feb	24	Fr		08:00			Plugged in (1st charge in 1-1/2 years); Front Panel yellow "Battery Low" …			L0					20170224
		25	Sa		03:45		04:15	LINE and LOAD, all other LEDs off …; Swapped AC input cords with JC9#21 (TL3_3, A27)					20170225
				08:45			Unplugged (will come back to it soon for additional charging)			L			2/25/17			20170225

	Dec	7					[A26-27] New batteries ordered from BatterySharks.com	EML TA2	Slated for RHS					20171207
		12					[A26-27] New batteries received (A26 batteries from JC removed and added to salvage pile)	TA2		L0	Salvage					20171212
		19					[A26-27] New batteries installed (exact date unknown); Load testing (probably 50% load, and probably went 30-60 minutes on battery); Cleaned / My previously installed stickers removed/covered with new ones (12/19/17)				B29-40	~12/15/17	Continuous	~12/15/17	~12/15/17	20171219
		20	We		15:00			[A26-27] UPSs (and installed batteries) delivered to Richmond High School (installed, final payment rec'd from TurboNet, total $1700) - 1 Year Warranty	DBT TA2	Sold	L5					20171220
2018	May	18					A7-31	UFS					20180518
2021	Feb	24	We	~	12:15	~	17:00	[A26-27] Travel and onsite at RHS: Boost charger mounted to RHS fabricated battery box, which looks great; 27TMX batteries installed / Cables hooked up and attached to UPSs / Top UPS #21 (A27, TL3_3) 82.8-82.9v, bottom #20 (A26, TL3_2) 83.1v (MuRata+~0.25=Fluke), will put all loads on top UPS / Tested webcards, top #21 (TL3_3) 41% load, bottom #20 (TL3_2) could not access (needs reboot?); Removed batteries from TL3_2 and TL3_3 (to shop); Photos	IMG TA2		L5	B62-B67					20210224
		25	Th	~	04:30	~	07:15	[A26-27] Onsite again to switch loads over to top UPS; Boost voltage is set too high, the bottom UPS went into OVP bypass beep and error / Adjusted boost down using Fluke, was 43.75v each supply, now 43.25 each supply (14.425 equivalent), 86.3v on Murata (battery bank sticker is wrong) / Brian moved all the loads from bottom UPS (TL3_2) to top UPS (TL3_3) without bringing anything down because they have dual power supplies / T450s2 reports 70% total load on top UPS / (2nd discharge test @ shop was @ 75% 1hr40mins, so estimated run-time 1hr50mins, front panel bargraph 3rd of 4 LEDs blinking) / Bottom UPS unplugged and mentioned to Brian that he can plug it in to speed recovery / "Pulled the plug" for 5 mins (AOK, 12v equivalent); Applied (2) labels for front of UPSs TL3_3 and TL3_2 "2/24/21 Batteries Removed ..."; Photos					20210225

## A27
UPSs: A27	A					TL3_3: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr ~50% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 30-60 mins ~50% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L5	B62-B67	~12/15/17	Continuous	~12/15/17	~12/15/17
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A27					20150815
		21					L					20150821
2016					A25-31					20160821
	Nov	1	Tu					Moved to main shop; Battery total 72.2 VDC (very good) 12.0,12.2,12.0,12.0,12.1,12.0; Will not remove batteries to test charge; Moved back to W side (tool cart)					20161101
2017	Feb	24	Fr		08:10	~	23:00	Plugged in (1st charge in 1-1/2 years); Front Panel yellow "Battery Low" …; Beeping (1 long and 2 short, every 4 secs)			L0					20170224
		25	Sa	~	00:00	~	00:30	There was no way to kill the beeps (in trying, I accidently put it online for a short period), so I unplugged it, and plugged it back in (OK for now) … / It started beeping again (I didn't touch it, I went back to sleep)					20170225
				~	02:30	~	04:15	LINE, FAULT, 100% FULL CHARGE, all other LEDs off; Unplugged and plugged into another AC outlet (it was in the central hanging GFC top outlet, moved to GFC next to freezer); No beeping, LINE and LOAD …; It started beeping again; Swapped AC input cords with JC2#20 (TL3_2, A26)					20170225
				04:21			Beeping again; Unplugged (will t-shoot later)			L					20170225
	Dec	7					A26-27	EML TA2	Slated for RHS					20171207
		12					TA2		L0	Salvage					20171212
		19					B41-52	~12/15/17	Continuous	~12/15/17	~12/15/17	20171219
		20	We		15:00				DBT TA2	Sold	L5					20171220
2018	May	18					A7-31	UFS					20180518
2021	Feb	24	We	~	12:15	~	17:00	A26-27	IMG TA2		L5	B62-B67					20210224
		25	Th	~	04:30	~	07:15					20210225

## A28
UPSs: A28	A					TL3_4: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-		2/26/17
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A28					20150815
		21					L					20150821
2016					A25-31					20160821
	Nov	1	Tu					Moved to main shop; Battery total 72.1 VDC (very good) 12.0,12.1,12.1,12.1,11.9,12.0; Will not remove batteries to test charge; Moved back to W side (brown table)					20161101
2017	Feb	25	Sa		04:30		08:45	Plugged in (1st charge in 1-1/2 years); LINE, LOAD, BAT LOW …; Noticed BAT LOW led is off					20170225
		26	Su		09:37			Unplugged (need to come back soon)					2/26/17			20170226
2018	May	17					A7-31					20180517
2019	May	19	Su					Battery six pack is 19.7 vdc total --> Salvage				-					20190519
		20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523

## A29
UPSs: A29	A					TL3_5: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-		3/4/21
2015	Aug	15		~	00:15			A7-29	IMG	Available	Triton Trailer	A29					20150815
		21					L					20150821
2016					A25-31					20160821
	Nov	1	Tu					Moved to main shop; Battery total 12.8 VDC (very bad) 0.3,4.7,0.6,3.5,2.9,1.0; Removed batteries for BK charge; Entire 6-pack scrapped / Moved back to W side (brown table)		Available		-					20161101
2018	May	17					A7-31					20180517
2019	May	20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523
2021	Mar	3	We	~	14:50			Salvaged batteries from RHS installed in TL3_7 and TL3_5 and Float rotation started; Float is 82.6v Fluke	L5			B29_34 B35_40		3/4/21			20210303
	Oct	1	Fr					Salvaged batteries from RHS --> Salvage (Midwest Scrap Management)	BR			-					20211001

## A30
UPSs: A30	A					TL3_6: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Dead ! MOV	L	-		2/28/17
2015	Sep	1	Th					[A30-31] Approximate date I picked up these two units from Nathan Van Duyn's house in Kansas City		Available	L	A30					20150901
2016					A25-31					20160901
	Nov	1	Tu					Moved to main shop; Labels "NVD 2015 #24" (7); Battery total 68.6 VDC (maybe OK) 12.2,10.2,10.4,11.9,12.2,11.8 / Removed batteries for BK charge (accidental 10 second short after measuring VDC); Moved back to W side (brown table)			L0					20161101
		2	We		11:00			Batteries main shop BK charge concluded: they're 98% charged; Load Tests "not very good" but all of the batteries made 5', will float on BK					20161102
		3	Th		08:30			Currently 0.107 A (7 batteries)					20161103
		22	Tu		07:50			BK float end, 0.116 A (7 batteries); Batteries under bench			L	A30 under bench		11/22/16			20161122
2017	Feb	24	Fr	~	10:15			Batteries under bench: OC DCV 13.0,12.9,12.9,11.6,13.0,12.9; On BK float			L0					20170224
		28	Tu	~	05:15			BK float end, 0.019 A @ 13.60 V (6 batteries)			L			2/28/17			20170228
2018	May	18					A7-31					20180518
2019	May	19	Su					OCV 12.1,7.9,11.8,6.5,11.9,11.2 (starting with lower right battery and then CCW) (61.2 vdc total) / I scrapped all the other 6-packs from the 3kva units today, this 6-pack is the best OCV and is being kept in case I need 72 vdc or for low current needs			L0	A30 on bench					20190519
				~	12:10	~	12:15	TL3_6 batteries all (6) in parallel charging on BK_1 (S2) @ float of 13.60 vdc …; 2.5 amps total; Photos	IMG					20190519
		20	Mo					A7-25 A28-31					20190520
				~	08:40			TL3_6 batteries floating on BK_1: Warmest battery is the 2nd one (86⁰F), 3rd one is also warm (79⁰F), curiously 4th one is the same temperature as all the others (76⁰F) / 0.7 amps total					20190520
		21	Tu	~	00:10	~	06:40	TL3_6 batteries floating on BK_1: 2nd battery 90-96⁰F; the others are 75-80⁰F; 0.8 amps total (up slightly from yesterday morning) … / 0.9 amps total, #2 battery is probably in thermal runaway, limited current to 0.3 amps, now CC @ 12.65vdc (slightly below intrinisic); #2 93⁰F					20190521
		22	We	~	12:15	~	12:55	TL3_6 batteries floating on BK_1: Battery #2 probably has a shorted cell, of the (6) it is the one that will not come up in voltage and is soaking up more than 300mA / Battery #1 and #5 are also soaking up a lot of current, but w/o a low voltage (they look like they'll get to 13.6v) / Battery #2 charging by itself on BK, it started at ~11.5vdc @ 300mA …; It doesn't look like #2 is going to make it --> salvage / The other (5) in parallel 13.6vdc @ 1.5 amp limit (#1 & #5 are taking most of this); Now 13.6vdc @ 1.3amps dropping...				-					20190522
				~	13:15	~	14:50	TL3_6 batteries floating on BK_1 (#2 battery not included): 0.98amps dropping; Increased BK voltage to 13.7vdc (Heathkit target voltage); 1.2amps dropping rapidly … / 0.27amps; These (5) will be useable / "Married" to JC3 #13 Battery #20 (A21 TL6_5_B) to make a 6-pack; All (6) in parallel on BK_1, 13.7vdc @ 1.5amp limit, started at 0.44amps...					20190522
				~	15:10	~	15:20	315mA; all (6) placed on Heathkit (adjusted to 13.7vdc Fluke) with Wattmon_9 …; Heathkit says 14.1 vdc @ 430 mA; Wattmon says 13.7 vdc			L					20190522
		23					A7-25 A28-31	IMG					20190523
		25	Sa	~	06:25	~	07:40	6-pack continues on Heathkit (TL3_6 w/o #2 battery): I saw ~350mA a few days ago, but then it started hopping up to ~425mA, then back below 400mA / Now the Heathkit is at maximum current (0.5A) and pack is 13.51vdc (Fluke); Battery #4 is warm 86⁰F; This is the battery that had low OCV on 2/24/17 and 5/19/19 / If this continues it will have to be replaced ...; 12.75v, 88⁰F					20190525
				~	09:05	~	09:55	6-pack continues on Heathkit (TL3_6 w/o #2 battery): 12.72v, 91⁰F; This is draining the other 5 batteries; Removed battery #4 from Heathkit / 5-pack 13v and climbing …; 13.72v/260mA					20190525
				~	12:00			5-pack continues on Heathkit (TL3_6 w/o #2 & #4 batteries): 13.74v/240mA					20190525
		28	Tu	~	18:35	~	18:45	5-pack continues on Heathkit (TL3_6 w/o #2 & #4 batteries): 13.75v/215mA / Unknown BB BP7-12 from salvage pile (see S2/BK_1 rejuvenation) used to replace battery #4 (which goes to salvage) … / 6-pack I'm going to keep on the bench is now TL3_6 with #2 and #4 batteries replaced with other salvage; 13.75vdc on Heathkit @ 265mA including Wattmon_9					20190528
2020	May	31	Su					5-pack sent to salvage	WP5 S1					20200531
2021	Jan	16	Sa					[A30-31] Tripp Lite A30 moved from W storage to bench and 2nd battery connection attached (see RHS/L5) / Cheater cord to switchable 120vac (A30 won't be used for full-power testing) / A30 Float is 82.5v, which is good news as it is ~0.5v lower than A31 and this indicates that the usual Float voltages on these 3kva units may be a closer average to Trojan specs than I thought / A30 being used only to boost charge current, or if batteries have reached Float to keep it lower than A31's Float (by removing AC to A31)	L5 A31 B62-B67 IMG	Testing		B62-67					20210116
		18	Mo					After the end of the 2nd discharge test TL3_6 smoked when AC input power was applied: / TL3_7 AC Input ON (loads came back up) then TL3_6 AC Input ON ... audible "pop" and smoke began coming out of one of the UPSs / (not sure which one, but probably TL3_6); Disconnected all power (AC + Batteries) / Removed cover on TL3_6; An MOV (Metal Oxide Varistor) melted down in the back right corner where the AC input comes in, photos / It has shorted line to ground (I had the cheater cord attached properly, photo of male plug with line and neutral marked red and black) / This might be a relatively easy repair if we really need to get this unit operational again, as it s/b possible to remove the circuit board (but there are 8-9 connections to remove); TL3_6 reassembled, cover on and moved to W Storage	L5 A31 B62-B67 SSC TA2 IMG	Dead ! MOV		-					20210118

## A31
UPSs: A31	A					TL3_7: TrippLite SU3000RTXL3U					Charge and Test Milestones

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	Online 1 Hr >80% Load	Float > 24 hrs	Battery 5 mins No Load	Battery 5 mins >80% Load
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				! 3/4 LED	L	-	1/18/21	3/5/21	1/18/21	1/18/21
2015	Sep	1	Th					A30-31		Available	L	A31					20150901
2016					A25-31					20160901
	Nov	1	Tu					Moved to main shop; Labels "NVD 2015 #25" (7); Battery total 72.4 VDC (good) 12.0,11.9,12.1,12.0,12.2,12.1; Will not remove batteries to test/charge / Moved back to W side (brown table)					20161101
2017	Feb	25	Sa		08:50			Plugged in (1st charge in 1-1/2 years); LINE, LOAD, BAT LOW ...			L0					20170225
		26	Su		09:38			Unplugged (need to come back soon)			L			2/26/17			20170226
2018	May	18					A7-31	UFS					20180518
2019	May	19	Su					Battery six pack is 17.8 vdc total --> Salvage				-		-			20190519
		20	Mo					A7-25 A28-31					20190520
		23					A7-25 A28-31	IMG					20190523
2021	Jan	5	Tu					Moved from stack to main bench for testing setup for RHS; Cover removed, fan shrouds loosened	L5		L0					20210105
		8	Fr					Fabricated temporary connection from RHS batteries to TrippLite; TrippLite powered up w/o AC (some drain to batteries, not much); Load removed (no charger)	L5 B62-B67	Testing					20210108
				~	14:28			Temporary wiring of TrippLite to AC; Float 82.95v=6x13.825v which is 1.95v above Trojan recommendations (81.0v=13.5x6)	IMG			B62-B67					20210108
		10	Su					Powered down the TrippLite and removed power (AC and battery); Removed blue glue from a potentiometer near the rear battery connection entrance / Reapplied power and adjusted ... but it doesn't seem to affect the Float voltage at all (left it where it was as close as possible) / Conclusion at this point is that for RHS we'll have to live with a Float voltage that is slightly higher (82.95v=6x13.825v) than Trojan specs (81.0v=6x13.5)	L5					1/9/21			20210110
		11	Mo					Experimented with Equalization boost chargers MW_3/4 on RHS batteries and TL3_7 TrippLite; See RHS L5 for details/conclusions	L5					20210111
		15	Fr					Researched what is needed to access the Tripp Lite 3kva units via port(s); Connected ethernet cable and explored the web interface @ 90.0.0.125 (DHCP assigned) / Username admin, Password <blank>; Tested UPS with SNMPWEBCARD active/connected and Events setting of 'Shutdown when On Battery' after 6 minutes works / Tested w/o SNMPWEBCARD active and 'Shutdown when On Battery' does not occur; NOTE Events Controls don't function if SNMPWEBCARD is not connected / Logs are being retained through power OFF (card battery "OK"); Turned OFF settings to Shutdown when On Battery (6 mins) and when Battery Low (3 mins) / Set clock to synchronize with NTP server	L5 B62-B67					20210115
		16	Sa					Removed temporary battery wiring from TL3_7/B62-B67 and replaced with new assembly with (2) battery module connectors; Replaced cover on TL3_7	L5 B62-B67		L					20210116
				A30-31	L5 A30					20210116
				Load testing begins with TL3_7: (TL3_6 is OFF no AC); Bathroom space heater on high is 54% output; Heat gun on high is 50%; Total for both causes beep (109%) / Heat gun on low by itself causes switch to Bypass and General Fault (batteries had to be disconnected in order to reset it); Space heater + heat gun on low is 79% / Added 150w heat lamp and output load is 85% (perfect, probably at least as high as RHS current loads) / Noticed again that LED #3 of 4 in load "bar graph" is not lighting/dead (or it is very dim) / Discharge began at 15:05 and TL3_7 quit (shut off) at 16:33 (total discharge time 1 hr 28 mins) / Tripp Lite %SoC was way off, thinking it had some small batteries, it said we were at 0% capacity after only 8 mins / Lowest total battery voltage seen 67.2 ((11.2v equivalent) but this was 13 mins before it died / Restored AC, also turned on TL3_6 to speed recovery (it is more important to recharge quickly than to see how long recovery takes with only one UPS; Killed loads	L5B62-B67 A30 IMG SSC				1/16/21		1/16/21	1/16/21	20210116
		18	Mo					2nd Load test, same conditions as the first test on Sa1/16 @ 85% except this time 75% (Heat gun on low + space heater on big variac @ 99% of line, photo) / See white sheet notes for extreme details; Discharge began at 14:30; Quit at 16:10 (1 Hr 40 Mins) / 64.6 (10.77 equivalent) lowest bank voltage seen 12 secs before it quit; See TL3_6 for details on A30 self destruction when starting recovery / Reattached the batteries to TL3_7 @ 19:05 (recovery started)	L5 B62-B67 A30 SSC TA2 IMG WS				1/18/21		1/18/21	1/18/21	20210118
2021	Feb	24	We					Powered down the TrippLite and removed power (batteries delivered to RHS)	L5 B62-B67	! 3/4 LED		-		1/22/21			20210224
2021	Mar	3	We	~	14:50			Test UPS TL3_7 moved to storage; Salvaged batteries from RHS installed in TL3_7 and TL3_5 and Float rotation started; TL3_7 LED yellow BATT LOW; Float is 82.9v Fluke	L5			B41_46 B47_52		3/5/21			20210303
	Oct	1	Fr					Salvaged batteries from RHS --> Salvage (Midwest Scrap Management)	BR			-					20211001

## A32
UPSs: A32	A					APC_1: APC BR500

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2019	Jul	9	Tu					Acquired from Keith Jones of TurboNet while onsite at OSWT (Odessa South Water Tower) to install W100_3	L7	Available	L	Dead	20190709
		11	Th	~	04:45	~	08:35	Battery is swollen and ruptured (to salvage); Cleaned; Initial test AOK (on B54); This sheet and summary completed; Inventory stickers applied; Opened, dissassembled (photos) / Cut circuit board trace to beeper (easy to repair later if desired); Fabricated ~ 1 foot long Black and Red #10 AWG Stranded battery cables with 5/16" ring connectors and attached directly to PCB board / Drilled hole in side of case; Reassembled and tested (oops!, beeper still functioning, unit won't stay on line, error beeps)	IMG		L0	B54	20190711
				~	18:10	~	20:20	Disassembled, removed beeper and repaired trace; Sticker applied "Beeper Removed"; W100 Test Setup; No load wattage is ~4 watts! (much better than Liebert which was ~45 watts)		W100 Testing			20190711
		14					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)	IMG				20190714
		17		~	19:00	~	22:00	Installed cooling fan in APC (A32); Modified APC in W100 Test Setup (WP5, C2, S7, A10, 6-pack/Heathkit)					20190717
	Aug	1					After having finished DR tests at 50, 100 and 150w to as low as APC can go we now know the APC LVD value: 9.8 to 9.9v	WRD				20190801
	Sep	5	Th	~	10:00	~	12:30	27 TMX (B54) removed from W100 Test Setup for delivery to RW; T-105s installed in W100 Test Setup	WP5			B8,B11	20190905
		26					On or after 9/26/19: W100 Test Setup powered down (6-pack is so poor could not keep >=6 volts) and no longer being used	W10	Available	L	-	20190926
2020	Jun	13		~	17:15			Used for quick DR tests of WP6-WP10 (B57-B61)	W10	W100 Test		B57-B61	20200613
		15	Mo		03:00			Wattmon_10 powered down (APC attached to WP10/B61 but hasn’t been used since Sa6/13)	WP6-WP10	Available		B61	20200615
2021	Jan	8	Fr					Bench Testing for Turbonet and Richmond High School (RHS) UPS Battery Contract: APC_1 in the background	IMG				20210108
		16	Sa					Seen in videos and photos of TurboNet/RHS bench testing					20210116
	Oct	19	Tu					Waiting on the bench to use for TurboNet MikroTik project (Schauer 2512, Traco DC-DC)	W10		L0	-	20211019
		24	Su					On the bench for use in testing Schauer JAC2512 (SBC_1)	BC6	Applied		B68 B69	20211024
				Video sent to Pavel via Viber	IMG				20211024
	Nov	13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup; Last Use of APC Load Setup					20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)					20211114
	Dec	4	Sa					ITECH Electronic Load was received yesterday; APC load setup dismantled and stored	DRD	Available	L	-	20211204

## B0
Batteries: B0	A					Old_Honda: Standard Battery B10

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Failing	L	S1	-
2010	Feb					Purchased (as evidenced by punched date sold 'FEB 10'); Probably some auto parts store; Bought to fit 1985 Honda.		Available	L			#N/A
Since it was purchased:					I may or may not have put it on a charger. I never installed it in the Honda, which was sold Feb 2012. It was in the shop garage for a long time, and so it got hot for long periods of time (80 to 90⁰F). Self-discharge brought it down below 9 OCV multiple times, but otherwise this battery has been used only for a few deep discharges (in 2015 it was used at RW a few times while the 27TMX was being charged at the shop, and it probably got down below 50%SoC). I neglected it, it didn't get charged very often, perhaps once per year if at all, and I know that when I was in Ukraine it was probably not being charged. When I got back from Ukraine I brought it into the main shop, under the bench. I started to trickle charge it more often on various and different chargers (search this workbook for "Honda ..." to find mentions of it being charged, sometimes in parallel with other batteries). Due to that at times it saw Absorption voltages for short periods (but nothing more than you'd see in an automobile). It did get occasional use, but only for a light load for a short time. In summary, it has been neglected by self-discharge, and that kind of damage brings its capacity into question. It would probably be very useable for light loads, but certainly would not have the Cranking Amps that it had when it was new. The last time I remember trickle charging it was Fall of 2018 sometime.		Neglected		Various	Sometimes	#N/A
2019	May	18	Sa					This history sheet created					20190518
				~	04:50	~	06:05	~9 OCV; Charging on BTJ_1 …; Removed BTJ_1 and after about 15 mins 12.4 OCV (very good for only an hours' trickle charge)				BC2		20190518
				~	06:18			Applied inventory sticker; Back on trickle charge (BTJ_1)		Available				20190518
		19					Photo of Fluke, BK & UPS Battery Charging - shows Old_Honda and BTJ_1 underneath the bench	IMG					20190519
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1					20190708
		14					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)					20190714
2020	Jan	23	Th	~	10:10			Charger BTJ_1 removed (to charge Gravely)				-		20200123
	Jun	13	Sa	~	04:45	~	08:00	Moved from under bench to where the 6-pack was in the DR Test Setup; OCV 11.07 to 9.9 (very self-discharged, 0%SoC, very slight load dropped it down); BK Charge Bulk to 14.3v (very quick, <3 mins); Absorption at 14.1v for 3 Hrs (1.47 Amps at end); Float 13.7v (after ~3 mins ~0.76 Amps, too much for Heathkit)	WP6-10	DR Bench		S2		20200613
				~	14:00			Float charge now ~0.4 amps; Transferred to Heathkit, set float 13.7 (13.6-13.8v); It probably doesn’t have very much capacity, but it s/b enough to keep the Wattmons and DR Test Setup fans going through a power failure		Bench		S1		20200613
		15	Mo	~	04:15			Float charge now ~180mA at 13.73v Fluke (it has formed up very well)					6/14/20 +	20200615
2021	Jan	8	Fr					Bench Testing for Turbonet and Richmond High School (RHS) UPS Battery Contract: B0 in the background (kept in Float on Heathkit)	IMG					20210108
		16	Sa					Seen in videos and photos of TurboNet/RHS bench testing					20210116
	Oct	24	Su					Video sent to Pavel via Viber					20211024
	Nov	13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup					20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; T-105s in recovery from deep discharge; Overhead lights off (dark)					20211114
	Dec	4	Sa					Various discharges for testing newly arrived ITECH Electronic Load; I hit it with ~20a discharge for 10-15m before voltage plummeted <9v (~4 AH discharge); B0 might have been a 30AH battery when new (C/100); I will, of course, charge it back up (with BK to help to 14.3v Bulk, 14.1v Absorption, then Heathkit Float ~13.7v)	Z17				12/5/21+	20211204
2022	Jan	8	Sa					Float 13.85-13.88vM (~13.8vF equivalent) @ ~550mA (Heathkit, near maximum possible); No load; Ambient ~25⁰C, Battery ~27⁰C; Float voltage is at high end of desired range (13.6-13.8v) and Float charge current is higher than I've ever seen it (usually see <200mA); Lowered Float to ~13.75vM (~13.68vF equivalent) @ ~460mA					-	20220108
	Feb	17	Th					Float 13.65vM (~13.6vF equivalent) @ 475mA; No Load	DRD					20220217
		24	Th					~13.6vM; ~0.56aE No Load (battery is using way too much charge current and is in failure mode); Problems started after the heavy discharges on Sa12/4/21; Concerns about Heathkit also noted		Failing		S1		20220224
	Mar	1	Tu					No-load charge current 0.56aE (maximum Heathkit can do); Concerns about Heathkit also noted; <12v no load when Heathkit is off (TODO "Replace B0")					20220301
	May	26	Th	~	10:00	~	19:15	(Preparing Schauer BC7); Heathkit is not charging; Added BK in parallel, set 13.6v/5.1a; Heathkit OFF ...; Heathkit disconnected from B0 (now using BK direct to #12 AWG Red/Blk)	T48S S1 IMG			S2		20220526
		27	Fr	~	13:25	~	16:00	BK charge is ~2.1a erratic (with ~600mA load from W10 and Engel fans) ...; B0 is warm, ~33⁰C, right side ~40⁰C (Fluke IRT); BK output ~2.2a; B0 has a shorted cell; To prolong life set BK 13.40v	T48S					20220527
	Jun	2	Th	~	03:00			B0 is very warm, in thermal runaway failure: BK set 13.4 and providing ~3.7a (of which <0.6a is Engel fans and W10); Lowered BK setting to 13.0v, now ~1.6a					20220602
		11	Sa					BC7 BTS test setup broken down: B0 removed from BK and placed on Heathkit: T2 UPS, No load ~13v ~320mA (with circulating fans ~480mA); Lowered setting to ~12.7v (no load ~10mA); B0 will have very small capacity but useful for short power failures	T48S BC7 S2			S1		20220611
	Sep	17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG					20220917
	Oct	5	We					W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 IMG WP11					20221005

## B1
Batteries: B1	A					20150422: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Sold	L7	WP4	4/6/21	4/5/21	100%	100%
2015	Apr	22	We					Drove to Columbia and picked up the battery, rec'd $26.00 core return credit for another old battery or batteries; 224 miles @ $0.54	TSP	New	L					20150422
				%SoC Low Point estimated based on self-discharge of 2.5% over 5 months; Highly likely to have been put on float charge in shop until needed; 20150423 Trojan_Application_Specs.pdf	LIB	Float		BC1	Continuous		88%		20150422
		30					Installed at RW (Rayville Water Tower); Photos of initial installation with Mark Webb and Keith Jones	IMG	Applied	L1	C1	4/30/15			100%	20150430
				This setup was deficient: I only had one 100W solar panel, and as I recall, TurboNet system went down multiple times, where the Battery %SoC probably had dropped to 0% (but I didn't know exactly how deep because the Wattmon had not yet been installed and running correctly); The TurboNet 12 to 24vdc converter probably drops out at about 9 or 10 volts, and it did this several times, so this battery was DEEP CYCLED; Back and forth to the shop for Trace charging (while TurboNet was being run on Old_Honda/B0), then reinstalled; 20150704 27TMX_Trojan_Data_Sheets.pdf	LIB					20150430
	Jul	6					Photo at RW	IMG					20150706
		15	We					Purchased (2) T105 Trojans for RW (see 20150715); 20150715 WP_DeepCycleBatteryStorage_0512.pdf	B2 B3 LIB					20150715
		17	Fr					Removed permanently from RW (as can be seen from #2 [RW] [SD Card #1] Battery Status Graph)					YES (3-5x)		0% (3-5x)	100% (3-5x)	20150717
				Off and on float charge at shop after that…		Float	L	BC1	Continuous			100%	20150717
	Dec	22	Tu					Watered @ shop (probably had been checked before then, but not noted).					12/22/15			20151222
				Continued off and on float charge at shop…					20151222
2016	Apr	21					Video and photos of batteries under the bench	IMG					20160421
	May	24	Tu					Absorption charge for about 1 hour (14.35 VDC) applied while charging 20150808 set					100%	20160524
	Jun	13	Mo		14:05			Installed at RW		Applied	L1	C1	6/13/16				20160613
		16	Th	~	10:40		15:22	Removed from RW; Started charging on Trace		Float	L	BC1	Continuous		41%		20160616
	Nov	30	We	~	09:40			Watered (down about 3/16")					11/30/16			20161130
2017	Jan	19	Th					Used onsite at RW to power soldering iron		Waiting Charge			1/19/17		98%	100%	20170119
		20	Fr					Charging on trace (with 4 batteries from RW) …		Bulk			Continuous				20170120
		21	Sa	~	14:15		15:15	Absorption …; Float		Float					20170121
		22	Su					Watered (down less than 1/8")					1/22/17			20170122
	Mar	29	We	~	17:00			Absorption/Equalization charging on trace (starting at ~13v in parallel with 4 batteries from RW) …		Equalization					20170329
		31	Fr	~	18:45			Float (~48 hours climbing to absorption 14.8v)		Float					20170331
	Apr	1	Sa	~	07:45			Watered: ~1/16" or less					4/1/17			20170401
	May	6	Sa					Removed from float; loaned to Travis and Jen (with Trace)		Applied	Jen		5/6/17			100%	20170506
		7	Su	~	13:00	~	16:20	Returned to shop, battery dead, charging …; Mostly charged, returned to Travis and Jen (with Trace)					0%	97%	20170507
		9	Tu	~	09:30	~	14:00	Returned to shop, battery ~12.6 OC, charging …; Float		Float	L		Continuous		85%		20170509
		15	Mo					Watered: ~1/8" or less [in the past 6 days the Trace switched to Absorption several times due to short power losses]; Placed in parallel with other batteries; Absorption … float					5/15/17			20170515
	Nov	2	Th	~	16:15			Watered: ~3/8" (much lower than I thought it would be, they've just been floating here in the shop for 7 months)					11/2/17			20171102
2018	Feb	25					Photos of WISPer#2 test setup	IMG		L0	C4					20180225
	Mar	4	Su					During the past few days I ran it down to maybe 50% SoC (not sure, bench Wattmon not setup very good for this); Recharged; Watered, cells 3 and 5 of 6 (from Neg. to Pos.) needed ~1/16", other cells OK (no water added to them)		WP Testing			3/2/18	3/4/18	50%	100%	20180304
		5					Photos of WISPer#2 test setup (WP2, Delta 150W, Genasun_3 no cover, fan taped to bench, BK for boost to Delta, W9)	IMG				3/5/18				20180305
		13					W100 Testing (Trace used as CW load, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK)					20180313
		14	We					Several Absorption cycles in the past week, but has been kept close to 100% charged; WISPOWER #2 discharge testing yesterday and today to 50% SoC as measured by 12.00v O.C. rest voltage (Fluke) [Wattmon SoC=42% but capacity was set as 100 AH with no Peukert Constant, and by O.C. rest voltage this 27TMX appears to have about 115 AH capacity at longest hour rate, which is very good for a 3 year old battery, as it is rated at 85AH (5 hrs) or 105AH (20 hrs)]; ... hiccup testing charge/discharge in 42-48% Wattmon SoC region ... discharged to ~40% SoC by OCV rest 11.90v (34.95% Wattmon SoC); more charge/discharge hiccup tests; fully recharged overnight (on Genasun)					40%	100%	20180314
		15	Th	~17:00	17:00	~	00:00	WISPOWER #2 discharge test to ~35% by OCV (11.80v @ 2W load, very close to OCV); Wattmon SoC was ~22% (105 AH capacity, 1.17 Peukert Constant, not very accurate); Photos 'W100 Testing' (Trace used as CW load, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)	IMG				NO: ~10 Hrs		35%		20180315
		16	Fr		00:00			Started charging on Genasun …					Continuous				20180316
		17	Sa	~	20:40	~	22:45	… Genasun finally reached Absorption …; Genasun Float, ~6% ratio (6W net charge) …					20180317
		18	Su	~	06:00	~	22:45	… Genasun float approximately 3% ratio …; Genasun in float for ~24 hours, 13.4v					100%	20180318
		20					W100 Testing, calibration of C252 (WP2, Delta 200W, Genasun mounted under fan, BK, Trace being used as CW load)	IMG					20180320
		29	Th	~	17:05			Removed from WP Testing and placed in parallel with Old_Honda on ENC-180-12 (14.2v Absorption … 13.4v Float)	B0	Charging	L	BC3					20180329
	Apr	3	Tu	~	06:15	~	07:15	Removed from float on ENC-180-12, Electrolyte levels all low ~1/8", corrected …; Placed on DR test setup for WISPer (WP) Testing	WRD	WP Testing	L0	C4		4/3/18		100%	20180403
	May	5	Sa	~	05:45			Removed from WP Testing (was Float)		Available	L		5/5/18				20180505
		7					Rec'd order for W100_2 from TurboNet	TW2-3 WP3	Slated for W100_2					20180507
	Jun	10					Charging on BTJ_1 (in parallel with Old_Honda/B0)				BC2	Continuous				20180610
		15	Fr	~	04:45			Moved from under bench to bench to power Wattmon_9 (BTJ_1)	W9	Applied					20180615
	Aug	9	Th					Being charged by W100_2; Slated for W100_2	WRD		L0	WP3					20180809
		12	Su	~	06:50			DR Test concluded; Disconnected from W100_2					8/12/18		50%	100%	20180812
		13	Mo					Finished product photos; Electrolyte Level Checked, all cells down ~1/8"; Installed at RW	IMG	Sold	L1		Continuous	8/13/18			20180813
2019	Apr	29	Mo		12:05		12:50	Travel & onsite at RW: Battery watered, only down ~1/8", I added a generous ~3/16"; Checked AC outlet & installed cover plate / Removed the last of the Wattmon stuff; Cleaned W100 fan/filter (compressor); Ant trap installed					4/29/19			20190429
	May	15	We		08:38		09:28	Power outage including Rayville, Wood Heights …; Power restored after 50 minutes; Load during this time was about 28 Watts/~2.3 Amps; Therefore battery discharged to ~98 %SoC					5/15/19		98%		20190515
		16	Th					Batteries s/b fully charged after the power outage yesterday					Continuous				20190516
	Jun	27	Th	~	09:00			RW down for sandblasting and painting (30-90 days?); Equipment box and battery moved to the shop	IMG		L	-	6/27/19			100%	20190627
		29	Sa	~	09:00			Moved to bench for W100 testing; Quick check of water levels and they look good	WRD		L0	WP5		6/29/19			20190629
		30	Su		14:00		21:50	1st Series Test, Discharge started …; Discharge to 34.7% SoC as per man'f specs @ 12v average					6/30/19		35%		20190630
	Jul	1	Mo		11:39			1st Series Test finished; Float					100%	20190701
		2	Tu		11:00		12:59	2nd Series Test, Discharge started …; Test failed due to W10 reboot; Discharge to 84.5% SoC as per man'f specs @ 12v average					7/2/19		85%		20190702
				17:36			WP4 transition to Float					100%	20190702
		3	We		09:00	~	15:19	3rd Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190703
		4	Th		02:07			WP5 transition to Float					100%	20190704
				14:30		18:31	4th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190704
		6	Sa		05:52			WP5 transition to Float					20190706
				11:02		13:02	4th Series Test @ 300w Concluded; 2 Hr Equalization with BK_1 …; Equalization ended, continues in Float					100%	20190706
		7	Su					Electrolyte level checked and AOK					7/7/19	7/7/19			20190707
				08:00		21:12	5th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average	WRD					50%		20190707
		8	Mo		04:23		06:40	WP5 transition to Float; Started Equalization …; Ended 30 Min Equalization with BK_1, continues in Float					100%	20190708
				10:18		23:31	6th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190708
				W100 Series Test setup: / WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG					20190708
		9	Tu		06:30	~	12:15	WP5 transition to Float …; WP5 charger disconnected (Series Test setup disassembled)	WRD			-				100%	20190709
				12:45	~	17:25	Loaded Subaru; Travel to Lexington, followed Keith to Odessa South Water Tower (OSWT, 9271 Donaldson Rd, Odessa, MO 64076) / Onsite 14:05-15:25, Helped Keith install W100_3 (WP4) and B1; Photos; Netonix is currently using 24-28w; Return travel	IMG		L7	WP4	Continuous				20190709
		10					From/to Keith Jones: "Latest power usage" (screenshot); "Seems to bounce between 25-33" / "Assuming 29 watts is the average the battery will go 24 hours to 50% discharge (a safe discharge for the battery) ... Or 48 hours if you don't mind abusing the battery (100% depth of discharge, totally dead)."; "Thanks Jeff"; "Be sure to set a notification SMS from the Netonix if the battery voltage drops below 13.0 volts as otherwise you may not know the AC power is off until 48 hours after happens."; "Gotcha thanks again"	SMS					20190710
2020	May	7					Mark reports that Keith was onsite at OSWT "in the past month" (phone call while returning from BFMS in KC)	L7					~4/15/20			20200507
		8					Keith reports that on that visit "no water was needed" (discussion while onsite at LWT) / I said I had a hard time believing that, but it could be it was cool enough after 7/9/19 installation that little water was used					~4/15/20			20200508
2021	Apr	5	Mo	~	14:45	~17:15		Onsite at OSWT for the Backup Power Supply Maintenance Program; See L7 for details; 25 minute discharge with 17 watt load to about 99.5 %SoC	TM21S SMS		L7	WP4	4/6/21	4/5/21	100%	100%	20210405

## B2
Batteries: B2	A					20150715_1/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Sold	Salvaged	-	2/19/16	1/1/17	88%	100%
2015	Jul	15	We					[B2-3] Drove to Kansas City and picked up the battery set	BFMS TSP	New	L					20150715
				[B2-3] Highly likely to have been put on float charge in shop until needed; 20150715 WP_DeepCycleBatteryStorage_0512.pdf	LIB	Float		BC1	Continuous				20150715
		17	Fr					[B2-3] Battery Status Graph on #2 Wattmon [RW] [SD Card #1] shows this is the date of installation at RW		Applied	L1	C1	7/17/15	Probably		100%	20150717
	Sep	3					[B2-3] Onsite at RW with Juliya	IMG					20150903
		16					[B2-3] Onsite at RW with Juliya (Sasha's iPhone)					20150916
	Oct	25	Su					[B2-3] %SoC Low Point from #2 [RW] [SD Card #1]					85%	100%	20151025
	Nov	1	Su					84%		20151101
		6	Fr					84%		20151106
		19	Th					66%		20151119
		21	Sa					62%	77%	20151121
		27	Fr					57%	84%	20151127
		30	Mo					[B2-3] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		54%	79%	20151130
	Dec	17	Th					[B2-3] Installed at RW		Applied	L1	C1	12/17/15	Probably		100%	20151217
		27	Su					[B2-3] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		51%	100%	20151227
2016	Feb	19	Fr					[B2-3] Installed at RN		Sold	L2	C5	2/19/16	Probably		100%	20160219
	Mar	16					[B2-3] Onsite at RN (to install web relay)	IMG					20160316
	Apr	19					[B2-3] %SoC Low Point from RN Battery Status Graph (lowest point as of 6/17/16 … I started using the correct Peukert Constant and AH Capacity soon after this date)					88%	100%	20160419
	Jul	16	Sa					[B2-3] Onsite at RN: Applied inventory stickers (20150715-1/2, 20150715-2/2); Photographed all stickers and man'f/finishing date codes	IMG					20160716
				Electrolyte Levels: all cells down ~3/8" to 1/2" but ~1/4" above plates; Water added					7/16/16			20160716
	Aug	15	Mo					Onsite at RN: watered batteries; This individual battery needed ~1/8" of additional water					8/15/16			20160815
	Oct	18	Tu					[B2-3] Onsite at RN to reset Ubiquiti and watered batteries: they were all about 3/16" low.					10/18/16			20161018
2017	Jan	1	Su					[B2-3] Onsite at RN to troubleshoot Wattmon connection difficulties: Butch watered the batteries, he said they were all about 1/8" low					1/1/17			20170101
2019	Jan	18	Fr	~	10:40			[B2-3] Mark Webb & Keith Jones onsite at RN: no power, batteries are dry					20190118
		21	Mo		08:21		08:39	[B2-3] Reason Swafford called: "I solved the problem."; He bought two "equivalent" batteries, not Trojan, but flooded, paid $130 each but had to turn in the two Trojans as cores; They don't yet have internet, he says Mark said the Tough Switch needs to be replaced / I explained again the need for (4) batteries instead of (2), and discussed the monitoring system, which, if they aren't interested in using they should disconnect			Salvaged	-					20190121

## B3
Batteries: B3	A					20150715_2/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Sold	Salvaged	-	2/19/16	1/1/17	88%	100%
2015	Jul	15	We					B2-3	BFMS TSP	New	L					20150715
				LIB	Float		BC1	Continuous				20150715
		17	Fr					Applied	L1	C1	7/17/15	Probably		100%	20150717
	Sep	3					IMG					20150903
		16					20150916
	Oct	25	Su					85%	100%	20151025
	Nov	1	Su					84%		20151101
		6	Fr					84%		20151106
		19	Th					66%		20151119
		21	Sa					62%	77%	20151121
		27	Fr					57%	84%	20151127
		30	Mo					Float	L	BC1	Continuous		54%	79%	20151130
	Dec	17	Th					Applied	L1	C1	12/17/15	Probably		100%	20151217
		27	Su					Float	L	BC1	Continuous		51%	100%	20151227
2016	Feb	19	Fr					Sold	L2	C5	2/19/16	Probably		100%	20160219
	Mar	16					IMG					20160316
	Apr	19					88%	100%	20160419
	Jul	16	Sa					IMG					20160716
				Onsite at RN: Electrolyte Levels: All cells down ~3/8" to 1/2" but ~1/4" above plates; Water added to cell #1, but I ran out of water on cell #2, and none added to cell #3					Partial			20160716
	Aug	15	Mo					Onsite at RN: Watered batteries; This individual battery cells #2 and #3 yet ~1/4" above plates (not in danger) and added ~1/4", cell #1 only needed ~1/8"					8/15/16			20160815
	Oct	18	Tu					B2-3					10/18/16			20161018
2017	Jan	1	Su					1/1/17			20170101
2019	Jan	18	Fr	~	10:40					20190118
		21	Mo		08:21		08:39				Salvaged	-					20190121

## B4
Batteries: B4	A					20150808_1/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Applied	L	A3-4	-	5/16/23	0% by man'f specs. / 64% by OCV	100%
2015	Aug	8	Sa					[B4-5] Drove to Kansas City and picked up the battery set; Also purchased some battery cable connectors	BFMS TSP	New	L					20150808
				[B4-5] Highly likely to have been put off and on float charge in shop until needed; Slated for Subaru Aux System (working on SAPS boxes)	MA2 SSRP	Float		BC1	Continuous				20150808
	Nov	30	Mo					[B4-5] Installed at RW; %SoC Low Point estimated from ~2 months since manufacturer at 2.5% self discharge per month		Applied	L1	C1	11/30/15	Probably	95%	100%	20151130
	Dec	17	Th					[B4-5] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		52%		20151217
		22	Tu					[B4-5] Watered					12/22/15			20151222
		27	Su					[B4-5] Installed at RW		Applied	L1	C1	12/27/15				20151227
2016	Jan	10	Su					[B4-5] %SoC Low Point (from #2 [RW] Battery Status Graph)					60%	98%	20160110
		27	We					45%	83%	20160127
	Mar	16					[B4-5] Onsite at RW (to install web relay)	IMG					20160316
	Apr	22	Fr					[B4-5] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		55%	100%	20160422
		29	Fr					[B4-5] Photos under the bench; Installed at RW	IMG	Applied	L1	C1	4/29/16	4/29/16			20160429
	May	6	Fr					[B4-5] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		46%		20160506
		13	Fr					[B4-5] Installed at RW		Applied	L1	C1	5/13/16			100%	20160513
		23	Mo					[B4-5] Removed from RW; put on Trace @ Bench		Float	L	BC1	Continuous		38%		20160523
	Jun	1	We					[B4-5] Installed at RW		Applied	L1	C1	6/1/16			100%	20160601
		13	Mo		14:05		14:33	[B4-5] Removed from RW; put on Trace @ Bench		Bulk	L	BC1	Continuous		32%		20160613
		14	Tu					[B4-7] Probably reached float early AM (after Absorption period ended)		Float					20160614
		15	We					[B4-7] Electrolyte levels checked (some cells down a tiny bit); Loaded for installation at RW	Slated for RW		Garage		6/15/16	6/15/16		100%	20160615
		16	Th	~	10:40			[B4-7] Installed at RW	IMG	Applied	L1	C1					20160616
	Nov	27	Su	~	12:00			[B4-7] Removed from RW		Uncharged	L				0%		20161127
		28	Mo	~	10:00	~	10:30	[B4-7] OC voltages are 5.7 to 5.8 …; On Trace @ Bench …		Charging		BC1	Continuous				20161128
		29	Tu		17:10			[B4-7] Still in Bulk @ 14.57v climbing [Note added 11/30/16: Trace was set for Flooded, which is 14.7v before switching to Absorption for 1 hour] …					20161129
		30	We	~	02:00			[B4-7] I heard the Trace switch to float		Float					20161130
				~	09:30	~	10:00	[B4-7] Power to Trace OFF (batteries are loaded only with power needed for Trace standby) …; Watered (all 4 batteries down ~1/4")					11/30/16	11/30/16			20161130
				10:22	~	11:17	[B4-7] Charging (Trace set for 14.7v Absorption) …; Float					Continuous				20161130
	Dec	16	Fr	~	14:00			[B4-7] Installed at RW, B4-5 in main box; Photos	IMG	Applied	L1	C1-2	12/16/16			100%	20161216

2017	Jan	3	Tu	~	11:30		12:55	[B4-7] Removed from RW …; On Trace		Charging	L	BC1	Continuous		33%		20170103
		4	We				17:09	[B4-7] Float		Float					20170104
		5	Th					[B4-7] Watered: 0 to 1/8" (some cells needed no water, most of them ~1/16", and a few 1/8")					1/5/17			20170105
		19	Th					[B4-7] Installed at RW, B4-5 in main box; Photos	IMG	Applied	L1	C1/2/6	1/19/17			100%	20170119
	Mar	29	We	~	08:35	~	09:35	[B4-7] Removed from RW ...; put on Trace @ Bench [%SoC Low Point 0.7%, fairly accurate, as it was 10.9v under 25w load]		Bulk	L	BC1	Continuous		1%		20170329
		31	Fr	~	18:45			[B4-7] Float (~57 hrs in bulk)		Float					20170331
	Apr	1	Sa	~	07:50			[B4-7] Watered: ~1/8" (~2/3 syringe)					4/1/17			20170401
	May	6	Sa					[B4-7] Removed from float		Available			5/6/17			100%	20170506
		15	Mo					[B4-7] Absorption … Float		Float			Continuous		99%		20170515
	Nov	2	Th	~	16:15			[B4-7] Watered: ~3/8" (much lower than I thought it would be, they've just been floating here in the shop for 7 months)					11/2/17			20171102
		3	Fr	~	16:30			[B4-7] Installed at RW		Applied	L1	C1/2/6	11/3/17			100%	20171103
	Nov	28	Tu	~	15:30			[B4-7] Removed from RW …; Watered when discharged (down ~1/8")		Charging	L	BC1	Continuous	11/28/17	25%		20171128
		30	Th					[B4-7] Electrolyte level checked: OK, maybe 1/16" higher than needed (charging raises the level ~ 1/8")		Float				11/30/17			20171130
	Dec	22	Fr	~	14:15			[B4-7] Installed at RW		Applied	L1	C1/2/6	12/22/17			100%	20171222
		29	Fr	~	14:30			[B4-7] Removed from RW and subsequently put on charge (very cold weather: had to swap due to freeze potential coming up this weekend) / 66% SoC Low Point (11.8v under load at 15⁰F)		Charging	L	BC1	Continuous		66%		20171229
2018	Jan	15	Mo	~	12:00			[B4-7] Electrolyte level checked: OK; Installed at RW		Applied	L1	C1/2/6	1/15/18	1/15/18		100%	20180115
	Feb	24	Sa	~	09:30			[B4-7] Removed from RW (and subsequently put on Trace); %SoC Low Point as per Wattmon 26.0%, but unable to carry Netonix load since last night, and reached 9.1v under only the Wattmon's load (2W); Consider downgrading total AH capacity of these batteries from 450AH to 340AH (about 75% of new)		Charging	L	BC1	Continuous		0%		20180224
	Mar	13	Tu					[B4-7] Trace removed for use as Constant Wattage load on WISPOWER #2 Testing		Available			3/13/18			100%	20180313
		17	Sa			~	00:10	[B4-7] Fluke OCV 6.34,6.36,6.37,6.35, as per Trojan Data Sheet Percentage Charge is 95,98,100,97% / Placed on Mean Well ENC-180-12 battery charger, set to Flooded (14.2 Absorption, 13.4 Float, not timed, goes to Float when current is 10% of maximum) ...		Charging		BC3	Continuous		98%		20180317
		19	Mo	~	13:00	~	15:00	[B4-7] … ENC yet in Absorption (14.22v, for ~2.5 days); Briefly lifted battery connection between B4 and B5 and ENC switched to Float …; 13.43-13.44v / Electrolyte Level Checked, OK, no water added		ENC Float				3/19/18			20180319
		29	Th	~	13:05	~	13:50	[B4-7] Removed from ENC Float …; Installed at RW		Applied	L1	C1/2/6	3/29/18			100%	20180329
	Apr	24					[B4-7] Photos of current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery)	IMG					20180424
	Jul	20	Fr					[B4-7] Genasun_5 (C6) and 3rd panel (P_3) removed from RW; Batteries began a slow decline until pulled 8/13/18				C1-2					20180720
	Aug	13	Mo					[B4-7] Onsite at RW 09:15; AC OK; Photos (before); Removed (4) T-105s and battery box; Photos (after)	IMG	Available	L				13%		20180813
		21	Tu	~	05:00	~	05:30	[B4-7] Cleaned; VOC B4=5.675, B5=5.71, B6=5.66, B7=5.65 (~15% SoC by chart in hallway) ...; Parallel/Series VOC 11.34v (~13% SoC by chart in hallway) / Charging on Trace				BC1					20180821
		23	Th	~	00:00			[B4-7] Approximate time when reached float					Continuous			100%	20180823
		28	Tu					[B4-7] Electrolyte Levels Checked, all cells down about 3/16" (5-1/2 months); Stopped charging with Trace (just Trace load to operate)					8/28/18	8/28/18			20180828
		29	We					[B4-7] Charging on Trace (to obtain another absorption cycle)					99%		20180829
	Nov	2	Fr	~	06:00	~	06:45	[B4-7] Removed from Trace ...; Charging on ENC (Bulk, Circuit T1, which is yet backed for short power failures … 20 mins then I triggered Float)				BC3	Continuous			100%	20181102
2019	Mar	26	Tu	~	20:00			[B4-7] 1-2 second power failure and T1 UPS did not keep it up, so ENC started Bulk/Absorption (flashing orange)					20190326
		27	We			~	02:40	[B4-7] ENC struggling up through ~14.2 vdc; Triggered float by lifting one pair briefly; Now flashing green					20190327
		29	Fr					[B4-7] Removed from ENC; Watered, all cells down ~1/4"			L0		3/29/19	3/29/19			20190329
		30	Sa					[B4-7] Attached to CP_1	IMG	Applied		A1					20190330
		31	Su				20:30	[B4-7] Moved to high shelf in rear room; Load testing to maybe 85% SoC; Attempted Equalization charge with BK_1 …; 26.8vdc			L	S2 A1			85%		20190331
	Apr	1	Mo		06:30		07:15	[B4-7] 29.7vdc (Trojan specs. for Bulk/Absorption 29.64vdc, it took about 8 hrs to rise to this voltage, I can hear the outgassing bubbles) … / 29.68vdc (not rising), 7.38,7.41,7.46,7.42vdc (-0.51,-0.10,+0.57,+0.03%)				S2					20190401
				08:10		08:20	[B4-7] 29.64vdc falling slowly, 7.37,7.40,7.45,7.41vdc (-0.51,-0.10,+0.57,+0.03%) nothing has changed ... / 29.63vdc, terminated "equalization" (BK_1 doesn't have enough power to reach full equalization of 32.4vdc); Spot check of Electrolyte Level and AOK					4/1/19			20190401
				08:35		08:53	[B4-7] BK_1 set 29.64vdc (Absorption) and 3.373amps (maximum allowed) …; It is obvious it could stay like that for hours, terminated --> Float (27.1vdc)				A1	Continuous			100%	20190401
				[B4-7] Notes on Absorption/Equalization charging of (4) T-105s in series (B4-B7) using BK_1: Best to do this after a power failure, or twice per year; There's probably not enough power to reach Equalization of 32.40vdc; OVP will not shut it off (it only keeps you from setting a higher voltage); Set Equalization 32.40vdc/3.086amps with a solid connection; Once it reaches 29.64vdc (Absorption) hold for 2 hours					20190401
		27	Sa		14:38		15:55	[B4-7] Power outage including entire area (Wood Heights, Lawson, Excelsior Springs); Reduced load to about 250 watts and left for town; No problems / Probably used about 12.5 AH (~5% of battery capacity) during 1-1/4 hour outage					4/27/19		95%		20190427
		28	Su		08:42	~	14:20	[B4-7] 26.22 vdc (charging with CP_1); Absorption/Equalization (BK_1 32.40vdc/3.086amps) … / CP_1 shut itself off somewhere above 30.00vdc (battery overvoltage protection)				S2 A1					20190428
				15:10		15:18	[B4-7] New settings for BK_1 30.00vdc/3.333amps; Started at 27.2vdc …; 30.00vdc and because we've done enough of this shut it down to float				A1	Continuous			100%	20190428
	May	15	We		08:38		09:28	[B4-7] Power outage including Rayville, Wood Heights …; Power restored after 50 minutes / Load during this time was about 385 Watts/~16 Amps (T400s being used during entire time); Therefore batteries discharged to ~94 %SoC					5/15/19		94%		20190515
				09:44		15:10	[B4-7] Bulk/Absorption/Equalization (BK_1 30.00vdc/3.333amps); Started at 25.5vdc …; 29.7vdc (planning on continuing for 2 hrs) …				S2 A1					20190515
				17:12			[B4-7] … 29.9vdc; BK OFF				A1	Continuous			100%	20190515
		16	Th					[B4-7] DE_1 (S3) adjusted to 27.0vdc and installed in parallel with CP_1 to speed return to float after a power failure				S2 A1					20190516
				[B4-7] CP_1 (A1) removed and discarded (too damaged to fix); Batteries are floating on DE_1 (S3)				S3					20190516
				~	23:45			[B4-7] Attached to PC_1 (A4); Float is 27.3 to 27.4vdc				S3 A4					20190516
		17	Fr	~	05:00			[B4-7] Also attached to PS700_2 (A3): There are 3 float chargers, the Liebert has the highest float voltage at ~27.5vdc, the PowerCom is a little lower at 27.3 to 27.4vdc, and the Delta is set for 27.0vdc; With all 3 chargers running float is sometimes 27.6vdc; Note that the Delta cannot put out full power below 27vdc, as there it will be in hiccup mode; Therefore, fully depleted batteries are not being helped much by the Delta, we need to use a smart charger for bulk which is not constant voltage, such as the Genasun, which is maximum current until we reach Absorption.				S3 A3 A4					20190517
				06:10		06:40	[B4-7] Simulated power failure test with near maximum loads on Liebert and PowerCom (T400s/T450s, monitors, emergency lights, Trace/SAPS in Subaru, anything I could easily set up, kept it going); Tried to turn on JAK2, but PowerCom cannot handle JAK2 starting up with everything else on; turned off some unessential stuff to try starting JAK2 again, but PowerCom cannot handle JAK2 startup (it probably would handle JAK2 except for the inrush power, which is greater than the ~155 watts I see when it is up and running); ... at 30 minutes 24.5vdc, Liebert says ~75% battery remains (3 bars out of 4, but it said this a few minutes after starting the test), very slight "hot" smell but probably just dust/dirt on the heat sinks; Estimated <5% of battery capacity used; Power restored ...					5/17/19		95%		20190517
				10:40		12:00	[B4-7] … 27.0 vdc …; 27.5 vdc					Continuous			100%	20190517
		23					[B4-7] Photo of Network UPSs on high shelf in rear room: PowerCom, Liebert, Delta, Trojan T-105s	IMG					20190523
	Jun	29	Sa	~	08:15	~	08:45	[B4-7] T1 Bypassed; Network loads moved to T2 (PowerCom); T2 Bypassed; Liebert removed; T2 Not Bypassed / Liebert installed in W100 Series Test setup (temporary, for a few days)				S3 A4					20190629
	Jul	10	We	~	07:30	~	08:10	[B4-7] Liebert (A3) moved back to rear room for Network and N Desk; T2 bypass; A3 connected to batteries; T1 and T2 bypass NOT / Network and N Desk brought down and moved to T1; T450s (R); PC_1 (T2) will be used for bench T2 circuit only				S3 A3 A4					20190710
	Oct	5	Sa	~	08:52			[B4-7] Electrolyte Level Checked, down 1/2" almost to plates; BK 27.48 vdc; Equalization, 30.00/3.333; Liebert (T1) beep, silenced …; Equalization 2 Hours					10/5/19			20191005
	Dec	19		~	09:00	~	11:45	[B4-7] Power failure, 758 customers; 95% SoC guestimate					95%		20191219
2020	Mar	10		~	22:12	~	02:14	[B4-7] Power failure, 750+ customers, 4 hours (I worked at T400s for the last ~3 hours); 50% SoC guestimate					50%		20200310
	Nov	21	Sa	~	12:15	~	13:43	[B4-7] Cleaned; Electrolyte Levels Checked, plates are exposed, dry down at least 1/4" into the plates and maybe more (13.5 months since last check), capacity has been damaged, added ~298 fl oz (2.4 gals); Tightened connections (8)					11/21/20		100%	20201121
				~	13:43	~	15:44	[B4-7] BK 27.45 vdc; Equalization, 30.00/3.333; 2 Hours				S2					20201121
				~	18:15			[B4-7] BK 27.46 vdc without S3 (Trojan recommends 27.0 volts); Reattached S3 (same float)				S3 A3 A4					20201121
2021	Jan	12	Tu	~	09:00	~	09:30	[B4-7] Temperatures measured and electrolyte levels checked B3-B7: Range from left to right is 87 to 78⁰F; The two on the left (B3 & B4) are the warmest because they are next to the UPS units which radiate heat; The warmer batteries are lower on electrolyte; B3, B4, B5 are down ~1/4" or 1/3 of the way to the plates; For B7 on the right (which is the coolest battery) the levels are only down about 3/16" and cell 1 of 3 is "full" (meniscus showing); It has been 52 days (1.7 months) since they were checked which says we cannot go more than 5 months without adding water; TODO Move batteries away from UPSs	L5					20210112
				[B4-7] Removed GXT2_1 and GXT2_2 Liebert UPSs from the shelf above the door to make room; Bypassed UPSs; Powered down and disconnected B4-B7 / Removed DE_1 (S3); Cleaned batteries and shelf; Moved B4-B7 all the way to the right side of the shelf in a 2x2 layout / Placed an insulating box between the UPSs and the batteries; Re-connected B4-B7; Un-bypassed the UPSs; Added ~48 oz (3 pints) of water for all (4) batteries	A5-A6 S3			A3-4		1/12/21			20210112
				~	16:48	~	18:48	[B4-7] BK 27.49 vdc; Equalization, 30.00/3.333; 2 Hours; NOTE Use 29.8v next time, as there was a Liebert A3 Error for overvoltage; Photos of PC_1, PS700_2, BK_1 and B4-B7; Photos also include TurboNet/RHS project with B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	S2 IMG					20210112
		14	We					[B4-7] Photos of network UPS AC power distribution center for T1 and T2 (rear room) / This photo and the photos from Tu1/12 and Mo1/8 (RHS project) were posted on my Facebook timeline	IMG					20210114
	Jun	26	Sa					[B4-7] Electrolyte levels checked, plates exposed slightly in 6 out of 12 cells (5.5 months since filled); Overfilled ~1/4" (half way up the relief slot); Added ~1.4 gals Equalization, 29.80/3.355, clip leads, 2 Hours; 27.49v Float (BK)	S2					6/26/21			20210626
	Dec	25	Sa					[B4-7] Electrolyte levels checked, +0 to +1/8" above plates, plates not exposed but very close to it, "lead scum floaters" on top of lowest cells (B6 cell 1, B7 cell 2, counting negative to positive); Overfilled ~1/4" (half way up the relief slot, ~1.3 gals total); Cleaned; 27.49vBK, 0.031aE, Liebert (A3) is providing all of the Float (with a small amount back feeding to PowerCom A4); BK "Equalization" started at 08:26 (set 32.40v/2.086a, started in CC <30vBK); Bypassed A3 (T1) and A4 (T2) and turned them off to obtain slightly more current; 09:20 BK set 30.50v/3.278v (CC, gives us close to the the highest current possible, 3.13aE); 10:26 Equalization stopped (2h) MailCOPA reminder for 5/25/22 (repeat every 5 months)	S2			A3-4		12/25/21			20211225
2022	Aug	1	Mo			~	15:42	[B4-7] Electrolyte levels checked, all plates exposed except B4 cell 2, B5 cell 3 and B7 cell 3 (neg. to pos.); Cleaned / Positive connection bulging (raised deformed plastic); Overfilled ~1/8" (1/3 way up the relief slot, ~1.7 gals total); 27.44vB; Caps left OFF for Equalization / Bypassed A3 (T1) and A4 (T2), turned them off and unplugged them to obtain slightly more power (higher Vs); BK solid connection (#12 red/blk solid) / "Equalization" started at 13:42 (set 30.5v/3.278v Preset A) but adjusted to obtain highest power ... the best setting for the entire 2 hrs was 29.2v/3.424a / 15:42 Equalization stopped (2h), set Float 27.00v; Cleaned again; Float ~0.74aB (no parasitic load from A3/4 which are attached but off and unplugged) / MailCOPA reminder for 1/1/23 (repeat every 5 months, don't equalize)	S2		L0		-	8/1/22			20220801
		2	Tu					[B4-7] Google search: «As I understand, positive post "extrusion" is typically the result of positive grid corrosion typically caused by "over charging / over equalization". When you charge a battery at 100% state of charge, the energy is turned into H2 and O2 gasses. The good thing is this mixes up the electrolyte and reduce[s] stratification issues (low density at the top of the cell and high density electrolyte at the bottom). The bad thing is that the O2 forms at the positive plate and causes grid (and probably lead) oxidation--causing the plates to "grow" and put the positive post up and bulge the sides of the case.» / CONCLUSIONs: Batteries are being abused by overcharging (27.5v Float is high for the temperature which is ~26-27⁰C); Don't Equalize (it makes it worse) / If I get into a position where they need to be replaced it would be best to redesign the system from scratch: (4) T-105s but with (2) 450w to 1200w sine wave inverters for T1 and T2 (with or without AC bypass), and an SCP-75-24 with BTS to charge the batteries, total system cost ~$500-$700 without batteries (search DigiKey/Mouser) / Example of replacement equipment: Mean Well NTU-1200-124US $326.30x2 (has AC bypass); SCP-75-24 $32.80				-					20220802
				~	08:08	~	08:11	[B4-7] ITECH Battery Test: C/20=11.25a; Stop 10v (oops! s/b 20v); Discharged for 3 mins (~0.6 AH) and realized my error, terminated					99%		20220802
				~	08:15	~	08:54	[B4-7] Plugged in Liebert (A3) and PowerCom (A4) to recover charge lost in aborted test (>2.5aE total, should require only ~15m, but will give it more)				A3-4				100%	20220802
				~	08:54	~	15:26	[B4-7] ~27.4vI; ~1.1aE; Unplugged UPSs and started ITECH Battery Test (11.25a, Stop 20v) ...; 23,525s (6.5h) 73.511 AH (32.7% of new capacity) / CONCLUSION: These batteries are still very useable for this application, the C/20 capacity runtime of 6.5h is plenty for what I need them for				-			0% by man'f specs. / 64% by OCV		20220802
				~	19:25	~	19:35	[B4-7] 24.589vI (64% SoC by OCV); There's a lot of capacity left but it can't be used at 11.25a ...; UPSs ON; Liebert (A3) shows battery status 2/4 bars / UPSs plugged in (charging, both UPSs ~2.7aE); At this low charge rate it will take at least 27h to recover; Bypass removed			L	A3-4					20220802
		4	Th					[B4-7] Expected recovery to 100% SoC (if no power failures)					Continuous			100%	20220804
2023	May	16	Tu					[B4-7] Electrolyte levels checked, all plates exposed except B5 cell 3, B7 cell 3 (positive cells, barely covered); Cleaned / Overfilled ~1/8" (1/3 way up the relief slot, ~2.3 gals total); No Equalization; MailCOPA reminder for 10/16/23 (repeat every 5 months, don't equalize) / Installed window A/C (temporary, if it works it will need to be tightened up) set 60⁰F (lowest setting allowed) Energy Saver ON / Based on 60mV/⁰C Tcomp the ideal battery T for 500mV high Float is ~17⁰C (~63⁰F); Before starting to cool the room down the battery T was ~27⁰C	IMG					5/16/23			20230516
		18	Th					[B4-7] Window A/C has reduced room temperature as low as it can go (room air ~20⁰C); Batteries are still above 27⁰C (batteries are heating themselves) / Installed Kill-A-Watt to monitor A/C electric consumption (latest bill from AUE is $0.109/KwH); Initial indications are <$1 per day / I have an idea that should work to reduced the battery float voltage: Dual diodes back to back, with suppression contactor to extend run time & max power capacity / I call this a Float Reducer and it should drop the charging voltage to <27v but allow bidirectional operation (with or without contactor) / 20230518^28 B4-7 Float Reducer (A3-4) White Sheet Scan.jpg / Soon after this day I started bypassing and unplugging both UPSs at night, and I also don't run the Liebert at all (T1) as it has a higher Float than the PowerCom (T2) which is charging only during the work day	WS SSC LIB			A3-4	-				20230518
		28	Su					[B4-7] Completed initial designs for the Float Reducer and ordered diodes; Files added to LIB > Vishay and SMC Diode Solutions: / 20230528.1 B4-7 Float Reducer (A3-4) White Sheet Scan.jpg / 20230528.2 B4-7 Float Reducer (A3-4) White Sheet Scan.jpg / 20230528.3 Vishay Power Silicon Rectifier Diodes Datasheet (VS-1N1183R for B4-7 Float Reducer) vs-1n1183series.pdf	WS SSC LIB DKE					20230528
	Jun	2	Fr					[B4-7] Received and labeled diodes in DKE order; Unfortunately, since I chose the SMC Schottky I've discovered a Vishay PowerTab with better ultralow Vf [project DWP] / So the Schottky received today may just go into stock; A shame, but I also want to experiment with installing the PowerTab Vishays (that are slated for WP14-15), so I'll wait to assemble the Float Reducer until those are rec'd / 20230528.4 DKE Invoice B4-7 Float Reducer (A3-4) SSC.jpg	SSC LIB DKE					20230602

## B5
Batteries: B5	A					20150808_2/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Applied	L	A3-4	-	5/16/23	0% by man'f specs. / 64% by OCV	100%
2015	Aug	8	Sa					B4-5	BFMS TSP	New	L					20150808
				MA2 SSRP	Float		BC1	Continuous				20150808
	Nov	30	Mo					Applied	L1	C1	11/30/15	Probably	95%	100%	20151130
	Dec	17	Th					Float	L	BC1	Continuous		52%		20151217
		22	Tu					12/22/15			20151222
		27	Su					Applied	L1	C1	12/27/15				20151227
2016	Jan	10	Su					60%	98%	20160110
		27	We					45%	83%	20160127
	Mar	16					IMG					20160316
	Apr	22	Fr					Float	L	BC1	Continuous		55%	100%	20160422
		29	Fr					IMG	Applied	L1	C1	4/29/16	4/29/16			20160429
	May	6	Fr					Float	L	BC1	Continuous		46%		20160506
		13	Fr					Applied	L1	C1	5/13/16			100%	20160513
		23	Mo					Float	L	BC1	Continuous		38%		20160523
	Jun	1	We					Applied	L1	C1	6/1/16			100%	20160601
		13	Mo		14:05		14:33			Bulk	L	BC1	Continuous		32%		20160613
		14	Tu					B4-7		Float					20160614
		15	We					Slated for RW		Garage		6/15/16	6/15/16		100%	20160615
		16	Th	~	10:40				IMG	Applied	L1	C1					20160616
	Nov	27	Su	~	12:00					Uncharged	L				0%		20161127
		28	Mo	~	10:00	~	10:30			Charging		BC1	Continuous				20161128
		29	Tu		17:10					20161129
		30	We	~	02:00					Float					20161130
				~	09:30	~	10:00					11/30/16	11/30/16			20161130
				10:22	~	11:17					Continuous				20161130
	Dec	16	Fr	~	14:00				IMG	Applied	L1	C1-2	12/16/16			100%	20161216

2017	Jan	3	Tu	~	11:30		12:55			Charging	L	BC1	Continuous		33%		20170103
		4	We				17:09			Float					20170104
		5	Th					1/5/17			20170105
		19	Th					IMG	Applied	L1	C1/2/6	1/19/17			100%	20170119
	Mar	29	We	~	08:35	~	09:35			Bulk	L	BC1	Continuous		1%		20170329
		31	Fr	~	18:45					Float					20170331
	Apr	1	Sa	~	07:50					4/1/17			20170401
	May	6	Sa					Available			5/6/17			100%	20170506
		15	Mo					Float			Continuous		99%		20170515
	Nov	2	Th	~	16:15					11/2/17			20171102
		3	Fr	~	16:30					Applied	L1	C1/2/6	11/3/17			100%	20171103
	Nov	28	Tu	~	15:30					Charging	L	BC1	Continuous	11/28/17	25%		20171128
		30	Th					Float				11/30/17			20171130
	Dec	22	Fr	~	14:15					Applied	L1	C1/2/6	12/22/17			100%	20171222
		29	Fr	~	14:30					Charging	L	BC1	Continuous		66%		20171229
2018	Jan	15	Mo	~	12:00					Applied	L1	C1/2/6	1/15/18	1/15/18		100%	20180115
	Feb	24	Sa	~	09:30					Charging	L	BC1	Continuous		0%		20180224
	Mar	13	Tu					Available			3/13/18			100%	20180313
		17	Sa			~	00:10			Charging		BC3	Continuous		98%		20180317
		19	Mo	~	13:00	~	15:00			ENC Float				3/19/18			20180319
		29	Th	~	13:05	~	13:50			Applied	L1	C1/2/6	3/29/18			100%	20180329
	Apr	24					IMG					20180424
	Jul	20	Fr					C1-2					20180720
	Aug	13	Mo					IMG	Available	L				13%		20180813
		21	Tu	~	05:00	~	05:30					BC1					20180821
		23	Th	~	00:00					Continuous			100%	20180823
		28	Tu					8/28/18	8/28/18			20180828
		29	We					99%		20180829
	Nov	2	Fr	~	06:00	~	06:45					BC3	Continuous			100%	20181102
2019	Mar	26	Tu	~	20:00					20190326
		27	We			~	02:40					20190327
		29	Fr					L0		3/29/19	3/29/19			20190329
		30	Sa					IMG	Applied		A1					20190330
		31	Su				20:30				L	S2 A1			85%		20190331
	Apr	1	Mo		06:30		07:15					S2					20190401
				08:10		08:20					4/1/19			20190401
				08:35		08:53					A1	Continuous			100%	20190401
				20190401
		27	Sa		14:38		15:55					4/27/19		95%		20190427
		28	Su		08:42	~	14:20					S2 A1					20190428
				15:10		15:18					A1	Continuous			100%	20190428
	May	15	We		08:38		09:28					5/15/19		94%		20190515
				09:44		15:10					S2 A1					20190515
				17:12					A1	Continuous			100%	20190515
		16	Th					S2 A1					20190516
				S3					20190516
				~	23:45					S3 A4					20190516
		17	Fr	~	05:00					S3 A3 A4					20190517
				06:10		06:40					5/17/19		95%		20190517
				10:40		12:00					Continuous			100%	20190517
		23					IMG					20190523
	Jun	29	Sa	~	08:15	~	08:45					S3 A4					20190629
	Jul	10	We	~	07:30	~	08:10					S3 A3 A4					20190710
	Oct	5	Sa	~	08:52					10/5/19			20191005
	Dec	19		~	09:00	~	11:45					95%		20191219
2020	Mar	10		~	22:12	~	02:14					50%		20200310
	Nov	21	Sa	~	12:15	~	13:43					11/21/20		100%	20201121
				~	13:43	~	15:44					S2					20201121
				~	18:15					S3 A3 A4					20201121
2021	Jan	12	Tu	~	09:00	~	09:30		L5					20210112
				A5-A6 S3			A3-4		1/12/21			20210112
				~	16:48	~	18:48		S2 IMG					20210112
		14	We					IMG					20210114
	Jun	26	Sa					S2					6/26/21			20210626
	Dec	25	Sa					S2			A3-4		12/25/21			20211225
2022	Aug	1	Mo			~	15:42		S2		L0		-	8/1/22			20220801
		2	Tu					-					20220802
				~	08:08	~	08:11					99%		20220802
				~	08:15	~	08:54					A3-4				100%	20220802
				~	08:54	~	15:26					-			0% by man'f specs. / 64% by OCV		20220802
				~	19:25	~	19:35				L	A3-4					20220802
		4	Th					Continuous			100%	20220804
2023	May	16	Tu					IMG					5/16/23			20230516
		18	Th					WS SSC LIB			A3-4	-				20230518
		28	Su					WS SSC LIB DKE					20230528
	Jun	2	Fr					SSC LIB DKE					20230602

## B6
Batteries: B6	A					20150910_1/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Applied	L	A3-4	-	5/16/23	0% by man'f specs. / 64% by OCV	100%
2015	Sep	10	Th					[B6-7] Drove to Kansas City and picked up the battery set; Slated for RN	BFMS TSP	New	L					20150910
				[B6-7] Highly likely to have been put off and on float charge in shop until needed		Float		BC1	Continuous				20150910
		19	Sa					[B6-7] Finished installation at RN		Applied	L2	C5	9/19/15			100%	20150919
	Nov	17	Tu					[B6-7] Watered: Battery SoC in low 80% range, so not a good time to do it, but since it is not easy to go to the tower, we added water anyway / Not a very accurate watering (Butch did it in the rain and the mud)					11/17/15			20151117
2016	Feb	19	Fr					[B6-7] Removed from RN; Watered; On Trace @ Shop		Float	L	BC1	Continuous	2/19/16	46%	100%	20160219
	Apr	21					[B6-7] Video and photos of batteries under bench	IMG					20160421
		22	Fr					[B6-7] Watered (only one cell slightly low); Installed at RW		Applied	L1	C1	4/22/16	4/22/16		100%	20160422
		29	Fr					[B6-7] Removed from RW; On Trace @ Shop		Float	L	BC1	Continuous		50%		20160429
	May	6	Fr					[B6-7] Photos under the bench of one of the 2 batteries; Installed at RW; Electrolyte Level Checked (but no water needed)	IMG	Applied	L1	C1	5/6/16	5/6/16		100%	20160506
		13	Fr					[B6-7] Removed from RW; On Trace @ Shop		Float	L	BC1	Continuous		42%		20160513
		23	Mo					[B6-7] Installed at RW; Electrolyte Level Checked (but no water needed)		Applied	L1	C1	5/23/16	5/23/16		100%	20160523
	Jun	1	We					[B6-7] Removed from RW; On Trace @ Shop		Float	L	BC1	Continuous		21%		20160601
		13	Mo		16:25			[B6-7] In parallel with set 20150808 as it comes up through 13.1 volts in bulk (for Absorption/Equalization)	B4-5	Equalization					20160613
		14	Tu					B4-7		Float					20160614
		15	We					Slated for RW		Garage		6/15/16	6/15/16		100%	20160615
		16	Th	~	10:40			B4-7; Installed at RW on the ground, B6-7 underneath the main box (exposed); Photos	IMG	Applied	L1	C1					20160616
	Nov	27	Su	~	12:00			B4-7		Uncharged	L				0%		20161127
		28	Mo	~	10:00	~	10:30			Charging		BC1	Continuous				20161128
		29	Tu		17:10					20161129
		30	We	~	02:00					Float					20161130
				~	09:30	~	10:00					11/30/16	11/30/16			20161130

				10:22	~	11:17					Continuous				20161130
	Dec	16	Fr	~	14:00					Applied	L1	C1-2	12/16/16			100%	20161216
		22					IMG					20161222
2017	Jan	3	Tu	~	11:30		12:55			Charging	L	BC1	Continuous		33%		20170103
		4	We				17:09			Float					20170104
		5	Th					1/5/17			20170105
		19	Th					Applied	L1	C1/2/6	1/19/17			100%	20170119
	Mar	29	We	~	08:35	~	09:35			Bulk	L	BC1	Continuous		1%		20170329
		31	Fr	~	18:45					Float					20170331
	Apr	1	Sa	~	07:50					4/1/17			20170401
	May	6	Sa					Available			5/6/17			100%	20170506
		15	Mo					Float			Continuous		99%		20170515
	Nov	2	Th	~	16:15					11/2/17			20171102
		3	Fr	~	16:30					Applied	L1	C1/2/6	11/3/17			100%	20171103
	Nov	28	Tu	~	15:30					Charging	L	BC1	Continuous	11/28/17	25%		20171128
		30	Th					Float				11/30/17			20171130
	Dec	22	Fr	~	14:15					Applied	L1	C1/2/6	12/22/17			100%	20171222
		29	Fr	~	14:30					Charging	L	BC1	Continuous		66%		20171229
2018	Jan	15	Mo	~	12:00					Applied	L1	C1/2/6	1/15/18	1/15/18		100%	20180115
	Feb	24	Sa	~	09:30					Charging	L	BC1	Continuous		0%		20180224
	Mar	13	Tu					Available			3/13/18			100%	20180313
		17	Sa			~	00:10			Charging		BC3	Continuous		98%		20180317
		19	Mo	~	13:00	~	15:00			ENC Float				3/19/18			20180319
		29	Th	~	13:05	~	13:50			Applied	L1	C1/2/6	3/29/18			100%	20180329
	Apr	24					IMG					20180424
	Jul	20	Fr					C1-2					20180720
	Aug	13	Mo					IMG	Available	L				13%		20180813
		21	Tu	~	05:00	~	05:30					BC1					20180821
		23	Th	~	00:00					Continuous			100%	20180823
		28	Tu					8/28/18	8/28/18			20180828
		29	We					99%		20180829
	Nov	2	Fr	~	06:00	~	06:45					BC3	Continuous			100%	20181102
2019	Mar	26	Tu	~	20:00					20190326
		27	We			~	02:40					20190327
		29	Fr					L0		3/29/19	3/29/19			20190329
		30	Sa					IMG	Applied		A1					20190330
		31	Su				20:30				L	S2 A1			85%		20190331
	Apr	1	Mo		06:30		07:15					S2					20190401
				08:10		08:20					4/1/19			20190401
				08:35		08:53					A1	Continuous			100%	20190401
				20190401
		27	Sa		14:38		15:55					4/27/19		95%		20190427
		28	Su		08:42	~	14:20					S2 A1					20190428
				15:10		15:18					A1	Continuous			100%	20190428
	May	15	We		08:38		09:28					5/15/19		94%		20190515
				09:44		15:10					S2 A1					20190515
				17:12					A1	Continuous			100%	20190515
		16	Th					S3 A1					20190516
				S3					20190516
				~	23:45					S3 A4					20190516
		17	Fr	~	05:00					S3 A3 A4					20190517
				06:10		06:40					5/17/19		95%		20190517
				10:40		12:00					Continuous			100%	20190517
		23					IMG					20190523
	Jun	29	Sa	~	08:15	~	08:45					S3 A4					20190629
	Jul	10	We	~	07:30	~	08:10					S3 A3 A4					20190710
	Oct	5	Sa	~	08:52					10/5/19			20191005
	Dec	19		~	09:00	~	11:45					95%		20191219
2020	Mar	10		~	22:12	~	02:14					50%		20200310
	Nov	21	Sa	~	12:15	~	13:43					11/21/20		100%	20201121
				~	13:43	~	15:44					S2					20201121
				~	18:15					S3 A3 A4					20201121
2021	Jan	12	Tu	~	09:00	~	09:30		L5					20210112
				A5-A6 S3			A3-4		1/12/21			20210112
				~	16:48	~	18:48		S2 IMG					20210112
		14	We					IMG					20210114
	Jun	26	Sa					S2					6/26/21			20210626
	Dec	25	Sa					S2			A3-4		12/25/21			20211225
2022	Aug	1	Mo			~	15:42		S2		L0		-	8/1/22			20220801
		2	Tu					-					20220802
				~	08:08	~	08:11					99%		20220802
				~	08:15	~	08:54					A3-4				100%	20220802
				~	08:54	~	15:26					-			0% by man'f specs. / 64% by OCV		20220802
				~	19:25	~	19:35				L	A3-4					20220802
		4	Th					Continuous			100%	20220804
2023	May	16	Tu					IMG					5/16/23			20230516
		18	Th					WS SSC LIB			A3-4	-				20230518
		28	Su					WS SSC LIB DKE					20230528
	Jun	2	Fr					SSC LIB DKE					20230602

## B7
Batteries: B7	A					20150910_2/2: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description
				Applied	L	A3-4	-	5/16/23	0% by man'f specs. / 64% by OCV	100%
2015	Sep	10	Th					B6-7	BFMS TSP	New	L					20150910
				Float		BC1	Continuous				20150910
		19	Sa					Applied	L2	C5	9/19/15			100%	20150919
	Nov	17	Tu					11/17/15			20151117
2016	Feb	19	Fr					Float	L	BC1	Continuous	2/19/16	46%	100%	20160219
	Apr	21					IMG					20160421
		22	Fr					Applied	L1	C1	4/22/16	4/22/16		100%	20160422
		29	Fr					Float	L	BC1	Continuous		50%		20160429
	May	6	Fr					IMG	Applied	L1	C1	5/6/16	5/6/16		100%	20160506
		13	Fr					Float	L	BC1	Continuous		42%		20160513
		23	Mo					Applied	L1	C1	5/23/16	5/23/16		100%	20160523
	Jun	1	We					Float	L	BC1	Continuous		21%		20160601
		13	Mo		16:25				B4-5	Equalization					20160613
		14	Tu					B4-7		Float					20160614
		15	We					Slated for RW		Garage		6/15/16	6/15/16		100%	20160615
		16	Th	~	10:40			B4-7; Installed at RW on the ground, B6-7 underneath the main box (exposed); Photos	IMG	Applied	L1	C1					20160616
	Nov	27	Su	~	12:00			B4-7		Uncharged	L				0%		20161127
		28	Mo	~	10:00	~	10:30			Charging		BC1	Continuous				20161128
		29	Tu		17:10					20161129
		30	We	~	02:00					Float					20161130
				~	09:30	~	10:00					11/30/16	11/30/16			20161130

				10:22	~	11:17					Continuous				20161130
	Dec	16	Fr	~	14:00					Applied	L1	C1-2	12/16/16			100%	20161216
		22					IMG					20161222
2017	Jan	3	Tu	~	11:30		12:55			Charging	L	BC1	Continuous		33%		20170103
		4	We				17:09			Float					20170104
		5	Th					1/5/17			20170105
		19	Th					Applied	L1	C1/2/6	1/19/17			100%	20170119
	Mar	29	We	~	08:35	~	09:35			Bulk	L	BC1	Continuous		1%		20170329
		31	Fr	~	18:45					Float					20170331
	Apr	1	Sa	~	07:50					4/1/17			20170401
	May	6	Sa					Available			5/6/17			100%	20170506
		15	Mo					Float			Continuous		99%		20170515
	Nov	2	Th	~	16:15					11/2/17			20171102
		3	Fr	~	16:30					Applied	L1	C1/2/6	11/3/17			100%	20171103
	Nov	28	Tu	~	15:30					Charging	L	BC1	Continuous	11/28/17	25%		20171128
		30	Th					Float				11/30/17			20171130
	Dec	22	Fr	~	14:15					Applied	L1	C1/2/6	12/22/17			100%	20171222
		29	Fr	~	14:30					Charging	L	BC1	Continuous		66%		20171229
2018	Jan	15	Mo	~	12:00					Applied	L1	C1/2/6	1/15/18	1/15/18		100%	20180115
	Feb	24	Sa	~	09:30					Charging	L	BC1	Continuous		0%		20180224
	Mar	13	Tu					Available			3/13/18			100%	20180313
		17	Sa			~	00:10			Charging		BC3	Continuous		98%		20180317
		19	Mo	~	13:00	~	15:00			ENC Float				3/19/18			20180319
		29	Th	~	13:05	~	13:50			Applied	L1	C1/2/6	3/29/18			100%	20180329
	Apr	24					IMG					20180424
	Jul	20	Fr					C1-2					20180720
	Aug	13	Mo					IMG	Available	L				13%		20180813
		21	Tu	~	05:00	~	05:30					BC1					20180821
		23	Th	~	00:00					Continuous			100%	20180823
		28	Tu					8/28/18	8/28/18			20180828
		29	We					99%		20180829
	Nov	2	Fr	~	06:00	~	06:45					BC3	Continuous			100%	20181102
2019	Mar	26	Tu	~	20:00					20190326
		27	We			~	02:40					20190327
		29	Fr					L0		3/29/19	3/29/19			20190329
		30	Sa					IMG	Applied		A1					20190330
		31	Su				20:30				L	S2 A1			85%		20190331
	Apr	1	Mo		06:30		07:15					S2					20190401
				08:10		08:20					4/1/19			20190401
				08:35		08:53					A1	Continuous			100%	20190401
				20190401
		27	Sa		14:38		15:55					4/27/19		95%		20190427
		28	Su		08:42	~	14:20					S2 A1					20190428
				15:10		15:18					A1	Continuous			100%	20190428
	May	15	We		08:38		09:28					5/15/19		94%		20190515
				09:44		15:10					S2 A1					20190515
				17:12					A1	Continuous			100%	20190515
		16	Th					S3 A1					20190516
				S3					20190516
				~	23:45					S3 A4					20190516
		17	Fr	~	05:00					S3 A3 A4					20190517
				06:10		06:40					5/17/19		95%		20190517
				10:40		12:00					Continuous			100%	20190517
		23					IMG					20190523
	Jun	29	Sa	~	08:15	~	08:45					S3 A4					20190629
	Jul	10	We	~	07:30	~	08:10					S3 A3 A4					20190710
	Oct	5	Sa	~	08:52	~	10:52					10/5/19			20191005
	Dec	19		~	09:00	~	11:45					95%		20191219
2020	Mar	10		~	22:12	~	02:14					50%		20200310
	Nov	21	Sa	~	12:15	~	13:43					11/21/20		100%	20201121
				~	13:43	~	15:44					S2					20201121
				~	18:15					S3 A3 A4					20201121
2021	Jan	12	Tu	~	09:00	~	09:30		L5					20210112
				A5-A6 S3			A3-4		1/12/21			20210112
				~	16:48	~	18:48		S2 IMG					20210112
		14	We					IMG					20210114
	Jun	26	Sa					S2					6/26/21			20210626
	Dec	25	Sa					S2			A3-4		12/25/21			20211225
2022	Aug	1	Mo			~	15:42		S2		L0		-	8/1/22			20220801
		2	Tu					-					20220802
				~	08:08	~	08:11					99%		20220802
				~	08:15	~	08:54					A3-4				100%	20220802
				~	08:54	~	15:26					-			0% by man'f specs. / 64% by OCV		20220802
				~	19:25	~	19:35				L	A3-4					20220802
		4	Th					Continuous			100%	20220804
2023	May	16	Tu					IMG					5/16/23			20230516
		18	Th					WS SSC LIB			A3-4	-				20230518
		28	Su					WS SSC LIB DKE					20230528
	Jun	2	Fr					SSC LIB DKE					20230602

## B8
Batteries: B8	A					20160421_1/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Applied	MA2	BC1	Usually	8/1/22	30%	100%
2016	Apr	21	Th					[B8-11] Drove to Kansas City and picked up the battery set / Put them on the floor in the shop (no charging yet); Video and photos	BFMS TSP IMG	New	L					20160421
	May	8	Su					[B8-11] At rest, OCV, in order 1/4, 2/4, 3/4, 4/4: 6.33, 6.33, 6.27, 6.30; %SoC Low Point is estimated based on six months on the shelf at 2.5% self-discharge per month			L0				85%		20160508
				[B8-11] Electrolyte levels checked but no water added (they're all maybe 1/8" below what they should be)					5/8/16			20160508
		10	Tu		06:10			[B8-11] Parallel/Series attachment (2x2 6volt battery units) on Trace charger: 12.60 VDC powering Trace logic; Started Bulk charging (12.8 VDC) …		Bulk		BC1	Continuous				20160510
				07:10			[B8-11] 13.69 VDC, Bulk …					20160510
				07:22			[B8-11] 13.73 VDC, Bulk …					20160510
				07:52			[B8-11] 13.83 VDC, Bulk …					20160510
				07:59			[B8-11] 13.85 VDC, Bulk …					20160510
				08:12			[B8-11] 13.89 VDC, Bulk …					20160510
				08:17			[B8-11] 13.90 VDC, Bulk …					20160510
				08:41			[B8-11] 13.97 VDC, Bulk …					20160510
				08:47			[B8-11] 14.00 VDC, Bulk …					20160510
				09:33			[B8-11] 14.16 VDC, Bulk …					20160510
				09:56			[B8-11] 14.25 VDC, Bulk …					20160510
				10:05			[B8-11] 14.28 VDC, Bulk …					20160510
				10:47			[B8-11] 14.41 VDC, Bulk …					20160510
				11:48			[B8-11] 14.57 VDC, Bulk …					20160510
				14:13			[B8-11] 14.7 VDC (+/-0.1 VDC, erratic due to Trace regulator), I would guess it probably reached regulation at about 13:30; now Absorption …		Absorption					20160510
				14:57			[B8-11] 13.3 VDC (+/-0.1 VDC, erratic due to Trace regulator), I would guess it probably reached float at about 14:30 (1 hour Absorption); Float …		Float					20160510
				~	15:10			[B8-11] Watered: no water added to 1/4, 2/4 and 4/4, but battery #3/4 needed about 1/8"					5/10/16			20160510
				~	15:15			[B8-11] Started another Trace charge cycle by killing power to Trace and reapplying … but it only stayed in Absorption for a minute before dropping to float …			L					20160510
		24	Tu					[B8-11] Equalization charge for about 1 hour (14.35 VDC) applied while charging 20150808 set	B4 B5					100%	20160524
	Jun	13	Mo		16:25			[B8-11] In parallel with set 20150808 as it comes up through 13.1 volts in bulk (for Absorption/Equalization)		Equalization					20160613
		14	Tu					[B8-11] Probably reached float early AM (after Absorption period ended)		Float					20160614
	Nov	27	Su	~	12:15			[B8-11] Installed at RW: Two of the four are on the ground underneath the main box (exposed, not sure which ones)		Applied	L1	C1	11/27/16				20161127
	Dec	16	Fr	~	13:45	~	15:00	[B8-11] Removed from RW (SoC Low Point is fairly accurate, was 11.0 volts under load) …; Charging		Bulk	L	BC1	Continuous		25%		20161216
		19	Mo					[B8-11] (It reached float yesterday); Added about 1/8" to 3/16" water		Float				12/19/16			20161219
2017	Jan	3	Tu	~	10:50	~	11:30	[B8-11] Removed from float …; Installed at RW. NOTE: when I installed it, I accidently reversed the R Inside battery (not sure which one this is now) and I got a heavy discharge for about 1 second. The effect of this was to discharge the Outside batteries and the R side battery into the L Inside battery (18v cross charge into L Inside battery). As this was only for a second, I don't think I lost much charge or damaged any of the batteries.		Applied	L1	C1-2	1/3/17			100%	20170103
		19	Th					[B8-11] Removed from RW (SoC Low Point 23.260%, ~9.0 volts under load)	Waiting Charge		L				0%		20170119
		20	Fr	~	06:40			[B8-11] Charging …		Bulk		BC1	Continuous				20170120
		21	Sa	~	14:15		15:15	[B8-11] Absorption …; Float		Float					20170121
		22	Su					[B8-11] Watered (down ~ 1/16")					1/22/17			20170122
	Mar	29	We					[B8-11] Removed from float and installed at RW		Applied	L1	C1/2/6	3/29/17			100%	20170329
	Nov	3	Fr	~	16:15			[B8-11] Removed from RW (and subsequently put on Trace)		Charging	L	BC1	Continuous		39%		20171103
		4	Sa					[B8-11] Watered: down ~ 3/8" (watered while still in bulk @ 14.0v)					11/4/17			20171104
		5	Su					[B8-11] Entered float; water levels are OK, some cells slightly high		Float				11/5/17			20171105
		28	Tu	~	15:30			[B8-11] Installed at RW		Applied	L1	C1/2/6	11/28/17			100%	20171128
	Dec	22	Fr	~	14:15			[B8-11] Removed from RW (and subsequently put on Trace)		Charging	L	BC1	Continuous		37%		20171222
		23	Sa					[B8-11] Electrolyte levels checked but no water needed					12/23/17			20171223
		29	Fr	~	14:00			[B8-11] Installed at RW		Applied	L1	C1/2/6	12/29/17			100%	20171229
2018	Jan	15	Mo	~	12:00			[B8-11] Removed from RW (and subsequently put on Trace); %SoC Low Point as per Wattmon (11.4 VDC under load, very cold)		Charging	L	BC1	Continuous		44%		20180115
		18	Th					[B8-11] Electrolyte levels checked: very little water needed, only one cell down 1/16"					1/18/18			20180118
	Feb	24	Sa	~	09:30			[B8-11] Installed at RW		Applied	L1	C1/2/6	2/24/18			100%	20180224
	Mar	29	Th	~	13:53	~	15:00	[B8-11] Removed from RW (WSoC 27.22%, 10.9v under ~25w load) … / Initial cold OCV (less than 2 hours rest) 5.70,5.70,5.70,5.69v --> 3.4% SoC Low Point by OCV & T-105 Data Sheet			L					20180329
				~	17:45		18:15	[B8-11] OCV rising, now rested almost 4 hrs and batteries are closer to room T, series/parallel 11.47v --> 8.1% SoC Low Point by OCV & T-105 Data Sheet / Some slight discharge during W100 test setup …; Charging on W100 (WISPer/Genasun)	WRD	Charging	L0	WP2	Continuous		8%		20180329
	Apr	2		~	15:15			[B8-11] Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	WRD EML					20180402
		3	Tu	~	06:00		06:45	[B8-11] Removed from W100 test setup; Electrolyte Levels corrected (B8-1/4 low ~1/8", B9-2/4 OK, B10-3/4 cells 1&2 low ~1/8" cell 3 low ~1/16", B11-4/4 OK, the most negative cells in the string of six were low, perhaps they outgassed more, not sure why) …; Charging on ENC-180-12 (14.2v Absorption, 13.4v Float), I swapped my usual practice of putting the odd numbered batteries on the negative side to putting the even numbered batteries on the negative side (and will keep this up if applied on a Genasun, as the imbalance in the strings could be due to pulsed charging)	WRD	Absorption	L	BC3		4/3/18		100%	20180403
				08:45	[B8-11] Briefly lifted connection to switch ENC to Float (13.4v)		Float					20180403
	Jun	11		~	04:00			[B8/11] (2) T-105s removed from ENC (for Mini SAPS); Watered (all down ~1/8"); Installed in Subaru		Available	MA2		6/11/18	6/11/18		100%	20180611
	Nov	2		~	06:25			[B8/11] Trace installed in Subaru on these (2) T-105s (Trace says 12.3-12.4v, %SoC Low Point is estimated for ~5 months self-discharge); Charging (will usually be plugged in when Subaru is in the garage, but not always); Circuit O (not UPS protected, so whenever we get a power failure, we'll get an Absorption cycle)		Applied		BC1	It Will Be		90%		20181102
2019	Mar	15	Fr	~	08:00			[B8/11] Batteries used for trip to Iowa					3/15/19			100%	20190315
		17	Su			~	22:30	[B8/11] I didn't charge them until I came back; They had no problems keeping the Engel cooler and the laptop going on the Trace inverter, in fact I could have run for 7 to 10 days; %SoC Low Point is estimated based on 250AH, 63 hrs, 1A average; At the end the Trace was Slow Red Flash (12.0 to 12.2 vdc) under slight load / Charging (will usually be plugged in when Subaru is in the garage, but not always)					Most of the time		75%		20190317
		19	Tu	~	09:30			[B8/11] Electrolyte level checked: only 1 cell needed <1/16", no water added to all the other cells					3/19/19		100%	20190319
	Apr	18					[B8/11] Batteries used for Trace inverter power of sabersaw, at old house site to cut up trash; %SoC estimated					90%		20190418
				[B8/11] Trace is now on T1 UPS protection, so we don't get an Absorption cycle every time the power dies					100%	20190418
		25					[B8/11] Batteries used for Trace inverter power of compressor (to air Butch's tires); %SoC estimated					90%		20190425
		27					[B8/11] Float					100%	20190427
	Jun	22	Sa	~	05:00			[B8/11] Trace moved from Subaru to W100 test bench; Batteries not being charged		Available		-	6/22/19				20190622
	Aug	5					[B8/11] Batteries moved from Subaru to main shop floor (unfortunately, I've had to park the Subaru outside in the heat because of the Gravely repairs, and in the past week or so they've seen some very high temperatures)			L					20190805
		11	Su	~	02:30	~	02:45	[B8/11] OCV 6.33/6.32, SoC as per man'f specs. 93.3%/91.4% (92.3% average); This represents 50 days of self-discharge, sometimes under very hot conditions (4.6%/month) …; Charging on Trace on UPS T1	WP5			BC1			92%		20190811
	Sep	5	Th	~	12:15	~	12:30	[B8/11] Removed from Trace and installed in W100 Test Setup; Added ~1/4" water		W100 Test	L0	WP5	8/12/19	9/5/19		100%	20190905
2020	May	8	Fr					[B8/11] WP5 removed from test setup for delivery to Lexington	WP5	Available	L	-	5/8/20				20200508
		10	Su	~	13:45	~	14:45	[B8/11] Cleaned and checked electrolyte levels, 3/8" or more down, ~1quart of water total for 6 cells; Reinstalled in Subaru (no charger)			MA2			5/10/20			20200510
		23	Sa	~	12:00			[B8/11] Trace reinstalled in Subaru; I will charge the batteries from time to time when it is parked in the garage or I’m where there is AC / %SoC from 5-15% self-discharge per month		Applied	MA2	BC1			90%		20200523
	Nov	21	Sa	~	10:00	~	11:00	[B8/11] Cleaned and checked electrolyte levels, 3/8" or more down, ~24 fl oz of water total for 6 cells; Tightened connections (4) / ~50% SoC Low Points from memory maybe twice, although most of the time it's probably ~90%					Usually	11/21/20	50%	100%	20201121
2021	Jun	26	Sa					[B8/11] Electrolyte levels are ~1/4" above the plates, 3/8" or more down; Overfilled to 1/3 up relief slot; Can easily go 7-8 months between checks; ~0.2 gals added					6/26/21	90%		20210626
	Jul	17	Sa					[B8/11] Yesterday tshooting of Trace (see BC1) which appears not to be charging; Battery was fairly severely discharged ("Status" slow flashing red 12.0-12.v) / %SoC 60% (guessing); Achieved full charge with Trace on stool outside Subaru door (Bulk ~8 hours, Absorption ~14.8v for an hour or so, Float 13.25v) / Electrolyte levels are OK, +1/16" to +1/8", brought them all to +1/8"; Cleaned top of battery and tightened connections				BC1		7/17/21	60%		20210717
	Dec	25	Sa					[B8/11] Electrolyte levels are all ~factory (meniscus on filler tube, +5/8" above plates); ~13.27vF (13.34vM); Generous fill to 1/2 way up the filler tube (~1/4" above factory, ~0.2gals total); MailCOPA reminder set for 12/25/22 (repeat every 12 months); Cleaned; Tightened connections (small nudges); Equalization ~12:20-14:20 (2h)	S2			BC1		12/25/21			20211225
2022	Apr	17	Su					[B8/11] Tshooting of Trace which was not charging; Fixed by “slam” on BC1 / Lowest battery OCV 12.5~12.7v so battery was not deeply discharged; %SoC Low Point is a guess					80%	100%	20220417
	Jul	2	Sa					[B8/11] Electrolyte levels are all ~factory or ~1/16" higher; No water added; Cleaned / Added red/blk wires for windshield washer fluid pump on old cooler (5/16" ring connectors, switch inline on red)					7/2/22			20220702
	Aug	1	Mo					[B8/11] Colorado trip (Su7/3 to Mo7/18) %SoC Low Point estimated (at one point in the trip I was solid red for quite a while) / Electrolyte levels are all ~factory or ~1/16" higher; No water added; MailCOPA reminder set for 7/1/23 (repeat every 15 months)					8/1/22	30%	100%	20220801

## B9
Batteries: B9	A					20160421_2/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L3	WP7	6/29/22+	6/28/22	0%	?
2016	Apr	21	Th					B8-11	BFMS TSP IMG	New	L					20160421
	May	8	Su					85%		20160508
				5/8/16			20160508
		10	Tu		06:10					Bulk		BC1	Continuous				20160510
				07:10					20160510
				07:22					20160510
				07:52					20160510
				07:59					20160510
				08:12					20160510
				08:17					20160510
				08:41					20160510
				08:47					20160510
				09:33					20160510
				09:56					20160510
				10:05					20160510
				10:47					20160510
				11:48					20160510
				14:13					Absorption					20160510
				14:57					Float					20160510
				~	15:10					5/10/16			20160510
				~	15:15					L					20160510
		24	Tu					B4 B5					100%	20160524
	Jun	13	Mo		16:25					Equalization					20160613
		14	Tu					Float					20160614
	Nov	27	Su	~	12:15					Applied	L1	C1	11/27/16				20161127
	Dec	16	Fr	~	13:45	~	15:00			Bulk	L	BC1	Continuous		25%		20161216
		19	Mo					Float				12/19/16			20161219
2017	Jan	3	Tu	~	10:50	~	11:30			Applied	L1	C1-2	1/3/17			100%	20170103
		19	Th					Waiting Charge		L				0%		20170119
		20	Fr	~	06:40					Bulk		BC1	Continuous				20170120
		21	Sa	~	14:15		15:15			Float					20170121
		22	Su					1/22/17			20170122
	Mar	29	We					Applied	L1	C1/2/6	3/29/17			100%	20170329
	Nov	3	Fr	~	16:15					Charging	L	BC1	Continuous		39%		20171103
		4	Sa					11/4/17			20171104
		5	Su					Float				11/5/17			20171105
		28	Tu	~	15:30					Applied	L1	C1/2/6	11/28/17			100%	20171128
	Dec	22	Fr	~	14:15					Charging	L	BC1	Continuous		37%		20171222
		23	Sa					12/23/17			20171223
		29	Fr	~	14:00					Applied	L1	C1/2/6	12/29/17			100%	20171229
2018	Jan	15	Mo	~	12:00					Charging	L	BC1	Continuous		44%		20180115
		18	Th					1/18/18			20180118
	Feb	24	Sa	~	09:30					Applied	L1	C1/2/6	2/24/18			100%	20180224
	Mar	29	Th	~	13:53	~	15:00				L0					20180329
				~	17:45		18:15		WRD	W100 Testing		WP2	Continuous		8%		20180329
	Apr	2		~	15:15				WRD EML					20180402
		3	Tu	~	06:00		06:45		WRD	Absorption	L	BC3		4/3/18		100%	20180403
				08:45			Float					20180403
	May	5	Sa	~	06:00	~	06:22	[B9-10] Removed from ENC Float and installed in W100 test setup; Slated for TurboNet (Wellington Water Tower); B9 and B10 were chosen for this sale because they are the 'oddballs' in the set of (4), with different man'f dates/codes; B10 required more water than B9; B10 ~1/8", B9 ~1/16" (and cells 1 and 3 were high enough to begin with); I was generous with the water because it may be a long time before they are watered again	WRD	W100 Testing	L0	WP2		5/5/18			20180505
		7	Mo		01:30	~	13:35	[B9-10] Discharged to 50% WSoC (40w DR Test) ...; Float		Slated for WWT					50%		20180507
		8	Tu	~	07:00	~	12:15	[B9-10] Removed from Genasun Float (~1% ratio) …; Installed at WWT, photos and video (W100_1, DE_2, Genasun_3, 20160421_2/4, 20160421_3/4)	WRD IMG	Sold	L6					100%	20180508
	Nov	30					[B9-10] Email to Keith and Mark "Wellington Water Tower Flooded Trojan T-105 batteries": Have they been watered? - No, but Mark says they will do that soon.	EML					20181130
2019	Apr					[B9-10] Phone conversation with Mark where he mentions in passing that "Yes, we did water them." / Not sure when they were watered, and not sure exactly when he told me this, but probably in April 2019					April 2019?			20190430
2020	May	7	Th					[B9-10] Mark reports that Keith was onsite at WWT "a few days ago" (phone call while returning from BFMS in KC)	L6					~5/1/20			20200507
		8	Fr					[B9-10] Keith reports that when he checked the electrolyte levels only "a little" water was needed (maybe 1/8")					20200508
2021	Mar	12	Fr	~	13:30	~	16:05	[B9-10] Onsite at WWT for the Backup Power Supply Maintenance Program; See L6 for details / %SoC Low calculated from mean during 20' discharge of 13.2v and 10.1 amps, 3.4 AH / 225 AH is 1.5% discharge to 98.5 %SoC [see notes Su3/14/21 TM21S]	DBT TM21S SMS SSC		L6	WP2		3/12/21	98%		20210312
		13	Sa					[B9-10] Email Report to Mark and Keith; Recommended tshooting high power levels; Run-time Estimate ">12 Hrs @ 133 watts"	EML TM21S				3/13/21			100%	20210313
	May	9	Su	~	05:45	~	07:20	[B9-10] 1 hr 35 min power failure; 2-1/2 hr Absorption 14.7v; Float 13.93v; %SoC Low Point based on derating C/20 rating (225 AH) to 90% (202.5 AH)	EML SSC TM21S				5/10/21		92%		20210509
	Aug	4	We	~	10:55	~	11:45	[B9-10] Keith reports that WWT AC power was off for 2 days 1-2 months ago; Therefore battery was heavily discharged / Power levels as per Netonix too high; See L6 for details	SMS IMG		L6				0%	?	20210804
		13	Fr	~	10:40	~	12:10	[B9-10] Onsite at WWT with Keith: Battery 13.34v Fluke, 78⁰F, very high humidity; Cleaned battery terminals (much corrosion build up); Electrolyte +1/4 to 3/8" above plates, with one cell much higher (20160421_2/4 middle cell); Generous water fill to +1/8" above cup (top of meniscus @ score line); See L6 for further details	SMS SSC DBT TM21F					8/13/21			20210813
2022	Jun	28	Tu	~	15:15	~	16:30	[B9-10] Onsite at WWT: T-105s ~27⁰C (81⁰F); W100_1 and ambient ~34⁰C; W100 fan is running / T-105s 13.515vM (13.44vF equivalent, good Float V for current battery T); Float ~0.035aE; Electrolyte OK (will fill at RCWT); Removed to take to RCWT	TM22 L6		Subaru	-		6/28/22			20220628
				~	17:20	~	19:20	[B9-10] Onsite at RCWT to swap batteries: Cleaned T-105s from WWT and installed on chair with cardboard to level / Lead posts and ring connectors filed with emery board (corrosion, WWT is a humid site and the cross connect uses old ring connectors) / Electrolyte ~3/16" below factory, ~1/2" above plates, generous fill to meniscus 1/2 up slot; Photos	TM22 IMG		L3	WP7	6/29/22+	6/28/22			20220628

## B10
Batteries: B10	A					20160421_3/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L3	WP7	6/29/22+	6/28/22	0%	?
2016	Apr	21	Th					B8-11	BFMS TSP IMG	New	L					20160421
	May	8	Su					85%		20160508
				5/8/16			20160508
		10	Tu		06:10					Bulk		BC1	Continuous				20160510
				07:10					20160510
				07:22					20160510
				07:52					20160510
				07:59					20160510
				08:12					20160510
				08:17					20160510
				08:41					20160510
				08:47					20160510
				09:33					20160510
				09:56					20160510
				10:05					20160510
				10:47					20160510
				11:48					20160510
				14:13					Absorption					20160510
				14:57					Float					20160510
				~	15:10					5/10/16			20160510
				~	15:15					L					20160510
		24	Tu					B4 B5					100%	20160524
	Jun	13	Mo		16:25					Equalization					20160613
		14	Tu					Float					20160614
	Nov	27	Su	~	12:15					Applied	L1	C1	11/27/16				20161127
	Dec	16	Fr	~	13:45	~	15:00			Bulk	L	BC1	Continuous		25%		20161216
		19	Mo					Float				12/19/16			20161219
2017	Jan	3	Tu	~	10:50	~	11:30			Applied	L1	C1-2	1/3/17			100%	20170103
		19	Th					Waiting Charge		L				0%		20170119
		20	Fr	~	06:40					Bulk		BC1	Continuous				20170120
		21	Sa	~	14:15		15:15			Float					20170121
		22	Su					1/22/17			20170122
	Mar	29	We					Applied	L1	C1/2/6	3/29/17			100%	20170329
	Nov	3	Fr	~	16:15					Charging	L	BC1	Continuous		39%		20171103
		4	Sa					11/4/17			20171104
		5	Su					Float				11/5/17			20171105
		28	Tu	~	15:30					Applied	L1	C1/2/6	11/28/17			100%	20171128
	Dec	22	Fr	~	14:15					Charging	L	BC1	Continuous		37%		20171222
		23	Sa					12/23/17			20171223
		29	Fr	~	14:00					Applied	L1	C1/2/6	12/29/17			100%	20171229
2018	Jan	15	Mo	~	12:00					Charging	L	BC1	Continuous		44%		20180115
		18	Th					1/18/18			20180118
	Feb	24	Sa	~	09:30					Applied	L1	C1/2/6	2/24/18			100%	20180224
	Mar	29	Th	~	13:53	~	15:00				L0					20180329
				~	17:45		18:15		WRD	W100 Testing		WP2	Continuous		8%		20180329
	Apr	2		~	15:15				WRD EML					20180402
		3	Tu	~	06:00		06:45		WRD	Absorption	L	BC3		4/3/18		100%	20180403
				08:45			Float					20180403
	May	5	Sa	~	06:00	~	06:22	B9-10	WRD	W100 Testing	L0	WP2		5/5/18			20180505
		7	Mo		01:30	~	13:35			Slated for WWT					50%		20180507
		8	Tu	~	07:00	~	12:15		WRD IMG	Sold	L6					100%	20180508
	Nov	30					EML					20181130
2019	Apr					April 2019?			20190430
2020	May	7	Th					L6					~5/1/20			20200507
		8	Fr					20200508
2021	Mar	12	Fr	~	13:30	~	16:05		DBT TM21S SMS SSC		L6	WP2		3/12/21	98%		20210312
		13	Sa					EML TM21S				3/13/21			100%	20210313
	May	9	Su	~	05:45	~	07:20		EML SSC TM21S				5/10/21		92%		20210509
	Aug	4	We	~	10:55	~	11:45		SMS IMG		L6				0%	?	20210804
		13	Fr	~	10:40	~	12:10		SMS SSC DBT TM21F					8/13/21			20210813
2022	Jun	28	Tu	~	15:15	~	16:30		TM22 L6		Subaru	-		6/28/22			20220628
				~	17:20	~	19:20		TM22 IMG		L3	WP7	6/29/22+	6/28/22			20220628

## B11
Batteries: B11	A					20160421_4/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Applied	MA2	BC1	Usually	8/1/22	30%	100%
2016	Apr	21	Th					B8-11	BFMS TSP IMG	New	L					20160421
	May	8	Su					L0				85%		20160508
				5/8/16			20160508
		10	Tu		06:10					Bulk		BC1	Continuous				20160510
				07:10					20160510
				07:22					20160510
				07:52					20160510
				07:59					20160510
				08:12					20160510
				08:17					20160510
				08:41					20160510
				08:47					20160510
				09:33					20160510
				09:56					20160510
				10:05					20160510
				10:47					20160510
				11:48					20160510
				14:13					Absorption					20160510
				14:57					Float					20160510
				~	15:10					5/10/16			20160510
				~	15:15					L					20160510
		24	Tu					B4 B5					100%	20160524
	Jun	13	Mo		16:25					Equalization					20160613
		14	Tu					Float					20160614
	Nov	27	Su	~	12:15					Applied	L1	C1	11/27/16				20161127
	Dec	16	Fr	~	13:45	~	15:00			Bulk	L	BC1	Continuous		25%		20161216
		19	Mo					Float				12/19/16			20161219
2017	Jan	3	Tu	~	10:50	~	11:30			Applied	L1	C1-2	1/3/17			100%	20170103
		19	Th					Waiting Charge		L				0%		20170119
		20	Fr	~	06:40					Bulk		BC1	Continuous				20170120
		21	Sa	~	14:15		15:15			Float					20170121
		22	Su					1/22/17			20170122
	Mar	29	We					Applied	L1	C1/2/6	3/29/17			100%	20170329
	Nov	3	Fr	~	16:15					Charging	L	BC1	Continuous		39%		20171103
		4	Sa					11/4/17			20171104
		5	Su					Float				11/5/17			20171105
		28	Tu	~	15:30					Applied	L1	C1/2/6	11/28/17			100%	20171128
	Dec	22	Fr	~	14:15					Charging	L	BC1	Continuous		37%		20171222
		23	Sa					12/23/17			20171223
		29	Fr	~	14:00					Applied	L1	C1/2/6	12/29/17			100%	20171229
2018	Jan	15	Mo	~	12:00					Charging	L	BC1	Continuous		44%		20180115
		18	Th					1/18/18			20180118
	Feb	24	Sa	~	09:30					Applied	L1	C1/2/6	2/24/18			100%	20180224
	Mar	29	Th	~	13:53	~	15:00				L					20180329
				~	17:45		18:15		WRD	Charging	L0	WP2	Continuous		8%		20180329
	Apr	2		~	15:15				WRD EML					20180402
		3	Tu	~	06:00		06:45		WRD	Absorption	L	BC3		4/3/18		100%	20180403
				08:45			Float					20180403
	Jun	11		~	04:00			B8/11		Available	MA2		6/11/18	6/11/18		100%	20180611
	Nov	2		~	06:25					Applied		BC1	It Will Be		90%		20181102
2019	Mar	15	Fr	~	08:00					3/15/19			100%	20190315
		17	Su			~	22:30					Most of the time		75%		20190317
		19	Tu	~	09:30					3/19/19		100%	20190319
	Apr	18					90%		20190418
				100%	20190418
		25					90%		20190425
		27					100%	20190427
	Jun	22	Sa	~	05:00					Available		-	6/22/19				20190622
	Aug	5					L					20190805
		11	Su	~	02:30	~	02:45		WP5			BC1			92%		20190811
	Sep	5	Th	~	12:15	~	12:30			W100 Test	L0	WP5	8/12/19	9/5/19		100%	20190905
2020	May	8	Fr					WP5	Available	L	-	5/8/20				20200508
		10	Su	~	13:45	~	14:45				MA2			5/10/20			20200510
		23	Sa	~	12:00					Applied	MA2	BC1			90%		20200523
	Nov	21	Sa	~	10:00	~	11:00					Usually	11/21/20	50%	100%	20201121
2021	Jun	26	Sa					6/26/21	90%		20210626
	Jul	17	Sa					BC1		7/17/21	60%		20210717
	Dec	25	Sa					S2			BC1		12/25/21			20211225
2022	Apr	17	Su					80%	100%	20220417
	Jul	2	Sa					7/2/22			20220702
	Aug	1	Mo					8/1/22	30%	100%	20220801

## B12_13
Batteries: B12_13	A					20150805_7.5_1: SigmasTek SP12-7.5

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	Continuous
2015	Jul	31					[B12_13-18_21] Ordered from BatterySharks.com	EML	On Order				20150731
	Aug	5					[B12_13-18_21] Received		Available	L			20150805
		6					Installed in UPS PS700_1 ('Liebert Powersure Interactive 700' ), placed in service in the garage (light over bench)		Applied		A2	Continuous	20150806
2017	Oct / ?	?					The batteries went dead (they self-destructed, melted, deformed); It is sometimes very hot in the garage, so I'm not surprised, because the SigmasTek datasheet says the long term float life is ~2-4 years at 86⁰F / Batteries added to pile in W side storage for recycling.		Dead	Salvaged	-		2017MM?

## B14_15
Batteries: B14_15	A					20150805_7.5_2: SigmasTek SP12-7.5

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	Continuous
2015	Jul	31					B12_13-18_21	EML	On Order				20150731
	Aug	5					Available	L			20150805
		6					Installed in UPS PC_1 (A4, 'Powercom KIN-1000AP') and placed in service in front room (reading lights)		Applied		A4	Continuous	20150806
2018	May	1					UPS dead: very warm		Unknown	L0			20180501
		3					Opened UPS and found batteries to be 'toast', one of them deformed; UPS OK; Batteries were in service 2 years 9 months / I'm not surprised, because the SigmasTek datasheet says the long term float life is ~2-4 years at 86⁰F; Batteries added to pile in W side storage for recycling.		Dead	Salvaged	-		20180503

## B16_17
Batteries: B16_17	A					20150805_7.5_3: SigmasTek SP12-7.5

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	7/17
2015	Jul	31					B12_13-18_21	EML	On Order				20150731
	Aug	5					Available	L			20150805
		6					Installed in UPS PS700_2 ('Liebert Powersure Interactive 700'), plugged in but not placed in service				A3	Continuous	20150806
				Installed UPS at Mark Hall residence on SERVANT2 (date of installation unknown, but probably within a month after I installed the batteries)		Applied	Hall Bsmt			20150806
2017	Jul					Mark died, and they shut down SERVANT2, and may have also unplugged the UPS		Unknown			7/17	20170706
2018	May	7					I visited Sheila and Isaac and it does not look like the UPS had been plugged in (dead when pressing front power button) / Returned unit to shop; Batteries are deformed, melted, 1.26v total for both batteries in series		Dead	Salvaged	-		20180507

## B18_21
Batteries: B18_21	A					20150805_18: SigmasTek SP12-18

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	Continuous
2015	Jul	31					B12_13-18_21	EML	On Order				20150731
	Aug	5					Available	L			20150805
		13					Attached externally to UPS GXT2_2 (A6, Liebert 1500VA) and placed in service in rear room on T1 shop circuit (exact date unknown, but labels for system in rear room were printed 8/12/18)		Applied		A6	Continuous	20150813
2018	May	3					Photos of 20150805_18 (B18_21) and 20150813 (B22_25) batteries	IMG					20180503
		5					Photos of UPSs: GXT2_1, GXT2_2, 20150805_18 and 20150813 batteries					20180505
		6					Photos of 20150805_18 (B18_21) and 20150813 (B22_25) batteries; See .doc for 'Liebert UPSs Battery Test' (videos) / Both GXT2_1 and GXT2_2 UPSs and batteries are good for >1 hour operation with typical loads on shop circuits T1 and T2	IMG AED					20180506
		12	Sa		08:24		09:31	Power outage in Wood Heights area including Rayville, 1 hr 7 mins: I continued working at T400s with some careful use of power on the T1 and T2 circuits (and it looked like I would have had another 30 mins of backup power if it had been needed)					20180512
	Jun	2	Sa	~	05:30			Brownouts: T1 circuit kept going OK					20180602
				~	05:48	~	12:24	Power outage, 6-1/2 hours; I minimized the loads and kept GXT2_2 (T1) and GXT2_1 (T2) going; T1 died completely at ~08:35; T2 died completely at ~11:55; Power restored at ~12:24					20180602
2019	Mar	31	Su					Batteries --> Salvage		Dead	Salvaged	-		20190331

## B22_25
Batteries: B22_25	A					20150813: SigmasTek SP12-18

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	Continuous
2015	Aug	8					Ordered from BatterySharks.com	EML	On Order				20150808
		13					Received		Available	L			20150813
				Attached externally to UPS GXT2_1 (A5, Liebert 2000VA) and placed in service in rear room on T2 shop circuit (exact date unknown, but labels for system in rear room were printed 8/12/18)		Applied		A5	Continuous	20150813
2018	May	3					Photos of 20150805_18 (B18_21) and 20150813 (B22_25) batteries	IMG					20180503
		5					Photos of UPSs: GXT2_1, GXT2_2, 20150805_18 and 20150813 batteries					20180505
		6					Photos of 20150805_18 (B18_21) and 20150813 (B22_25) batteries; See .doc for 'Liebert UPSs Battery Test' (videos). Both GXT2_1 and GXT2_2 UPSs and batteries are good for >1 hour operation with typical loads on shop circuits T1 and T2.	IMG AED					20180506
		12	Sa		08:24		09:31	Power outage in Wood Heights area including Rayville, 1 hr 7 mins: / I continued working at T400s with some careful use of power on the T1 and T2 circuits (and it looked like I would have had another 30 mins of backup power if it had been needed)					20180512
	Jun	2	Sa	~	05:30			Brownouts: T2 circuit was dropped briefly (there was a pretty good load at the time, as I was using T400s and both monitors); This could be an indication that the batteries are close to 'end of life'					20180602
				~	05:48	~	12:24	Power outage, 6-1/2 hours; I minimized the loads and kept GXT2_2 (T1) and GXT2_1 (T2) going; T1 died completely at ~08:35; T2 died completely at ~11:55; Power restored at ~12:24					20180602
		30	Sa	~	11:40			UPS GXT2_1 beeping, red "Fault Indicator" light is lit, A&C LEDs (UPS failed battery test, long beep every minute): This is while I was using T400s with both monitors on; Battery pack is very warm / Pressed On for > 1sec which silenced beeping, but Fault Indicator remains on (red); CONCLUSION: batteries are toast		Hot/Bad				20180630
	Aug	31	Fr	~	06:15			Brief power failure (thunderstorm), GXT2_1 (A5) beeping and error indications, no output, disconnected input power and turned OFF, power to T2 circuit bypassed		Dead				20180831
2019	Mar	31	Su					Batteries --> Salvage			Salvaged	-		20190331

## B26
Batteries: B26	A					20170718: SigmasTek SP12-100

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L18	WP1	7/26/22+?
2017	Jul	14					Ordered from BatterySharks.com	EML	On Order				20170714
		18					Received		Available	L			20170718
	Aug	6					In service testing WISPer #1	WRD	WISPer #1 Testing	L0	WP1	Continuous	20170806
		7					Photos of WISPer#1 bench testing	IMG					20170807
	Sep	5					Photo with WISPer#1					20170905
		6					WISPer #1 and battery installed at RCWT (final payment rec'd from TurboNet)	IMG TW1	Sold	L3			20170906
2019	Apr	2	Tu		09:05		10:35	Onsite at RCWT: 48⁰F, battery 14.1vdc, load 15.2vdc (DC Netonix is running but no loads on it, Schottky is blocking, Tcomp on battery charger is AOK, s/b 14.15vdc battery) / Removed AC, battery 13.9vdc, load 13.6vdc (AOK); AC on, battery 13.8vdc, load 15.2vdc (AOK); Power supplies are both cold; No visible signs of heat damage; Everything is working as it should / Waited ~20 mins for Keith to show up; 'Show and Tell', discussion [Service Call to be billed as 'No Fault Found' and 'Defective DC Netonix']	DBT					20190402
2021	Mar	12	Fr	~	10:25	~	11:55	Onsite at RCWT for the Backup Power Supply Maintenance Program; See L3 for details	DBT TM21S SMS SSC		L3	WP1		20210312
		13	Sa					Email Report to Mark and Keith; ; See L3 for details	EML TM21S				3/13/21	20210313
	Aug	5	Th	~	07:45	~	08:55	Onsite at RCWT: Workers painting the tower unplugged WP1 1-8 hours and destroyed the Netonix with water; Battery SoC at worst ~70% based on testimony of workers; See L3 for details / Note added 12/20/21, 12/26/21 August 4th is when the W50 most likely blew its fuse, either from the water on the Netonix (load short, most likely cause) or when recovering the SLA after the power was restored (not likely)	SMS TM21F		L3		8/6/21+?	20210805
	Oct	15	Fr	~	12:00	~	12:47	Internet down @ shop (see RW for details); Caused by power loss @ RCWT; Battery SoC estimated ~95% (~40w load, ~2.6AH)	SMS SSC TM21F		L3		10/16/21+?	20211015
		22	Fr	~	16:13	~	17:11	Internet down @ shop (see RW for details); Caused by power loss @ RCWT; Battery SoC estimated ~95% (~40w load, ~3.2AH)	SMS TM21F				10/23/21+?	20211022
		24	Su	~	16:44	~	17:40	Internet down @ shop (see RW); Most likely caused by power loss @ RCWT (but not sure, I didn't contact Mark & Keith); Battery SoC ~95% (~40w load, ~3.1AH)	TM21F				10/25/21+?	20211024
	Dec	16	Th	~	15:20	~	16:15	Onsite at RCWT: Power and Netonix are OFF; SLA 12.71vM OCV; 15:36 W50 powered by Trace, 12.71vM no charging, Netonix is up (~2.65aE @ 15.05vM = ~40w) / 15:49 Their other stuff powered by Trace (~0.43aE @ ~120vac = ~52w); 16:07 Call to Mark (4m), I told him the battery is "shot" [I found out later the W50 fuse was open] and the W50 won't handle everything at site (if Keith puts the other stuff on the Netonix ~90w), we agreed to meet @ RHS for him to give me the 27TMX and for me to get the W100 from RHST ...; Departed for RHS	TM21F SMS		L3	WP1	3/13/21-8/4/21	20211216
				~	17:20	~	19:15	Onsite at RCWT: AC power is ON; SLA 12.71vM not charging (once again, due to blown fuse, but I thought it was "shot"); Removed SLA and W50 to take to shop			Subaru	-		20211216
		17	Fr	~	01:25	~	02:35	SLA cleaned and on the bench; 12.648vI OCV (~92.5% SoC by OCV according to Trojan chart, which probably applies); Discovered and replaced W50 PS1 blown fuse; Charging / CONCLUSIONS Fuse was blown by load short on 8/4/21, battery has been resting and there has been no backup for 4.4 months	TM21F		L0	WP1		20211217
				~	12:50	~	16:05	Installed in Engel Battery Enclosure and stabilizing towards 25.0⁰C; W50 BTS on top of the battery covered with 1/2" foam insulation	TM21F PLN					20211217
				~	17:10	~	17:25	Checked and corrected W50 Float @ 25.0⁰C: 13.508->13.635vI (shooting for 13.65vI, very hard to get any closer) (0.33aE, ~4.5w); Started a series of W50 BTS checks, stabilizing towards 5⁰C ...	TM21F PLN Z0			WP1		20211217
		19	Su					Finished series of W50 BTS checks @ 25.0⁰C (0.18aE, 13.642vI) and 30.0⁰C [See TM21F 1/28/22 for Analysis and Conclusions]; Engel left at 30.0⁰C overnight for stability testing ...				WP1		20211219
		20	Mo				17:55	Engel set reduced to 21.0⁰C (regulating on battery) for W50 Autopsy (Why did it blow the fuse?); B26 is very fully charged, W50 0.19aE, 13.75vWL (2.6w) ...; ITECH CC Battery Test started	TM21F PLN Z0				12/18-20/21	20211220
		21	Tu		01:55			ITECH Battery Test discharge ended at 8.00 hours, resting; Library\SigmasTek\20211220^21 Discharge; SigmasTek SP12-100, 3.3a to 8h, 21⁰; Wattmon Data & Graphs.ods / 26.66 AH discharge total (ITECH and Wattmon); ~74% SoC by OCV (3 hr rest); Useable capacity (21⁰C, 3.333a) estimated as ~103 AH, and probably could maintain a 40w load for >24 hours @ 25⁰C / Battery capacity is phenomally good for being 4.5 years old (but this battery has been at RCWT in a cool ambient with no deep discharges)	TM21F LIB					20211221
				~	13:15	~	21:58	Recovery started ...; Recovered to 100% Wattmon SoC (0.48aWL)	TM21F Z0			WP1		20211221
		22	We					Recovery Analysis	TM21F LIB					20211222
				~	08:04	~	11:58	Slight discharges during ITECH testing of W50 high power limits (PS1 fuse blown)	TM21F SSC IMG					20211222
				Engel set increased 21->25⁰C (Engel stabilization testing)	TM21F PLN Z0					20211222
		23	Th	~	15:32			Engel set -20⁰C (but not sure it will get there)					20211223
		25	Sa	~	22:05			Engel did not reach -20⁰C (lowest seen -17.7/-18.5 battery/air); Engel set -15⁰C to setup for D&R @ 75w test					20211225
		26	Su		10:15			Discharge started: Engel regulating @ -15.0⁰C; ITECH 75.00w Load; W10 logging (unfortunately, no temperatures) and automatic control to end discharge / The Engel is struggling to maintain -15⁰C as the ~7a discharge is warming the battery significantly				-	12/22-26/21	20211226
				17:43			Discharged ended and Recovery started (W10 automatic control): 10.85vWL minimum @ ~7.8a discharge; Wattmon integration 53.59 AH discharge to 48.96% SoC (based on 105AH capacity) / Engel did not maintain regulation at -15⁰C (no notes on how bad it got, I was sleeping) / Library\SigmasTek\20211226 Discharge; SigmasTek SP12-100 (WP1-W50 Schottky), 75w to 9.6v, -15⁰~-12⁰; Wattmon Data & Graphs.ods	TM21F LIB			WP1		20211226
		27	Mo	~	02:30	~	02:40	During Recovery the Engel was warmer than -9.0/-12.1 (battery/air ⁰C) as now it is cooling down slowly as charge current drops through 1.39aE	TM21F PLN Z0					20211227
				~	09:30	~	10:00	Engel set 25.0⁰C, Engel OFF, Heat 40 ...; Removed air gap shrink tubing and set Heat 50 (battery now warming up as rapidly as possible w/o opening cover); Battery is not yet 100% SoC					20211227
				~	10:48	~	10:54	7.1/30.8 (battery/air ⁰C), Air is +23.7 above Battery; Opened cover ~2m to examine condensation (a pool in the bottom and some on B26) and heat pad temperatures are too hot to touch except briefly (100⁰C?) ...; 8.3/31.6, Air is +24.3 above Battery; Charge 0.52aE rising, if the battery was fully charged I would expect the charge rate to be dropping as the charge V drops (for higher BTS T), BUT it's rising (this is probably due to better migration in the paste of the SLA, and this effect might also be seen with an FLA)					20211227
				~	15:10			25.5/28.4 (Battery T is staying high); Set 25.2, Heat 5, Engel ON; Although not yet completely stabilized, these settings s/b good for the night for a target of 25.0⁰C					20211227
				14:25		17:46	100% WSoC, 5.9wWL ...; 13.63vWL, 0.22aWL, 3.0wWL (dropping, battery fully recovered @ 25.0⁰C)	TM21F PLN					20211227
				Recovery Analysis	TM21F LIB			WP1		20211227
		28	Tu	~	07:27			Heat and Engel OFF, cover opened, fans OFF [W50/B26 Testing Concluded until after catching up on invoicing and recordkeeping]; Battery T will rise and fall daily with shop ambient	TM21F PLN Z0				12/28/21+	20211228
				20211228 Credit - Richmond City.pdf; Recommendations for Further Discussion (W50/SLA should go to WWT, T-105s from WWT should go to RCWT)	TM21F DBT L3					20211228
		29	We					Photos of Engel Battery Enclosure; Review of Heater Pad purchase on Zoro.com [Sa1/1/22 SSC of approved review on Zoro.com]	DNT IMG SSC Z0					20211229
2022	Jan	28	Fr					Calc analysis of W50 BTS tests (data from 12/18-19/21) Conclusions (compensation average, wrong float voltage)	TM21F LIB SSC			WP1		20220128
		30	Su					Calc analysis of W50/SLA Recovery (data from 12/21-22/21) Conclusions	TM21F LIB					20220130
	Feb	17	Th	~	11:30			WP1 removed from bench, B26 removed from Engel (placed under bench on maintenance charge)	DRD		L	WP1		20220217
	Jun	28	Tu					Prepared W50/B26 for installation at WWT: Battery cleaned; Inventory Sticker 0.47.lbx	TM22 LBX		L0			20220628
				~	14:20	~	14:55	Onsite at TLNB: Keith stated his intentions that WWT would eventually be AC only (3 customers) and that he'd pull the W50/B26 (yet to be installed there today) for use at Carrollton (L18 CFS)	TM22 L16		Subaru	-		20220628
				~	15:15	~	16:30	Onsite at WWT: Installed to replace B9/10 T-105s; BTS silver-taped to top of battery ~35⁰C (~95⁰C); 13.34vM (13.27vF equivalent, good Float V for current battery T); Float ~0.030aE	TM22		L6	WP1	6/29/22+	20220628
	Jul	19	Tu					Call from Keith: Ordered new site CFS; He removed the W50/SLA from WWT to take to CFS (sometime while I was in CO in the past two weeks) / B26 is in Keith's service vehicle but will probably be installed at CFS on Mo7/25 when he goes to string the cables (including the Power Cable Assembly on order)	T48-4		L18			20220719
		21	Th	~	11:05	~	11:35	With Keith at shop to discuss Power Cable Assembly for CFS: I saw B26 (from WWT) in the back of his vehicle (HOT!) and he confirmed again that the W50 is partially installed at CFS / He plans to be onsite at CFS Mo7/25 to install cables and hookup the W50/B26/Netonix/antenna					7/26/22+?	20220721
	Aug	25	Th					Call from Mark and Keith: CFS is up and running on W50/B26	T48-3		L18			20220825
	Sep	15	Th					B26 mentioned in Report (discussed move to CFS with Keith Tu7/19): / 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 DBT EML		L18			20220915
	Dec	28	We		12:00		14:00	Onsite at CFS: B26 behind T-105s (photo); WP1 is sandwiched behind the enclosure up against the wall, on edge horizontal, powers the DC Netonix / Keith plans to come back "maybe next week" to move all loads to the W150 (some now on AC, some now on WP1/B26) / Keith may move WP1/B26 to CCC (new Location L19) after he gets done with it at CFS	T48-4 IMG		L18	WP1		20221228

## B27_28
Batteries: B27_28	A					20171108: SigmasTek SP12-100

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L16	A2	7/6/22+
2017	Nov	6					Ordered from BatterySharks.com	EML	On Order				20171106
		8					Received		Available	L			20171108
				Installed on (attached to) UPS PS700_1 ('Liebert Powersure Interactive 700')	Fiber UPS Testing		L0	A2	Continuous	20171108
		9					UPS and batteries installed on fiber setup in TurboNet Lexington office basement (final payment rec'd from TurboNet)	TA1 DBT	Sold	L4			20171109
2018	May	8					I was in Lexington (to install WISPer #2 W100 at WWT): Fiber setup is running somewhere between 113-225 watts (Liebert UPS PS700_1 shows 2 bars out of 4, 450/2 = ~225 watts) / I told Keith it would probably only go about 8 hours at that load.					20180508
2020	May	8	Fr					Onsite at TL (to deliver WP5/B56 to LWT and discuss other spinoffs): Inspected; 27.45v Fluke; No heat, no bulging, no cracks; Mark and Keith reported a 30 min outage a few weeks ago and no problems	L4					20200508
	Aug	11	Tu	~	12:05	~	13:45	While with Keith onsite at Swafford tower he related that he had just gotten the fiber setup with UPS moved to the New Building (A2/B27_28 L4->L16)	L4		L16	A2		20200811
2021	Mar	14	Su	~	12:20	~	13:30	Onsite at TLNB for the Backup Power Supply Maintenance Program; Ambient 85⁰F; See L16 for details	DBT TM21S SMS				3/15/21+	20210314
	Aug	13					Lexington office discussion with Keith (MikroTik) / [Note added 12/27/21 (during .ods General Review): I remember checking on the server room and found that they had installed an air conditioner to lower the ambient / It was about 75⁰F (Keith had a thermostat reading this) and I recommended he set it to 68⁰F (which I saw him do)]	TM21F		L16			20210813
	Sep	22					Lexington Meeting with Keith and Mark (MikroTik) / [Note added 12/27/21 (during .ods General Review): I remember checking on the server room and it was nice and cool (I had asked Keith to set the A/C thermostat at 68⁰F)]					20210922
2022	Mar	9	We	~	14:06			SMS from Mark "I think we need this at the Lexington tower" and photo of Liebert UPS and batteries on fiber backbone / Images\DC\20220307;09DC MO, Lexington, From Mark Webb, TurboNet; LWT Power Outage, TLNB Server Room [O]\20220309 1503 From Mark Webb, MMS, TLNB Server Room IMG_0039.heic and .jpeg	TM22 SMS IMG		L16			20220309
	Jul	5	Tu					Lexington Power Failure, Call to Keith: Power loss for several hours in Lexington; Based on a 56w load (exact wattage unknown) for 3 hours (exact duration unknown) this was a 7AH discharge			L16		7/6/22+	20220705
		22	Fr					Lexington Power Failure: Keith notified me of this when he was here at the shop to pickup the power cable for CFS / When he left the Lexington shop at about 11:00 the power had been off for about 30m and the Liebert was showing 4/4 bars battery remaining; I didn't hear about when the power was restored	T48-4 TM22					20220722

## B29_34
Batteries: B29_34	A					20171212_1: SigmasTek SP12-9

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	-
2017	Dec	7					[B29_34-47_52] Ordered from BatterySharks.com	EML	On Order				20171207
		12					[B29_34-47_52] Received		Available	L			20171212
				Installed in 'TrippLite SU3000RTXL3U' UPS JC#20 (TL3_2, A26) Left side 'six-pack' (exact date unknown)		Testing	L0	A26	Continuous	20171212
		20					[B29_34-47_52] UPS delivered to Richmond High School (installed, final payment rec'd from TurboNet) - 1 Year Warranty	TA2 DBT	Sold	L5			20171220
2021	Feb	24	We	~	12:15	~	17:00	[B29_34-47_52] Travel and onsite at RHS: Removed batteries from TL3_2 and TL3_3 (to shop); Photos	L5 IMG TA2	Weak	Subaru	-	-	20210224
	Mar	3	We	~	14:50			[B29_34-35_40] Salvaged batteries from RHS installed in TL3_7 and TL3_5 and Float rotation started (can only power 1 UPS at a time)	L5		L	A29		20210303
		4	Th			~	15:00	[B29_34-35_40] 24 Hour Float completed (UPS disconnected from AC power)					3/4/21	20210304
	Oct	1	Fr					[B29_34-47_52] Batteries from RHS -> Midwest Scrap Management	BR	Dead	Salvaged	-	-	20211001

## B35_40
Batteries: B35_40	A					20171212_2: SigmasTek SP12-9

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	-
2017	Dec	7					B29_34-47_52	EML	On Order				20171207
		12					Available	L			20171212
				Installed in 'TrippLite SU3000RTXL3U' UPS JC#20 (TL3_2, A26) Right side 'six-pack' (exact date unknown)		Testing	L0	A26	Continuous	20171212
		20					B29_34-47_52	TA2 DBT	Sold	L5			20171220
2021	Feb	24	We	~	12:15	~	17:00		L5 IMG TA2	Weak	Subaru	-	-	20210224
	Mar	3	We	~	14:50			B29_34-35_40	L5		L	A29		20210303
		4	Th			~	15:00					3/4/21	20210304
	Oct	1	Fr					B29_34-47_52	BR	Dead	Salvaged	-	-	20211001

## B41_46
Batteries: B41_46	A					20171212_3: SigmasTek SP12-9

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	-
2017	Dec	7					B29_34-47_52	EML	On Order				20171207
		12					Available	L			20171212
				Installed in 'TrippLite SU3000RTXL3U' UPS JC#21 (TL3_3, A27) Left side 'six-pack' (exact date unknown)		Testing	L0	A27	Continuous	20171212
		20					B29_34-47_52	TA2 DBT	Sold	L5			20171220
2021	Feb	24	We	~	12:15	~	17:00		L5 IMG TA2	Weak	Subaru	-	-	20210224
	Mar	3	We	~	14:25	~	14:50	[B41_46-47_52] Salvaged batteries from RHS installed in TL3_7 and TL3_5 and Float rotation started: 25 mins Float (will return later, can only power 1 UPS at a time)	L5		L	A31		20210303
		4	Th	~	15:00			[B41_46-47_52] Float started (AC power applied to UPS)					20210304
		5	Fr	~	15:00			[B41_46-47_52] 24 Hour Float ended (AC power removed from UPS)					3/5/21	20210305
	Oct	1	Fr					B29_34-47_52	BR	Dead	Salvaged	-	-	20211001

## B47_52
Batteries: B47_52	A					20171212_4: SigmasTek SP12-9

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Dead	Salvaged	-	-
2017	Dec	7					B29_34-47_52	EML	On Order				20171207
		12					Available	L			20171212
				Installed in 'TrippLite SU3000RTXL3U' UPS JC#21 (TL3_3, A27) Right side 'six-pack' (exact date unknown)		Testing	L0	A27	Continuous	20171212
		20					B29_34-47_52	TA2 DBT	Sold	L5			20171220
2021	Feb	24	We	~	12:15	~	17:00		L5 IMG TA2	Weak	Subaru	-	-	20210224
	Mar	3	We	~	14:25	~	14:50	B41_46-47_52	L5		L	A31		20210303
		4	Th	~	15:00					20210304
		5	Fr	~	15:00					3/5/21	20210305
	Oct	1	Fr					B29_34-47_52	BR	Dead	Salvaged	-	-	20211001

## B53
Batteries: B53	A					LI_20180601: Sharpcost 5250mAh Li-Ion for Samsung GT-I9300

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Discarded	-	-
2018	May	30	We					Ordered from Amazon.com (Sharpcost)	EML	On Order				20180530
	Jun	1	Fr					Received		Available	L0			20180601
		4	Mo					Photos; Inventory sticker applied; Installed in Samsung phone	IMG	Applied	L	GT-I9300		20180604
2019	Jun	18	Tu					Discarded (phone has been locking up and shutting down whenever I shoot pictures, battery was toast)		Discarded	-	-		20190618

## B54
Batteries: B54	A					20190605: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L1	WP3	4/27/21	3/1/22	47%	100%
2019	Jun	5	We					Purchased at BFMS, $166.50 + 78 miles @ $0.58; On this trip I also went to Wabash to recycle batteries, visited Karen Thomas, went to Lowe's and Price Chopper in Liberty; Therefore WP5/W100_4 Mileage and Hours is 1/4 what it would normally take; But cost on Batteries Summary Sheet is typical (not shared with other errands) / Originally slated for Odessa	WP5 BFMS	Available	Subaru					20190605
		8	Sa	~	09:30	~	17:30	Moved battery from Subaru to shop; Watered (all down ~1/8", but remember it isn't fully charged now); 12.18 OCV (Fluke); Inventory sticker applied; Charging on ENC (BC3), looking for 14.2v Absorption and 13.4v Float …; I noticed 14.22v, flashing orange (I don't know when the ENC switched to Absorption regulation)	Initial Charge		L0	BC3		6/8/19			20190608
		9	Su	~	01:00			I noticed it is now 13.44v, flashing green (I don't know when the ENC switched to Float regulation)		Float					20190609
		22	Sa	~	04:45			27TMX removed from ENC, moved to test bench and water levels checked (perfect electrolyte level, no water needed)	W100 Testing			-	6/22/19	6/22/19		100%	20190622
				~	05:30			Quick test of W100_3 and W100_4 (both less than 3 mins, Absorption ~14.4v)				WP4/5					20190622
		28	Fr					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1 / 50% SoC low point as per man'f specifications and Wattmon Coulomb Counting	IMG WRD					50%		20190628
		29	Sa					Parallel testing concluded; Began setup for Series Test with B1	WRD			WP4				100%	20190629
		30	Su		14:00		21:50	1st Series Test, Discharge started …; Discharge to 34.7% SoC as per man'f specs @ 12v average					6/30/19		35%		20190630
	Jul	1	Mo		11:05			1st Series Test finished; Float					100%	20190701
		2	Tu		11:00		12:59	2nd Series Test, Discharge started …; Test failed due to W10 reboot; Discharge to 84.5% SoC as per man'f specs @ 12v average					7/2/19		85%		20190702
				17:36			WP4 transition to Float					100%	20190702
		3	We		09:00	~	15:19	3rd Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190703
		4	Th		01:46			WP4 transition to Float					100%	20190704
				14:30		18:31	4th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190704
		6	Sa		03:34			WP4 transition to Float					20190706
				11:02		13:02	4th Series Test @ 300w Concluded; 2 Hr Equalization with BK_1 …; Equalization ended, continues in Float					100%	20190706
		7	Su					Electrolyte level checked and AOK					7/7/19	7/7/19			20190707
				08:00		21:12	5th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average	WRD					50%		20190707
		8	Mo		04:14		06:40	WP4 transition to Float; Started Equalization …; Ended 30 Min Equalization with BK_1, continues in Float					100%	20190708
				10:18		23:31	6th Series Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190708
				W100 Series Test setup: / WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG					20190708
		9	Tu		06:22	~	12:15	WP4 transition to Float …; WP4 charger disconnected for delivery to Odessa	WRD			-				100%	20190709
		11	Th	~	20:00			WP5 charger (started with Absorption)				WP5					20190711
		12	Fr		02:00		08:12	7th DR Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190712
				18:48			WP5 transition to Float					100%	20190712
		13	Sa		03:00		16:00	8th DR Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190713
				22:52			WP5 transition to Float					100%	20190713
		14	Su		05:23		06:23	1 Hr Equalization on BK_1, continues in Float; Electrolyte levels checked and AOK					7/14/19			20190714
				08:00		12:01	9th DR Test, Discharge started …; Discharge to 50% SoC as per man'f specs @ 12v average					50%		20190714
				W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)	IMG					20190714
		15	Mo		23:30			WP5 transition to Float	WRD				Continuous			100%	20190715
		16	Tu		06:46		09:16	WP5 Absorption with no load					20190716
		22	Mo		05:56	~	08:26	WP5 Absorption with 50w load (triggered by switching trim Variacs OFF/ON, if Genasun sees <12.8v for even a few seconds it will go to Absorption)					20190722
		24	We		03:00		09:59	DR Test #10, 150w to as Low as APC will Go, Discharge started … / Discharge to 10.5% SoC as per man'f specs @ 12v average, but OCV says "new" capacity is higher, see OCV below and WISPer DC UPS Notes					7/24/19				20190724
				~	15:35	~	15:52	OCV 11.74v, and from chart on the wall in the hall this is ~30% SoC (Wattmon SoC ~10%, battery has higher capacity than man'f specs.) … / Charging very slowly against 150w load					30%		20190724
		28	Su		07:53			WP5 transition to Float, but battery was very deeply discharged and ratio is high (it's still charging)					20190728
				15:00		17:00	Equalization on BK_1 …; Continues in Float w/no load					20190728
				~	17:15			Batteries never fail to amaze me! Ratio is yet ~5% (a little higher than it was before Equalization, when it was ~4.5%) / They are not yet fully charged as per 3% rule, but they have to be above 99.5%; Screenshot; Electrolyte level checked and AOK	WRD SSC					7/28/19		100%	20190728
		29	Mo		09:00			DR Test #11 (50w to as Low as APC will Go), Discharge started	WRD				7/29/19				20190729
		30	Tu		09:01		10:50	Discharge to 5.7% WSoC …; 11.469 OCV (18-20% by chart on the wall in the hall)					19%		20190730
				11:00		22:00	Started recovery, charging against 50w load … WP5 transition to Float					20190730
				22:45		01:10	Another Genasun 2.5 Hr Absorption cycle					20190730
		31	We	~	03:15	~	07:45	Ratio 2.5% (2.7w/107AH) …; Ratio 1.9% (2.02w/107AH); Continues in Float					100%	20190731
				10:00		20:35	DR Test #12 (100w to 10% WSoC), Discharge started …; Discharge to 12.8% WSoC (APC quit)					20190731
	Aug	1	Th		04:59		05:12	11.6 OCV (~25% by chart on the wall in the hall) …; Started recovery, charging against 100w load					25%		20190801
				21:56			WP5 transition to Float					20190801
		2	Fr		02:50		18:27	Ratio 4.7% (4.8w/102AH), not fully charged yet but has to be >99.5% …; Ratio 1.8% (1.8/102AH, 13.404v)					8/2/19			100%	20190802
		4	Su		21:00			Began Discharge, DR Test #13 (5.100 Amps CC to 10.5v as per man’f specs.)					20190804
				W100 DR Test Setup, CC with Ballast (BK_1, 6-pack/Heathkit, B54)	IMG					20190804
		5	Mo		15:00		15:36	End Discharge to 10.5v; Calculations and adjustments for temperature show that B54 now has ~90% capacity as per man'f specifications / Charging against 5.099 Amps CC load …; Killed CC load for maximum recovery rate	WRD					0%		20190805
				23:12			Transition to Float					20190805
		6	Tu		22:16		22:39	Ratio 2% (13.502v,2.1w/105AH) …; Electrolyte levels are AOK					8/6/19	8/6/19		100%	20190806
		7	We	~	08:15	~	14:55	Called Keith, NA; SMSs …; Call from Keith: He's in California setting up wireless for a wine train; He'll be back from CA and FL in 1-2 weeks; B54 and W100_2 won't be installed at Lexington until he is back and there is time to do it; I mentioned that RW tower may be finished in about 2 weeks and he said "I don't care"	SMS WP3 L1 WP5					20190807
	Sep	5	Th	~	10:00	~	10:45	Removed from W100 Test Setup for delivery to RW; Added water (1/16" low) …; Keith and Brandon left for RW with equipment box, battery and my post driver		Sold	L1	WP3	9/5/19	9/5/19			20190905
				~	16:23			Keith reports that Netonix is hooked up and running (w/o AC)	SMS					20190905
		6	Fr		13:13		14:20	Call to Keith who is onsite at RW; Mark is on the tower; Please come and help with AC / Prep. and onsite; AC connection finalized; Zip ties; WP3 is in Float …; Returned to shop; Onsite again, silicone in conduit					Unknown		20190906
2020	May	8	Fr					While onsite at LWT Keith reported that he was onsite at RW "a few weeks ago" and that the electrolyte levels were "OK"	L1					~4/15/20		100%	20200508
2021	Mar	10	We	~	14:30	~	16:25	Onsite at RW for contracted maintenance: Battery electrolyte levels were very low with exposed plate in cell 6/6 / Calibration of Netonix Power Supply Input Voltage was not necessary; Therefore 14.2v Float and 28.9w Load were correct from Mo3/8 / Began an hours long discharge to below Genasun spec. of 12.8v to trigger a new charge cycle (12.4v Netonix to be sure) ...	TM21S SMS EML SSC		L1	WP3		3/10/21			20210310
		11	Th	~	08:45	~	09:00	Onsite at RW to reapply AC power and shoot a photo showing the watering system in use: 12.2v low (Netonix); 40°F / Discharge was for 17.25 Hrs and %SoC Low calculated from average amps and slightly derated battery capacity	TM21S SMS SSC IMG					64%		20210311
				11:19			Screenshot of Netonix Input Voltage graph showing Bulk/Absorption transition / Bulk maximum/Absorption 14.8/14.6-14.7v (spec. @ 25⁰C is 14.6/14.4v, so this is OK, as it's currently about 45⁰F)	TM21S SSC					20210311
				13:36			Screenshot of Netonix Input Voltage graph showing transition from Absorption to Float; 13.8v (spec. @ 25⁰C is 13.5v, so this is AOK at the lower temperature)					3/12/21+			100%	20210311
	Dec	23	Th	~	10:27	~	10:30	Logged into Netonix, cleared log, no power losses in past 24 hours, Float 13.7-13.8v	TM21F EML		L1					20211223
		27	Mo	~	06:55			Logged into Netonix: Load ~56w; Float 13.78v	TM21F SSC					20211227
2022	Jan	5	We	~	11:19			Logged into Netonix, no power losses in past 24 hours, Load ~56w, Float 14.0v	TM22 SSC EML		L1					20220105
	Mar	1	Tu	~	17:30	~	17:50	Onsite at RW: Electrolyte OK, ~1/8" above plates; Overfilled slightly (bottom of meniscus at score line, ~1/3 of air slot remains); As it has been about 1 year since I checked the battery it would be good to remember that "the guys" might have done it sometime in the past year and didn't bother to notify me (keep this exposed site with W100 on the "check every 6 months" list); Battery 14.03vF equivalent (14.11vM) at 75⁰F Fluke IRT (slightly high for that temperature, Genasun has not reset lately)	TM22		L1			3/1/22			20220301
	Apr	24	Su	~	09:49	~	19:20	No charging: Netonix notification EML 09:52; Logged into Netonix, SSCs; Load ~18w (battery should last ~48 hrs) ... / Charging resumed (not sure yet why); Bulk ~19:20~20:10; Absorption 14.5vN ~2.5h; Float 13.7vN ~22:40 to ~24:00	TM22 EML SSC		L1		-		88%	99%	20220424
		25	Mo	~	00:00			No charging again: Netonix notification EML 00:06; SSCs, 08:00 shows the entire event so far					20220425
		26	Tu	~	14:40	~	15:35	Onsite: No AC Power; 11.94vM; Load ~1.52aE (~18w); Power restored ~15:03 by wiggling plug in PWSD's exterior outlet	TM22 EML SMS SSC		L1				47%		20220426
		27	We	~	07:00			Logged into Netonix: Battery reached Float yesterday ~21:40; This battery now has 14 discharges to at or below 50% SoC since purchased June 2019 (3 years old)	TM22 SSC				4/27/21			100%	20220427

## B55
Batteries: B55	A					LI_20190618: Acevan Direct 2300mAh Li-Ion for Samsung GT-I9300 with Micro USB charger cable

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Lost	MO River	-
2019	Jun	12	We					Ordered from Amazon.com	EML	On Order				20190612
		18	Tu					Received; Summary completed and inventory stickers applied		Available	L0			20190618
				Installed in phone; Started phone w/o charger; 57%; Will drain completely (as per instructions) then charge and normal use; Scans of instruction card	SSC LIB	Applied	L	GT-I9300		20190618
2020	Jun	7	Su					Phone dropped in the Missouri River		Lost	MO River	-		20200607

## B56
Batteries: B56	A					20200507_1/2: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L10	WP5	4/15/22+	4/14/22	?	100%
2020	May	7	Th					[B56-57] Purchased (2) at BFMS, $166.50x2 + 78 miles @ $0.575	BFMS	Available	L					20200507
		8	Fr		07:08	~	09:30	[B56-57] Inventory and "I NEED WATER" stickers applied; 20200508 27TMX_Trojan_Data_Sheets.pdf; 12.54 OCV / [B56] Trace; Electrolyte levels down ~1/8", added water to ~+1/8"; SoC High Point is estimated based on quick 2 hour charge	LIB	Initial Charge		BC1		5/8/20	83%	95%	20200508
				Loaded into the Subaru for delivery to Lexington, but it wasn't installed on this trip (planning on sometime next week, kept the W100 and battery in the Subaru)		Sold	Subaru	-					20200508
		19	Tu		10:48		11:18	Call from Mark & Keith: Fr10am LWT install …	WP5					20200519
		20	We		04:30		05:15	20200508 Invoice - Lexington Water Tower W100.pdf	WP5 DBT					20200520
				~	07:00			12.60 OCV; Trace	WP5		L0	BC1			88%		20200520
		22	Fr	~	04:25	~	04:35	Removed from Trace	WP5		L	-	5/22/20			100%	20200522
				~	14:00			Installed at LWT (battery on float but no load until ~ Mo5/25)	TW4-5		L10	WP5	5/23/20				20200522
2021	Apr	16	Fr	~	14:30	~	16:00	Onsite at LWT for the Backup Power Supply Maintenance Program; See L10 for details	DBT TM21S EML		L10	WP5	4/17/21+	4/16/21	100%	100%	20210416
2022	Mar	7	Mo					Lexington Area Power Outage Yesterday Evening: MMS "screenshot" of LWT Netonix received from Mark; Analysis and conclusions; Input Voltage graph shows power outage (~2.2h) and Absorption (~2.5h); Float ~13.8v; %SoC Low Point based upon 20w load for 2.2h from C/100 new capacity 117 AH	TM22 SMS IMG SSC		L10		3/8/22+		97%	100%	20220307
	Apr	14	Th	~	10:55	~	15:25	Onsite with Keith, Dakota and Cole: Battery cleaned and tightened nuts; Electrolyte levels "Factory" (~5/8" above plates); Generous fill (1/2 up the slot)	T48-2 SMS IMG		L10			4/14/22			20220414
		15	Fr	~	08:35	~	08:36	(5) Netonix screenshots from Keith rec'd 08:40; [2 printed, analyzed and annotated Fr5/13]: Float 13.67vN, Genasun T-comp is perfect for 15⁰C	T48-2 EML IMG		L10		4/15/22+				20220415
	Jul	5	Tu					Lexington Power Failure: As reported by Keith for TLNB; Most likely also impacted LWT (but not known)	TM22 SMS		L10				?	100%	20220705
		22	Fr					T48-4 TM22		L10				?		20220722

## B57
Batteries: B57	A					20200507_2/2: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L11	WP6	6/17/20 +	4/16/21	99%	100%
2020	May	7	Th					B56-57	BFMS	Available	L					20200507
		8	Fr					LIB					20200508
		22	Fr	~	04:30	~	09:00	Initial charge on BK (with voltages monitored by Fluke): 12.49 OCV; Bulk at 5.1 A until 14.82v; Absorption near 14.82v for 2.5 Hrs; 13.5v float	WP6-10		L0	S2			80%		20200522
		23	Sa	~	07:45	~	08:05	Electrolyte levels down ~ 3/16” ...; Transferred to ENC (float 13.44v Fluke)				BC3	5/23/20	5/23/20		100%	20200523
	Jun	10	We					Slated for WP6	WP6	Assembly…					20200610
		11	Th					Electrolyte levels AOK	WP6					6/11/20			20200611
		12	Fr	~	11:00			Removed from ENC for use in quick tests of WP6-WP10 (<5’ Absorption each WISPer)	WP6-10			-	6/12/20				20200612
				Invoiced for delivery next week	WP6					20200612
		13	Sa	~	17:18	~	18:32	~1 Hr DR Test of WISPer as per WP6-10A Misc ...; Absorption and Float under bench (unusually long Absorption >4.2 hrs, not sure why WP6 did this)	W10			WP6			96%		20200613
		15	Mo	~	03:20			Electrolyte levels AOK		Float	L	WP6	6/14/20 +	6/15/20		100%	20200615
		16	Tu	~	08:45	~	09:15	Loaded Subaru for delivery of WP6-WP8 and B57-B59	WP6	Install…	Subaru	-	6/16/20				20200616
				~	10:30	~	11:00	Onsite at RWWT with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix); Rec’d $1450 TurboNet check	TW6-10	Sold	L11	WP6	6/17/20 +				20200616
2021	Apr	16	Fr	~	12:00	~	14:00	Onsite at RWWT for the Backup Power Supply Maintenance Program; Electrolyte levels down 3/4 to 7/8" (top 1/16" to 1/4" of all plates exposed); See L11 for details	DBT TM21S EML		L11	WP6		4/16/21	99%	100%	20210416
	Dec	27	Mo	~	07:55			Logged into Netonix: Load ~38w; Float ~13.5v (13.38v Netonix adjusted up 0.8% as per onsite error observed 4/16/21)	TM21F SSC		L11					20211227

## B58
Batteries: B58	A					20200610_1/4: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L17	WP11	10/22/22+	10/6/22	3%	100%
2020	Jun	8					[B58-61] Ordered from BFMS	TW6-10 EML	On Order					20200608
		10	We					Received at BFMS; Slated for WP7	BFMS WP7	Assembly…	Subaru					20200610
		11	Th					Cleaned: Stickers applied; electrolyte levels checked (all nominal, above plates); OCV 12.58			L0				87%		20200611
				~	11:42	~	15:30	Started initial charge on BK (with voltages monitored by Fluke): Bulk at 5.1 A until 14.82v ...; Absorption near 14.82v for 2.5 Hrs; 13.5v float	WP7			S2					20200611
		12	Fr					Invoiced for delivery next week	WP7					20200612
		13	Sa			~	04:30	Removed from BK	WP7			-	6/13/20			100%	20200613
		13	Sa	~	18:40	~	19:30	~1 Hr DR Test of WISPer as per WP6-10A Misc ...; Absorption and Float under bench (did not observer time of transfer to float)	W10			WP7			98%		20200613
		15	Mo	~	03:20			Electrolyte levels corrected: ~1/8” low; ~1 jar		Float	L	WP7	6/14/20 +	6/15/20		100%	20200615
		16	Tu	~	08:45	~	09:15	Loaded Subaru for delivery of WP6-WP8 and B57-B59	WP7	Install…	Subaru	-	6/16/20				20200616
				~	11:10	~	11:30	Onsite at RHST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L12	WP7	6/17/20-9/22/21				20200616
2021	Mar	16	Tu	~	13:00	~	13:45	Onsite at RHST for the Backup Power Supply Maintenance Program; See L12 for details	DBT TM21S SMS EML		L12	WP7		3/16/21			20210316
	Sep	22	We	~	14:45	~	15:15	Onsite at RHST for Fall 2021 Maintenance / Battery removed & W100 AC disconnected (there has been no Netonix load since 6/16/20, will take battery to shop for maintenance)	TM21F IMG L12		L	-					20210922
	Oct	20	We					Cleaned; OCV 12.70 F (97.3% SoC); Electrolyte levels are above plates / Charge to Absorption using BK (and W10), 14.82v 10:35-14:02 3.5 hrs, down to 2.9a (Schauer 2512 factory set Trip Point); Float 13.5v 14:04- / Electrolyte checked, 1/4" to 1/2" above plates, generous fill (top of meniscus to score line); Equalization BK 16.25v 14:45-17:29 (2.75 hrs, plateau at 15.23vBK, 15.18vF)	TM21F			S2		10/20/21	97%		20211020
		21	Th					Terminated Float on BK (13.5v, ~0.08 amps); Float on ENC under bench (13.44v F)				BC3	10/21-11/23/21			100%	20211021
		24	Su					Video sent to Pavel via Viber	IMG					20211024
	Nov	23	Tu	~	07:45			Pulled from Float on ENC; Electrolyte levels checked, OK (factory fill), added water for generous fill (top of meniscus to score line, 1/2 way up the slot) / Mark to pickup this morning (he'll take it to RHST, and hopefully let me know when it is installed on WP7)	TM21F		Mark	-		11/23/21			20211123
	Dec	16	Th	~	16:25	~	16:45	Onsite at RHST: Met Mark in parking lot and 27TMX to Subaru ...; Removed W100 from RHST; B58 and WP7 to be installed at RCWT	TM21F SMS		Subaru					20211216
				~	17:20	~	19:15	Onsite at RCWT: Electrolyte levels checked and AOK; 12.64vM OCV 12-16⁰C (~92% SoC by OCV); Installed sitting on chair / 18:12 W100 plugged into AC (Bulk, Absorption ...) / 18:33 SMS to Mark & Keith "... If another power failure estimated run time is 24 hours (but you've still got equipment not running on the battery back up)." / 18:34 SMS from Mark (also to Keith) "Can you put ALL the equip on the battery backup?"; 18:57 Absorption 0-4aE 14.81-14.91vM / 19:12 SMS to Mark (and Keith) "No, not without Keith to configure the Netonix" / 19:14 SMS to Mark and Keith "Leaving RCWT (all locked up)."; 19:15 SMS from Mark (also to Keith) 'two thumbs up'			L3	WP7	12/17/21+	12/16/21	92%	100%	20211216
2022	Jun	28	Tu	~	17:20	~	19:20	Onsite at RCWT to swap batteries: 27TMX (high on top of electrical box) ~26⁰C (~79⁰F); Ambient ~27⁰C (81⁰F); WP7 (W100_6) fan is running / 14.00vM (13.93vF equivalent, Float V is too high for current battery T, compensation has not reset lately); Float charge ~0.050aE erratic; Removed to take to shop	TM22 L3		Subaru	-					20220628
		29	We					Battery maintenance, B58 (27TMX): There's significant amounts of either electrolyte or condensation that came from the vent covers / It was probably tilted/shaked in removing it at RCWT or on the drive home, as I can think of no way that it could be condensation, seeing as how the battery has been warmer than ambient ever since it left RCWT / Electrolyte generous fill; OCV 12.69vF (96% SoC by OCV); BK equalization pushed significant amounts of electrolyte out onto battery and bench / CONCLUSIONS When equalizing the caps s/b removed; Fill to no more than 1/16" above factory (do not "generous fill")	TM22 L3		L0	S2		6/29/22	96%		20220629
				On BK for Float maintenance while in Colorado: Solid #12 connection, set 13.50v/5.100a	TM22		L	S2	6/30/22+			100%	20220629
	Aug	1	Mo	~	13:30			BK removed to use in equalizing batteries on network (B4-B7) ...				-	-				20220801
		2	Tu	~	20:00			12.64vB (92% by OCV); BK reapplied: Solid #12 connection, set 13.57v/5.1a (B58 on bench ~22-23⁰C)				S2	8/3/22+		92%	100%	20220802
		3	We					Checked electrolyte acid concentration by Specific Gravity: / Research: According to Trojan, SG s/b 1.277 or greater at 80⁰F; Subtract 4 points from reading for every 10⁰F below 80⁰F / Printed SSC of Trojan chart "State of Charge Measure of Open-Circuit Voltage" (27TMX/T-105), 20220803 130548 Screenshot.png which shows that Trojan's concentration is SG 1.277 for 100% charge; The SG of concentrated sulfuric acid is about 1.84 / Measured SG of (6) cells and corrected for 75⁰F (Fluke IRT): Level is meniscus to meniscus +1/16"; 1.251 to 1.273, all low, marginally below "Good" on hydrometer / 30m Equalization: Caps off but covered vent holes with paper towel; BK set 16.2/5.1a; CC for the entire 30m (15.53v high seen); Returned to Float 13.57v/5.1a / Re-measured SG of (6) cells: Corrected values are 1.255 to 1.258, which is much more consistent between cells and higher than first measurement, yet below 1.277 / CONCLUSIONs: Always equalize immediately before measuring SG / See FTR "I think the way to deal with this problem is" (rec'v acid and syringes; remove electrolyte to ~1/8" below fill tube); 98% Sulfuric Acid ordered / Packaged Hydrometer, Watering Jar and Baking Soda in small labeled box; TODO Notes on quoting and ordering 27TMX (need spares for rejuvenations)	TM22 SSC EML		L0			8/3/22			20220803
		4	Th					Syringes ordered (10, 20 and 60cc); See white sheet pencil calculations, it looks like we need to replace about 10cc of electrolyte with 98% acid (will start with 3cc)	TM22 EML WS					20220804
		7	Su					Reduced electrolyte level to meniscus showing on filler tube (~75cc removed from each cell); Added ~13cc of concentrated 98% Sulfuric to each cell (less for cell 4/6) / Equalizations before measuring SG; Acid concentration improved for average SG from 1.257 to 1.271 (s/b 1.277) / Nice numbers, ~1 point for each cc of concentrated acid added (27TMX) / CONCLUSION I hate doing this, and I don't want to ever do it again (unless it's MY BATTERY and I can save a $200 expense by correcting it)	TM22		L			8/7/22			20220807
		20	Sa					BK Float 13.57v ~80mA (~23⁰C bench ambient); Dual Supply Bench Testing Setup Assembled, B58 removed from BK and installed in Engel, target +25.0⁰C	T48-3 L17			BC9	8/21/22+				20220820
		22	Mo					Bench Testing: Various light discharges (Load Supply S13 OFF/ON while BC9 ON and BK used for boost)	T48-3 L17			BC9 S2	8/23/22+		99%	100%	20220822
		24	We					Tested Traco Maximum Power Limits in range 169-187w: S13 OFF/ON while BC9 ON and BK used for boost; Discharge during testing roughly estimated 12AH	T48-3 L17				8/25/22+		89%		20220824
		30	Tu					"W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; This battery is slated for LSWT on WP11	T48-3 L17			WP11					20220830
	Sep	4	Su					Measured BC9 (SCP-75-12) Load Regulation 0~105w; Slight discharges (very slight, mostly surface charge)	T48-3 PLN			WP11	9/5/22+		100%	100%	20220904
		17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG					20220917
		18	Su	~	10:00			Disassembled Bench Test Setup and Wiegmann Backplate: B58 disconnected (no longer under charge but remains in Engel)	T48-3 PLN WP11 IMG			-					20220918
				~	11:43			Maintenance Float provided by BK: Set 13.50v (solid #14 blue/gray ~5')	T48-3 PLN			S2	9/19/22+				20220918
	Oct	1	Sa					Engel (+25⁰C Target): Found Relay Contacts Fused Closed; B58 ~34⁰C (BK float was ~180mA, set reduced to 13.38v until battery cooled down)	T48-3 PLN WP11					20221001
		2	Su					W150_1 Bench Testing Started (+25⁰C): Bench testing setup modified (B58 in Engel); Removed from BK Float (was 13.50v ~78mA); Attached to WP11 (13.51vF) / Short discharges for transition tests; Moving Engel to -15⁰C ...	T48-3 PLN			WP11	10/3/22		99%	100%	20221002
		4	Tu					W150_1 Bench Testing (-15⁰C): Multiple AC OFF/ON Transition Tests with 180wI Traco load during very deep discharge to Traco low voltage cutout (8.2v) / Recovery while heating to +50⁰C: Battery T rose to ~58⁰C when relay contacts on Z19 stuck in heat, but BTS compensated charge was negative or zero (~12.75vF)				WP11	-		3%		20221004
		5	We					Bench Testing (stable at +50⁰C): (Battery is still in recovery); W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 PLN IMG					20221005
		6	Th					Bench Testing (~25⁰C): Recovery complete (0.16aE); Electrolyte checked and filled (1/16~1/8" below filler tube, filled only to meniscus formation) / Schauer Equalize Test (AC ON, 180wI Traco load, Engel open, 1h); Bench Testing Finished (B58 in Engel, cover open)	T48-3 PLN				10/7/22+	10/6/22		100%	20221006
		7	Fr					W150_1 Final Assembly and Invoice Date: Disconnected to finalize assembly; Removed from Engel; Labels applied to W150; Attached for float maintenance	T48-3					20221007
		8	Sa					Photos of W150_1: Product line and orthogonal photos; WP11 and B58 disconnected (they will not be powered again until they are installed at LSWT)	T48-3 IMG WP11			-	-				20221008
		10	Mo					Wiegmann Prep for LSWT: Photos; Installed Z20 Dinico and intake fan assembly, tested; B58 battery spacers, right side of battery centered on the fan	T48-3 IMG LBX L17					20221010
		11	Tu					Loaded Subaru for onsite installation at LSWT	T48-3 L17		Subaru					20221011
		21	Fr					Onsite at LSWT: Windy but warm; Photos; Installed spacers and B58; Fan control system plugged in and tested / Installed WP11; Connected B58, BTS and Z20 T2 on negative post, foam caps, battery terminal spray / Power levels measured, Traco Input 32.6w (27TMX runtime estimate ~>36h), Output 27.5w	T48-3 IMG		L17	WP11	10/22/22+				20221021
		28	Fr					20221011 Report, Photos & Invoice - Wiegmann and Power Cable Assemblies for LSWT.pdf: Emailed to Keith and Mark / B58 photo in Report (inside the Wiegmann on Mo10/10)	T48-3 DBT EML		L17					20221028

## B59
Batteries: B59	A					20200610_2/4: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L13	WP8	6/17/20 +	?	100%	100%
2020	Jun	8					B58-61	TW6-10 EML	On Order					20200608
		10	We					Received at BFMS; Slated for WP8	BFMS WP8	Assembly…	Subaru					20200610
		11	Th					Cleaned: Stickers applied; electrolyte levels checked (all nominal, above plates); OCV 12.47			L0				78%		20200611
		12	Fr					Invoiced for delivery next week	WP8					20200612
		13	Sa	~	19:35	~	20:05	Initial Charge: ~1 Hr DR Test of WISPer as per WP6-10A Misc ...; Absorption and Float under bench (did not observer time of transfer to float)	W10			WP8					20200613
		15	Mo	~	03:20			Electrolyte levels corrected: ~1/8” low; ~3/4 jar		Float	L	WP8	6/14/20 +	6/15/20		100%	20200615
		16	Tu	~	08:45	~	09:15	Loaded Subaru for delivery of WP6-WP8 and B57-B59	WP8	Install…	Subaru	-	6/16/20				20200616
				~	11:50	~	12:35	Onsite at ST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L13	WP8	6/17/20 +				20200616
2021	Jun	21	Mo	~	14:35	~	15:30	Onsite at ST for the Backup Power Supply Maintenance Program; Cell 1/6 plates exposed, all down ~3/4"; 5' discharge	DBT TM21S		L13			6/21/21	100%	100%	20210621
2022	Jun	3	Fr	~	11:27	~	12:01	33m phone call to Keith: "We lost Skeeter tower radios and switch"; This probably happened sometime in the past few weeks, not sure / I don't remember if he said he watered the battery, but he might have done so	TM22		L13			?			20220603

## B60
Batteries: B60	A					20200610_3/4: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L14	WP9	5/12/21 +	?	100%	100%
2020	Jun	8					B58-61	TW6-10 EML	On Order					20200608
		10	We					Received at BFMS; Slated for WP9	BFMS WP9	Assembly…	Subaru					20200610
		11	Th					Cleaned: Stickers applied; electrolyte levels checked (all nominal, above plates); OCV 12.59			L0				88%		20200611
		13	Sa	~	20:11	~	21:27	Initial Charge: ~1 Hr DR Test of WISPer as per WP6-10A Misc ...; Absorption and Float under bench (did not observe time of transfer to float)	W10			WP9					20200613
		15	Mo	~	03:20			Electrolyte levels corrected: Cells 2, 5 and 6 ~OK (neg to pos); Others ~1/16” low; ~1/4 jar		Float	L	WP9	6/14/20 +	6/15/20		100%	20200615
	Jul	6	Mo	~	09:00	~	12:00	Electrolyte levels corrected: Cells 1, 2, 5 and 6 were ~1/16” low; Loaded into Subaru …; Installed at Odessa North Water Tower (not charging but I’m sure KJ will charge); Photos and videos TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb	TW6-10 IMG	Sold	L14	WP9	7/7/20 +	7/6/20			20200706
2021	May	11	Tu	~	09:50	~	11:10	Onsite at ONWT for the Backup Power Supply Maintenance Program; See L14 for details	DBT TM21S EML SSC		L14	WP9	5/12/21 +	5/11/21	100%	100%	20210511
	Nov	23	Tu	~	12:20	~	15:40	Onsite at ONWT with Mark, Keith, Dakota and ?; Installed Mier enclosure with Schauer, T-105s, Traco and Dinico fan control system; WP9 and B60 are still Active	TOI		L14					20211123
2022	Feb	19	Sa					Mimosas stopped working; Keith onsite; (Nothing was said about B60 in the old system enclosure)	TM22 SMS		L14					20220219
		21	Mo	~	09:45	~	11:10	Onsite at ONWT with Keith and Dakota: Keith reported that the 27TMX in the old system was "topped off" (unknown when)	TM22 IMG		L14			?			20220221
	Jun	3	Fr	~	11:27	~	12:01	33m phone call to Keith: Netonix is still being used in old system box, but he has been onsite dealing with it [he may have watered the battery] / He's still hoping to eliminate the old system box, but it will take time	TM22		L14					20220603

## B61
Batteries: B61	A					20200610_4/4: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L15	WP10	10/1/21 +	9/22/21	100%	100%
2020	Jun	8					B58-61	TW6-10 EML	On Order					20200608
		10	We					Received at BFMS; Slated for WP10	BFMS WP10	Assembly…	Subaru					20200610
		11	Th					Cleaned: Stickers applied; electrolyte levels checked (all nominal, above plates); OCV 12.58			L0				87%		20200611
		13	Sa	~	21:31	~	21:40	Initial Charge: ~1 Hr DR Test of WISPer as per WP6-10A Misc ...; Absorption and Float on bench in DR Test Setup [as per log file Absorption ended at 00:01 or ~2.5 Hrs]	W10			WP10					20200613
		15	Mo	~	03:20			Electrolyte levels corrected: Cells 3, 4, 5 and 6 ~OK (neg to pos); Others ~1/16” low; ~1/5 jar		Float	L	WP10	6/14/20 +	6/15/20		100%	20200615
	Aug	14	Fr	~	08:35			Cleaned; Electrolyte levels corrected (only 2 cells slightly low, added about 1/8" to all cells); Float is 13.56v Fluke	WP10	Install	Subaru	-		8/14/20			20200814
				~	10:15	~	17:10	Onsite at New Tower (OT) 2x: Installed box, electrical service, WP10 and B61; Photos	IMG	Sold	L15	WP10	8/15/20 +				20200814
2021	Mar	16	Tu	~	14:10	~	15:50	Onsite at OT for the Backup Power Supply Maintenance Program; See L15 for details; 99.8% SoC Low Point in 10 min discharge test	DBT TM21S SMS IMG SSC		L15	WP10	3/17/21 +	3/16/21	100%	100%	20210316
	Aug	24	Tu	~	18:51			Power was down for ~1.4 hrs; %SoC based on 18.3w, 12.6v, 105AH	EML SSC TM21F		L15		8/25/21 +		99%		20210824
	Sep	22	We	~	13:20	~	14:30	Onsite at OT for Fall 2021 Maintenance; Electrolyte -1/8" to +1/8" above plates, cell 2/6 plates exposed; Disconnected battery for 1 min	TM21F IMG EML SSC				9/23/21 +	9/22/21	100%		20210922
		30	Th	~	13:00	~	19:30	Mark removed & reapplied AC (W100 needed to be reset)	EML SSC SMS TM21F				10/1/21 +				20210930

## B62
Batteries: B62	A					20201215_1/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					[B62-67] Ordered	L5 TA2	On Order					20201211
		15	Tu					[B62-67] Received at BFMS	BFMS		Subaru					20201215
		17	Th					[B62-67] Moved from Subaru to Rubbermaid cart; Cleaned: Stickers applied; Electrolyte levels checked (all nominal, above plates, ~1/4" low); [B62] OCV 12.605	TA2	Prep.	L0			12/17/20	89%		20201217
				~	04:45	~	09:05	Initial charge, individually on BK: Bulk 14.82v until CV [7mins]; Absorption 14.62v for 2.5 hrs; Float for >1 hour [105 mins]				S2				99%	20201217
		19	Sa	~	03:20			[B62-67] Parallel Float on BK (13.5v) ...; Electrolyte levels checked, down 0 to 1/4", average ~1/8", Filled to +1/16", ~1.9 quarts distilled water total	TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45	[B62-67] Parallel Equalization on BK: Set 16.20v (but BK will not have enough power to reach it); After 2 hrs we reached 15.02v (x6=90.12v); Float ...		Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50	[B62-67] Removed from float on BK; MW_2 and MW_3 test to see if we can reach Equalization but after 44 mins it was stuck at ~87v (14.5v each) / Removed from charge; BK (S2) used with MW_1 (S13) to Float	S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30	[B62-67] Attempted to reach Equalization (16.2x6=97.2v) but after 1.5 hours made it only to 95.9-96.0v total; Returned to Float	L5				1/6/21				20210105
		8	Fr	~	07:50			[B62-67] Removed from float on BK_1+MW_1	L5			-	1/8/21				20210108
				~	08:20	~	08:35	[B62-67] Tested MW_3 and MW_4 in series, each set to 48.6v; Failed to reach Equalization (supplies are fighting each other)	L5 S15-S16					20210108
				~	09:07	~	09:38	[B62-67] Tested MW_3 and MW_4 in series/parallel (middle of string tied between power supplies), each set to 48.6v; Failed to reach Equalization, ~89v maximum seen					20210108
				~	09:52	~	09:54	[B62-67] MW_3 and MW_4 set to 45.0v each (15.0x6=45.0x2=90.0), reached maximum 89.9v before quit					20210108
				~	10:01	~	10:06	[B62-67] 14.5x6=43.5x2=87.0 is OK, power supplies stop buzzing within a few seconds and it holds (charge terminated)					20210108
				[B62-67] Fabricated temporary connection from batteries to TrippLite; TrippLite powered up w/o AC (some drain to batteries, not much); Load removed (no charger)	L5 A31					99%		20210108
				~	14:28			[B62-67] Temporary wiring of TrippLite to AC; Float 82.95v=6x13.825v which is 1.95v above Trojan recommendations (81.0v=13.5x6)	IMG			A31	1/9/21			100%	20210108
		11	Mo					[B62-67] Experimented with Equalization boost chargers MW_3/4 on RHS batteries and TL3_7 TrippLite; See L5 for details/conclusions; Two hours at 14.6v (x6) to test ...	L5			A31 S15-16			99%		20210111
				[B62-67] Test concluded, all OK with TrippLite				A31	1/12/21			100%	20210111
		12	Tu					[B62-67] Photos of B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	IMG					20210112
		15	Fr					[B62-67] Researched what is needed to access the Tripp Lite 3kva units via port(s) and ran some tests; See RHS and TL3_7 for details and conclusions / Slight discharges during these tests (%SoC is a good guess as we never dropped much below intrinsic)	L5 A31					99%		20210115
		16	Sa					[B62-67] Removed temporary battery wiring from TL3_7/B62-B67 and replaced with new assembly with (2) battery module connectors (30min loss of Float)	L5 A31		L		1/16/21			100%	20210116
				[B62-67] Tripp Lite TL3_6 moved from W storage to bench and 2nd battery connection attached (15min loss of Float); TL3_6 Float is 82.5v, which is good news as it is ~0.5v lower than TL3_7 and this indicates that the usual Float voltages on these 3kva units may be a closer average to Trojan specs than I thought				A30-31			99%	100%	20210116
				[B62-67] Load testing begins with TL3_7 (see for details): (TL3_6 is OFF no AC); Set up output load of 85% (perfect, probably at least as high as RHS current loads) / Short loss of Float when I had to reset TL3_7 for a General Fault; Discharge began at 15:05 and TL3_7 quit (shut off) at 16:33 (total discharge time 1 hr 28 mins) / Tripp Lite %SoC was way off, thinking it had some small batteries, it said we were at 0% capacity after only 8 mins / Lowest total battery voltage seen 67.2 ((11.2v equivalent) but this was 13 mins before it died; Restored AC, also turned on TL3_6 to speed recovery (it is more important to recharge quickly than to see how long recovery takes with only one UPS / Killed loads: %SoC Low Point is a wild guess (I have no way to determine what it was, but as it ran until the UPS died this is probably a pretty good estimate) / [Note added 1/18/20 (see 2nd discharge test): 20% SoC Low modified to ~60%]	L5 A31 A30 IMG					60%		20210116
		18	Mo					[B62-67] Recovery nearing completion, today at 04:30 almost in Float @ 82.5v (13.75v equivalent) / Boost chargers ON @ 04:32 (87.5v/14.6v) until 07:32 (3 hours, S15-S16); TL3_7 (A31) AC input OFF during Absorption but then back on and TL3_6 (A30) OFF / With both TL3_7 and TL3_6 charging recovery required ~2 days, and so with only one UPS charging it would be ~4 days / Images and videos from Friday and Saturday ORCPM; .ods listed equipment "IMG"	L5					100%	20210118
				~	14:30	~	16:10	[B62-67] 2nd discharge test, 75% load; See TL3_7 and white sheet for details; Discharge began at 14:30; Quit at 16:10 (1 Hr 40 Mins) / 64.6 (10.77 equivalent) lowest bank voltage seen 12 secs before it quit; See TL3_6 for details on A30 self destruction when starting recovery / Battery bank OCV stabilized, 73.3v (12.2v equivalent, 2 Hrs 45 Mins at rest, 57% SoC as per Trojan); Reattached the batteries to TL3_7 and recovery started @ 19:05	L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					[B62-67] Recovery from 2nd discharge test completed: 22:08 Boost ON for 4 hours until Fr1/22 02:08	L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15	[B62-67] Finished and attached the boost charger box assembly and tested Boost/Absorption for 3 hours to see how warm it gets	L5 S15-S16 IMG					20210207
		24	We					[B62-67] Electrolyte levels checked (OK); Battery bank disassembled for delivery to RHS	L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00	[B62-67] Travel and onsite at RHS: Batteries installed; Cables hooked up and attached to UPSs / Top UPS #21 (A27, TL3_3) 82.8-82.9v, bottom #20 (A26, TL3_2) 83.1v (MuRata+~0.25=Fluke), will put all loads on top UPS; Photos	A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15	[B62-67] Onsite again to switch loads over to top UPS; Boost voltage is set too high, the bottom UPS went into OVP bypass beep and error / Adjusted boost down using Fluke, was 43.75v each supply, now 43.25 each supply (14.425 equivalent), 86.3v on Murata (battery bank sticker is wrong) / Brian moved all the loads from bottom UPS (TL3_2) to top UPS (TL3_3) without bringing anything down because they have dual power supplies / T450s2 reports 70% total load on top UPS (2nd discharge test @ shop was @ 75% 1hr40mins, so estimated run-time 1hr50mins, front panel bargraph 3rd of 4 LEDs blinking); Bottom UPS unplugged and mentioned to Brian that he can plug it in to speed recovery; "Pulled the plug" for 5 mins (AOK, 12v equivalent) / Applied (2) labels for front of UPSs TL3_3 and TL3_2 "2/24/21 Batteries Removed ..."; Photos					20210225
	Jul	28	We	~	14:30	~	16:00	[B62-67] Onsite at RHS to water batteries (to finish promised duties for original contract); See L5 for details; Brian ran 3 hrs boost ~Mo8/2	TA2		L5			7/28/21			20210728
	Nov	16	Tu					[B62-67] According to Brian Long there was a "3 hour" power failure last night and the equipment remained powered without fail; He also said that the loads are about the same as they were in Feb and Jul, when I gave an estimate of 1hr 50mins run-time; Therefore the batteries must have been very close to 0% capacity at load	SMS		L5				10%		20211116
		23	Tu					[B62-67] Can't be sure, but after that deep discharge the batteries probably didn't reach 100% until 4-7 days (the trickle charger is very slow, see tests above)					11/17/21+			100%	20211123

## B63
Batteries: B63	A					20201215_2/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					B62-67	L5 TA2	On Order					20201211
		15	Tu					BFMS		Subaru					20201215
		17	Th					B62-67; [B63] OCV 12.56	TA2	Prep.	L0			12/17/20	85%		20201217
				~	09:05	~	15:20	B62-67				S2				99%	20201217
		19	Sa	~	03:20				TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45			Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50		S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30		L5				1/6/21				20210105
		8	Fr	~	07:50				L5			-	1/8/21				20210108
				~	08:20	~	08:35		L5 S15-S16					20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				L5 A31					99%		20210108
				~	14:28				IMG			A31	1/9/21			100%	20210108
		11	Mo					L5			A31 S15-16			99%		20210111
				A31	1/12/21			100%	20210111
		12	Tu					IMG					20210112
		15	Fr					L5 A31					99%		20210115
		16	Sa					L5 A31		L		1/16/21			100%	20210116
				A30-31			99%	100%	20210116
				L5 A31 A30 IMG					60%		20210116
		18	Mo					L5					100%	20210118
				~	14:30	~	16:10		L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15		L5 S15-S16 IMG					20210207
		24	We					L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00		A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15					20210225
2021	Jul	28	We	~	14:30	~	16:00		TA2		L5			7/28/21			20210728
	Nov	16	Tu					SMS		L5				10%		20211116
		23	Tu					11/17/21+			100%	20211123

## B64
Batteries: B64	A					20201215_3/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					B62-67	L5 TA2	On Order					20201211
		15	Tu					BFMS		Subaru					20201215
		17	Th					B62-67; [B64] OCV 12.63	TA2	Prep.	L0			12/17/20	91%		20201217
				~	15:20	~	18:35	B62-67				S2				99%	20201217
		19	Sa	~	03:20				TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45			Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50		S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30		L5				1/6/21				20210105
		8	Fr	~	07:50				L5			-	1/8/21				20210108
				~	08:20	~	08:35		L5 S15-S16					20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				L5 A31					99%		20210108
				~	14:28				IMG			A31	1/9/21			100%	20210108
		11	Mo					L5			A31 S15-16			99%		20210111
				A31	1/12/21			100%	20210111
		12	Tu					IMG					20210112
		15	Fr					L5 A31					99%		20210115
		16	Sa					L5 A31		L		1/16/21			100%	20210116
				A30-31			99%	100%	20210116
				L5 A31 A30 IMG					60%		20210116
		18	Mo					L5					100%	20210118
				~	14:30	~	16:10		L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15		L5 S15-S16 IMG					20210207
		24	We					L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00		A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15					20210225
2021	Jul	28	We	~	14:30	~	16:00		TA2		L5			7/28/21			20210728
	Nov	16	Tu					SMS		L5				10%		20211116
		23	Tu					11/17/21+			100%	20211123

## B65
Batteries: B65	A					20201215_4/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					B62-67	L5 TA2	On Order					20201211
		15	Tu					BFMS		Subaru					20201215
		17	Th					B62-67; [B65] OCV 12.60	TA2	Prep.	L0			12/17/20	88%		20201217
		18	Fr	~	08:18	~	14:20	B62-67				S2				99%	20201218
		19	Sa	~	03:20				TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45			Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50		S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30		L5				1/6/21				20210105
		8	Fr	~	07:50				L5			-	1/8/21				20210108
				~	08:20	~	08:35		L5 S15-S16					20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				L5 A31					99%		20210108
				~	14:28				IMG			A31	1/9/21			100%	20210108
		11	Mo					L5			A31 S15-16			99%		20210111
				A31	1/12/21			100%	20210111
		12	Tu					IMG					20210112
		15	Fr					L5 A31					99%		20210115
		16	Sa					L5 A31		L		1/16/21			100%	20210116
				A30-31			99%	100%	20210116
				L5 A31 A30 IMG					60%		20210116
		18	Mo					L5					100%	20210118
				~	14:30	~	16:10		L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15		L5 S15-S16 IMG					20210207
		24	We					L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00		A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15					20210225
2021	Jul	28	We	~	14:30	~	16:00		TA2		L5			7/28/21			20210728
	Nov	16	Tu					SMS		L5				10%		20211116
		23	Tu					11/17/21+			100%	20211123

## B66
Batteries: B66	A					20201215_5/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					B62-67	L5 TA2	On Order					20201211
		15	Tu					BFMS		Subaru					20201215
		17	Th					B62-67; [B66] OCV 12.59	TA2	Prep.	L0			12/17/20	88%		20201217
		18	Fr	~	14:20	~	19:30	B62-67				S2				99%	20201218
		19	Sa	~	03:20				TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45			Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50		S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30		L5				1/6/21				20210105
		8	Fr	~	07:50				L5			-	1/8/21				20210108
				~	08:20	~	08:35		L5 S15-S16					20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				L5 A31					99%		20210108
				~	14:28				IMG			A31	1/9/21			100%	20210108
		11	Mo					L5			A31 S15-16			99%		20210111
				A31	1/12/21			100%	20210111
		12	Tu					IMG					20210112
		15	Fr					L5 A31					99%		20210115
		16	Sa					L5 A31		L		1/16/21			100%	20210116
				A30-31			99%	100%	20210116
				L5 A31 A30 IMG					60%		20210116
		18	Mo					L5					100%	20210118
				~	14:30	~	16:10		L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15		L5 S15-S16 IMG					20210207
		24	We					L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00		A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15					20210225
2021	Jul	28	We	~	14:30	~	16:00		TA2		L5			7/28/21			20210728
	Nov	16	Tu					SMS		L5				10%		20211116
		23	Tu					11/17/21+			100%	20211123

## B67
Batteries: B67	A					20201215_6/6: Trojan 27TMX

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L5	A27	11/17/21+	7/28/21	10%	100%
2020	Dec	11					B62-67	L5 TA2	On Order					20201211
		15	Tu					BFMS		Subaru					20201215
		17	Th					B62-67; [B67] OCV 12.57	TA2	Prep.	L0			12/17/20	86%		20201217
		18	Fr					B62-67				S2				99%	20201218
		19	Sa	~	03:20				TA2 IMG					12/19/20			20201219
		20	Su	~	03:45	~	05:45			Testing			12/20/20			100%	20201220
2021	Jan	4	Mo	~	18:51	~	19:50		S13-S14 S2 S13			S2 S13					20210104
		5	Tu	~	04:00	~	05:30		L5				1/6/21				20210105
		8	Fr	~	07:50				L5			-	1/8/21				20210108
				~	08:20	~	08:35		L5 S15-S16					20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				L5 A31					99%		20210108
				~	14:28				IMG			A31	1/9/21			100%	20210108
		11	Mo					L5			A31 S15-16			99%		20210111
				A31	1/12/21			100%	20210111
		12	Tu					IMG					20210112
		15	Fr					L5 A31					99%		20210115
		16	Sa					L5 A31		L		1/16/21			100%	20210116
				A30-31			99%	100%	20210116
				L5 A31 A30 IMG					60%		20210116
		18	Mo					L5					100%	20210118
				~	14:30	~	16:10		L5 A30 SSC TA2 IMG WS			A31			57%		20210118
		21	Th					L5				1/22/21 +			100%	20210121
2021	Feb	7	Su	~	14:15	~	17:15		L5 S15-S16 IMG					20210207
		24	We					L5 A31	Delivery	Subaru			2/24/21			20210224
				~	12:15	~	17:00		A26 IMG TA2	Sold	L5	A27					20210224
		25	Th	~	04:30	~	07:15					20210225
2021	Jul	28	We	~	14:30	~	16:00		TA2		L5			7/28/21			20210728
	Nov	16	Tu					SMS		L5				10%		20211116
		23	Tu					11/17/21+			100%	20211123

## B68
Batteries: B68	A					20211001_1/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L14	BC6	11/24/21 +	2/21/22	20%	100%
2021	Sep	28	Tu					[B68-71] Ordered from Electrolife Battery Co, Lawrence KS, Ronny	T48P	On Order					20210928
2021	Oct	1	Fr					[B68-71] Received in parking lot of Stanion Electric, Liberty	EBC T48P	Prep.	Subaru					20211001
		13	We					[B68-71] Moved from Subaru to garage floor			Garage					20211013
		21	Th					[B68-71] Moved from garage floor to Rubbermaid cart; Cleaned: Stickers applied; [B68] Electrolyte levels checked (nominal factory meniscus); OCV 6.295v			L0				88%		20211021
				~	08:50	~	14:55	Individual initial charge: 7.41v BK Bulk and Absorption down to 2.9a BK (6.1 hrs); 6.75v BK Float down to ~0.35a (5.6 hr); Electrolyte generous fill (meniscus top 1/2 way up the slot); Equalization 8.10v BK 20:30-21:00 (0.5 hr, highest voltage reached 7.93v BK); Brief Float; Removed from charge				S2		10/21/21		100%	20211021
				[B68-69] Not being charged, will be used for Schauer 2512 and Traco DC-DC testing (MikroTik project)		Sold		-					20211021
		24	Su					[B68-69] On the bench for testing Schauer JAC2512 (SBC_1)	A32			BC6					20211024
				[B68-71] Video sent to Pavel via Viber	IMG					20211024
		25	Mo	~	13:15			[B68-69] OCV 12.78v F (100% SoC is 12.74v); First power up of Schauer, 2-10s Bulk ~21a; 20m Absorption ending @ 14.81v (Trip Point 2.95a); Float 13.48v ...	T48P SSC			BC6					20211025
		26	Tu	~	04:30	~	04:43	[B68-69] Float 13.50v-13.51v F (13.489v WL), 0.118a WL, ~1.5w SSC ...; Short power "failures" (no load, no BTS), <=1s OFF no effect (lights don't dim), 2-3s OFF front panel lights dim, then Float, 5s OFF short 5w pulse in Float, 10s OFF Absorption stage ~2 mins SSC	SSC					20211026
				~	05:12	~	06:15	[B68-69] Short Absorption cycles while setting up APC load of ~120w (Schauer ON, tripped to Absorption)					20211026
				~	06:15	~	06:45	[B68-69] 120w load for 5m (Schauer OFF); Bulk ~1m (I briefly saw 25.0a charge); Absorption ~2.5m; Bulk+Absorption ~3.5m	SSC					100%	100%	20211026
				~	06:45	~	11:15	[B68-69] 120w load for 1h (Schauer OFF, Variacs 40/78); Bulk ~8m (26.3a max Extech); Absorption ~33m; Bulk+Absorption ~40m ...: 2.5w in Float before moving on	SSC LIB T48P					96%		20211026
				~	11:15			[B68-69] Discharged at highest wattage possible for APC/switch/Wattmon (~15a, ~184w, Variacs 46/75) / Shooting for deepest discharge possible to test Schauer recovery ...	T48P					20211026
		29	Fr		11:00			[B68-69] Started recovery from 0.10% WSoC (OCV SoC value may be slightly higher but didn't wait to see, which would have been another 24 hours) ...					0%		20211029
		30	Sa	~	00:29	~	04:10	[B68-69] Absorption-Float transition (Abs 5.4h); Bulk+Absorption 13.5h ...; Float at less than 4w	SSC LIB T48P					100%	20211030
				~	09:27	~	11:18	[B68-69] Schauer BTS test 25⁰C (batteries on bench, Wattmon Log values): Discharged 225->213.75 AH; Absorption 14.830v 3.057a ...; Float 13.520v 0.486a	T48P					95%		20211030
				~	23:30	~	01:07	[B68-69] Schauer BTS test 20⁰C (batteries on bench, Wattmon Log values): Discharged 225->213.75 AH; Absorption 14.919v 3.057a ...; Float 13.598v 0.631a					95%		20211030
		31	Su	~	02:59	~	05:41	[B68-69] Schauer BTS test 10⁰C (batteries on bench, Wattmon Log values): Discharged 225->213.75 AH; Absorption 15.119v 2.959a ...; Float 13.770v 0.291a					95%		20211031
2021	Nov	2	Tu	~	06:05			[B68-69] Schauer charger disconnected (to open, mark pots and shorten cable)	T48P IMG			-	11/1-2/21				20211102
				~	11:52	~	13:15	[B68-69] Schauer ON, Bulk+Absorption ~4 mins ...; Float adjusted down a very small amount and then returned to near factory setting (13.53-13.54vF)	T48P			BC6	-				20211102
				~	13:40	~	16:21	[B68-69] Discharged to various levels for testing Schauer; Lowest discharge to 217.2/255 AH ...; Float <0.3a <4w					85%	100%	20211102
		3	We	~	07:15			[B68-69] Batteries disconnected from test setup (to test Schauer with BK "jump start")				-					20211103
		5	Fr	~	16:20	~	17:25	[B68-69] OCV 12.855 (6.43v, 100% SoC is 6.37v); Reconnected battery and Schauer ON; Absorption 6m (2.92aW Trip Point) ...; Float <0.4a	T48P SSC			BC6			100%	100%	20211105
		6	Sa	~	08:29	~	12:00	[B68-69] Multiple short Absorptions during Schauer testing of VR5 Trip Point settings ... / Batteries in Float ~13.4vF with 108-109w continuous load at net charge of ~0.03aW					20211106
		7	Su	~	01:27	~	01:34	[B68-69] Another short Absorption during Schauer test of anomalies (fan speed and FP LED color)	T48P			BC6	11/6-10/21				20211107
				~	02:57	~	03:10	[B68-69] Another short Absorption while adjusting Schauer VR2 Float ... / Floating at ~13.57vF; Note that ending time of 03:10 is Wattmon time (which because of the DST change @ 02:00 was showing CDT not CST)				BC6					20211107
				~	03:07	~	03:50	[B68-69] Multiple short Absorptions while adjusting Schauer VR3 FLA Absorption	T48P SSC					20211107
		10	We	~	06:45	~	09:05	[B68-69] Schauer removed from test setup to modify for higher Trip Point, then reinstalled @ ~07:33; Multiple short Absorptions while testing VR5 Trip Point range				BC6					20211110
				~	10:06	~	10:28	[B68-69] Held in Absorption while adjusting Schauer VR3 FLA Absorption for 14.99v @ 11a	T48P					20211110
				~	10:32	~	11:40	[B68-69] Multiple short Absorptions (14.99v) while adjusting Schauer VR5 Trip Point for 11.0a					20211110
		12	Fr	~	04:04	~	04:17	[B68-69] Two short discharges with full recovery: Schauer OFF for 1s and 1m (~50w load); In the 1m discharge we dropped to 224.93 AH (99.97% Wattmon)	T48P SSC				11/11-12/21		100%	100%	20211112
				~	04:17	~	04:43	[B68-69] Short discharge with full recovery; Schauer OFF for 10m (~50w load); Low Point 224.34 AH (99.70% Wattmon)				BC6			100%		20211112
				~	05:25	~	07:23	[B68-69] Discharge and recovery; Schauer OFF for 41m while using APC load and ballast R for max discharge rate; Low Point 215.29 AH ...; Float at net charge 0.3a (4.1w)					96%		20211112
				~	08:26	~	20:32	[B68-69] Started deep discharge, hoping to reach 0% WSoC; APC and Ballast R, max rate 17.5aW (200wW); 18:23 Reduced to 11.6aW (120wW); 18:45 APC quit (9.99vWL) , continued with Ballast R, max rate 19.5aW; 20:32 Disconnected all loads to wait for OCV; 20:36 8.94vF (8.920vWL); 20:38 34.60 AH W, WL (15.4% SoC)	T48P			-					20211112
		13	Sa					[B68-69] Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup	IMG					20211113
				~	21:31			[B68-69] Deep discharge checked by OCV (has rested for >24 hrs): 34.85 AH W, 15.48% WL (it has drifted up 0.25 AH due to zero errors) / 11.755vF, %SoC by OCV as per Trojan 26%; This makes sense, as the C/∞ (infinity) chemical capacity is more than 225AH; There is no reason to believe the capacity of these T-105s has been significantly hurt by the previous 0% SoC Low Point on Tu10/26; To start recovery I'll try to do a "running start" with APC load 120w	T48P					20211113
				~	21:59	~	22:05	[B68-69] Deep discharge concluded; APC connected and load chased to 120w ... / Schauer ON, Low Point 33.98 AH WL (truncated), 15.10% WL (truncated, based on 225 AH C/20 Trojan specifications)				BC6			15%		20211113
		14	Su	~	00:13	~	00:22	[B68-69] Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)	IMG					20211114
				~	15:00	~	17:05	[B68-69] Fully recovered by test standard of 0.3a (4w) net charge (120w load, 13.415v Float); 15:25 APC load disconnected (->13.57vF Float) ... / Fully recovered (<0.3a 4w)	T48P SSC			BC6				100%	20211114
		16	Tu	~	10:13	~	11:34	[B68-69] Multiple short Absorptions while adjusting APC load for 155w, 150w and 145w					11/15-16/21				20211116
				12:01			[B68-69] Started deep discharge with 145w APC load ...	T48P			-					20211116
		17	We	~	02:06		09:30	[B68-69] APC quit @ 9.91vF, letting us rest; ~08:50 restarted APC load ~145w ...; 09:30 Discharge Total 180.4 AH to 19.8% WL (~29% SoC by OCV) / Library\Trojan\20211116^17 Discharge; Trojan T-105s, ~146w to 10v, ~23.5º; Wattmon Data & Graphs.ods; Schauer ON ...	T48P LIB			BC6			20%		20211117
		18	Th			~	10:00	[B68-69] Concluded recovery with ~145w APC load; APC disconnected; 13.56vF; Net charge 0.18a 2.5w / Full recovery as per test standards <0.3a / 4w when it tripped to Float at 03:50 because Float did not go above 0.23a / 3.08w after that	T48P			BC6				100%	20211118
		20	Sa	~	03:30			[B68-69] Schauer disconnected for mounting to backplate of Mier enclosure	TOI			-	11/19-20/21				20211120
		23	Tu	~	05:15			[B68-69] OCV 13.03vF (100% as per Trojan is 12.74v); Electrolyte level checked, B68 down ~1/16", B69 down ~1/8" (generous fill all to 1/2 way up the slot) / Installed in Mier for test fitting ...; Ready to go to ONWT	T48P TOI		L			11/23/21			20211123
				~	12:20	~	15:40	[B68-69] Onsite at ONWT with Mark, Keith, Dakota and ?; Installed Mier enclosure with Schauer, T-105s, Traco and Dinico fan control system / WP9 and B60 are still Active	TOI		L14	BC6	11/24/21 +				20211123
2022	Feb	19	Sa					[B68-69] Mimosas stopped working; Keith onsite / [Keith later reported that when he cycled power to the Schauer the fan only ran for <1m, so batteries must have been fully charged]	TM22 SMS		L14					20220219
		21	Mo	~	09:45	~	11:10	[B68-69] Onsite at ONWT with Keith and Dakota: Strange reports from Sa2/19 continue in careful questions/answers with Keith (battery was fully charged) / Float voltage high, something is wrong with observation, intrumentation, configuration of BC6 or BTS system	TM22		L14					20220221
				~	11:10	~	14:00	[B68-69] Onsite Alone (after Keith departed): Power Level Measurements and Estimates; Electrolyte filled to standard 'top of meniscus 1/2 way up the slot', B68 added ~1/16", B69 added ~1/8"; Tightened battery nuts and applied terminal spray; Many photos	TM22 IMG		L14			2/21/22			20220221
	Jun	3	Fr	~	11:27	~	12:01	[B68-69] 33m phone call to Keith: ONWT new system "has more on it"; More changes planned for next week	TM22		L14					20220603

## B69
Batteries: B69	A					20211001_2/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L14	BC6	11/24/21 +	2/21/22	20%	100%
2021	Sep	28	Tu					B68-71	T48P	On Order					20210928
2021	Oct	1	Fr					EBC T48P	Prep.	Subaru					20211001
		13	We					Garage					20211013
		21	Th					B68-71; [B69] Electrolyte levels checked (~+3/8" above plates, ~3/8" below factory meniscus); OCV 6.345v			L0				96%		20211021
				~	21:07	~	01:30	Individual initial charge: 7.41v BK Bulk and Absorption down to 2.9a BK (4.4 hrs); 6.75v BK Float down to ~0.25a (8.5 hrs); Electrolyte generous fill (meniscus top 1/2 way up the slot); Equalization 8.10v BK Fr10/22 10:00-10:30 (0.5 hr, highest voltage reached 8.05v BK); Brief Float; Removed from charge				S2		10/22/21		100%	20211021
				B68-69		Sold		-					20211021
		24	Su					A32			BC6					20211024
				B68-71	IMG					20211024
		25	Mo	~	13:15			B68-69	T48P SSC			BC6					20211025
		26	Tu	~	04:30	~	04:43		SSC					20211026
				~	05:12	~	06:15					20211026
				~	06:15	~	06:45		SSC					100%	100%	20211026
				~	06:45	~	11:15		SSC LIB T48P					96%		20211026
				~	11:15				T48P					20211026
		29	Fr		11:00					0%		20211029
		30	Sa	~	00:29	~	04:10		SSC LIB T48P					100%	20211030
				~	09:27	~	11:18		T48P					95%		20211030
				~	23:30	~	01:07					95%		20211030
		31	Su	~	02:59	~	05:41					95%		20211031
2021	Nov	2	Tu	~	06:05				T48P IMG			-	11/1-2/21				20211102
				~	11:52	~	13:15		T48P			BC6	-				20211102
				~	13:40	~	16:21					85%	100%	20211102
		3	We	~	07:15					-					20211103
		5	Fr	~	16:20	~	17:25		T48P SSC			BC6			100%	100%	20211105
		6	Sa	~	08:29	~	12:00					20211106
		7	Su	~	01:27	~	01:34		T48P				11/6-10/21				20211107
				~	02:57	~	03:10					BC6					20211107
				~	03:07	~	03:50		T48P SSC					20211107
		10	We	~	06:45	~	09:05					BC6					20211110
				~	10:06	~	10:28		T48P					20211110
				~	10:32	~	11:40					20211110
		12	Fr	~	04:04	~	04:17		T48P SSC				11/11-12/21		100%	100%	20211112
				~	04:17	~	04:43					BC6			100%		20211112
				~	05:25	~	07:23					96%		20211112
				~	08:26	~	20:32		T48P			-					20211112
		13	Sa					IMG					20211113
				~	21:31				T48P					20211113
				~	21:59	~	22:05					BC6			15%		20211113
		14	Su	~	00:13	~	00:22		IMG					20211114
				~	15:00	~	17:05		T48P SSC			BC6				100%	20211114
		16	Tu	~	10:13	~	11:34					11/15-16/21				20211116
				12:01				T48P			-					20211116
		17	We	~	02:06		09:30		T48P LIB			BC6			20%		20211117
		18	Th			~	10:00		T48P			BC6				100%	20211118
		20	Sa	~	03:30				TOI			-	11/19-20/21				20211120
		23	Tu	~	05:15				T48P TOI		L			11/23/21			20211123
				~	12:20	~	15:40		TOI		L14	BC6	11/24/21 +				20211123
2022	Feb	19	Sa					TM22 SMS		L14					20220219
		21	Mo	~	09:45	~	11:10		TM22		L14					20220221
				~	11:10	~	14:00		TM22 IMG		L14			2/21/22			20220221
	Jun	3	Fr	~	11:27	~	12:01		TM22		L14					20220603

## B70
Batteries: B70	A					20211001_3/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L18	WP12	12/29/22+	12/28/22	100%	100%
2021	Sep	28	Tu					B68-71	T48P	On Order					20210928
	Oct	1	Fr					EBC T48P	Prep.	Subaru					20211001
		13	We					Garage					20211013
		21	Th					B68-71; [B70] Electrolyte levels checked (~+3/8" above plates, ~3/8" below factory meniscus); OCV 6.36v			L0				98%		20211021
		22	Fr	~	10:40	~	14:55	Individual initial charge: 7.41v BK Bulk and Absorption down to 2.9a BK (4.3 hrs); 6.75v BK Float down to ~0.99a (0.3 hrs); Electrolyte generous fill (meniscus top 1/2 way up the slot); Equalization 8.10v BK 15:15-15:45 (0.5 hr, highest voltage reached 7.92v BK); Brief Float; Removed from charge				S2		10/22/21		100%	20211022
		23	Sa	~	07:50			[B70-71] Maintenance float on ENC under bench		Sold	L	BC3					20211023
		24	Su					B68-71	IMG				10/24/21-12/4/21				20211024
	Dec	3	Fr	~	03:30			[B70-71] Moved to bench, continued Float with ENC (brief Absorption); Will be used to setup W6 and etc. for ONWT, and for other testing this winter	DORM		L0					20211203
		4	Sa		16:30			[B70-71] Started discharge, C/20 capacity test to 10.0v with ITECH @ 11.25a CC ...	DRD Z17			-					20211204
		5	Su		09:09			[B70-71] Discharge ended, now resting; ITECH measured 16.7h, 187.3 AH; W10 measured 187.7 AH (+0.2%, very good agreement) / %SoC based on 225 AH capacity 16.6-16.7% (but battery did reach 10.0v); See FTR for Conclusions, I was testing @ ~22⁰C (and Trojan test spec is 27⁰C), adjustment of stated capacity for this difference results in a stated capacity of 213.8 AH, and this test result is ~88% of that (new battery, never heavily discharged before) / Library\Trojan\20211204^05 Discharge; Trojan T-105s, 11.25a to 10v, ~22⁰; Wattmon Data & Graphs.ods	DRD Z17 LIB					20211205
		6	Mo		09:30	~	21:55	[B70-71] OCV 11.821v ITECH (24h+ rest); Recovery started with ENC and BK_1 added to boost, 17.2aW ... / 12h25m later and batteries reached Absorption (14.800vI), on BK only (will bird dog 14.80-14.84vI) ...	DRD			BC3 S2			30%		20211206
		7	Tu	~	00:00	~	10:00	[B70-71] Terminated 2h5m Absorption (BK OFF); ENC Float (set 13.5v) ...; In the morning, Float 13.530vI, 0.19aW (~3w)				BC3	12/8-12/21			100%	20211207
		12	Su	~	07:50			[B70-71] Disconnected from ENC (to assemble Engel Battery Enclosure); Subsequently placed on shop floor in front of Ricoh box	DRD IMG Z0		L	-					20211212
2022	Feb	20	Su					[B70-71] OCV 12.652vI (92.5% SoC); Failed attempt at spare Schauer #2 preparation (BC7); Some discharge, Schauer won't start; No charge received since Su12/12/21	TM22 TM48S L14		L0					20220220
		21	Mo					[B70-71] Preparations to go onsite for ONWT Emergency; OCV 12.698vI (~97% SoC); Electrolyte above factory ~1/8", no water added (slightly low for usual goal "top of meniscus 1/2 way up slot"); Batteries loaded into Subaru; [Not needed/used at ONWT]	TM22 L14		Subaru			2/21/22			20220221
	May	11	We					[B70-71] Moved from Subaru to shop on Rubbermaid cart	TM22		L					20220511
		16	Mo			~	07:20	[B70-71] Moved to bench (slated to be used for Schauer set up); Cleaned; Interconnected; OCV 12.60vI; Charging with ENC, Extech to monitor			L0	BC3			88%		20220516
		17	Tu	~	16:35	~	16:36	[B70-71] Absorption maximum 14.530vWL ... / ENC transition to Float, which eventually settled at 13.530vWL; Wattmon Log values are in perfect agreeement with ITECH; Absorption was ~33 hours			L		5/18/22			100%	20220517
		24	Tu					[B70-71] (Schauer BC7 Preparation); Removed from ENC	T48S		L0	-					20220524
				[B70-71] Discharge ~7m @ 150w (average ~12.5v); Recovery Absorption ~15.0v	T48S PLN			BC7			99%		20220524
				[B70-71] Discharge ~22m @ 150w (average ~12.4v); Recovery Equalize ~16.2v ~35m					5/25/22		98%	100%	20220524
		26	Th					[B70-71] Instrumentation set up, T-105s in Engel with W10 current loops; 1m discharge @ 120w then Recovery, Live Energy SSC; Photos of test setup	T48S PLN SSC IMG			BC7	5/27/22		100%		20220526
		28	Sa					[B70-71] Engel is stable at 25.0⁰C; T Range BTS Tests started; Short discharges with long Absorptions to determine the Maximum Possible Continuous Wattage (MPCW) / Quick check of electrolyte levels, OK, slightly above factory; Started cooling batteries to new target of -10.0⁰C	T48S PLN SSC			BC7	5/29/22	5/28/22	100%		20220528
		31	Tu					[B70-71] Engel is stable at -10.0⁰C; Short discharges with long Absorptions to determine the MPCW; Started warming batteries to new target of 0.0⁰C	T48S PLN			BC7	6/1/22		100%		20220531
	Jun	2	Th					[B70-71] Engel is stable at 0.0⁰C; Short discharges with long Absorptions to determine the MPCW; Started warming batteries to new target of +10.0⁰C					6/3/22				20220602
		4	Sa					[B70-71] Engel is stable at +10.0⁰C; Short discharges with long Absorptions to determine the MPCW; Started warming batteries to new target of +20.0⁰C					6/5/22				20220604
		6	Mo					[B70-71] Engel is stable at +20.0⁰C; Short discharges with long Absorptions to determine the MPCW; Started warming batteries to new target of +30.0⁰C / Quick check of electrolyte levels, OK, slightly above factory					6/7/22	6/6/22			20220606
		9	Th					[B70-71] Engel is stable at +30.0⁰C; Short discharges with long Absorptions to determine the MPCW; Started warming batteries to new target of +40.0⁰C					6/10/22				20220609
		10	Fr					[B70-71] Discovered reversing T-comp problem with BC7: Unable to stabilize at +40⁰C; Started cooling batteries to shop ambient / Long time at too high a Float V near 40⁰C; Quick check of electrolyte levels, OK, at least factory					6/10/22			20220610
		11	Sa	~	09:28	~	09:35	[B70-71] BC7 BTS test setup broken down: Removed from Engel and placed on floor on ENC (T2 UPS)	T48S BC7		L	BC3					20220611
		16	Th					[B70-71] Proof of Principle tests of Traco and ~54v power supply on output: / Short discharges beyond ENC ability to supply but back to Float within minutes when load removed	T48-3 IMG L17					100%	100%	20220616
	Oct	12	We					[B70-71] Proposal/Estimate/Advance, W150s for CFS and Spare: B70/71 slated for CFS / Mark and Keith EML and SMS: 20221012 Proposal - CFS Installation.pdf (request for $1600 advance)	T48-4 EML SSC DBT SMS WP12					20221012
	Dec	28	We					[B70-71] Prep for installation at CFS: Removed from ENC; On bench; Cleaned / Electrolyte checked and filled: -1/16" to -1/8", B71 2/3 and 3/3 touching (partial meniscus); Filled to meniscus only (not overfilled) / Attempted fabrication of Foam Caps for terminals (abandoned); Loaded Subaru	T48-4 PLN L18 BC3		Subaru	-	-	12/28/22	100%		20221228
				12:00		14:00	[B70-71] Onsite at CFS: Keith had reserved only about 12" space at the bottom of the enclosure, but he angrily removed the bottom shelf to provide almost 24" / Installed W150_2, vertical on left side of enclosure (side panel is removeable) / T-105s installed in bottom front (with just enough space above to get your head above the cells); Photos / No loads could be attached, Keith plans to come back "maybe next week" to move all loads to the W150 (some now on AC, some now on WP1/B26) / He may leave the DC Netonix at CFS, and I told him to put it on the T-105s, not the W150; Did not measure power levels (Traco idle) / Did not check to be sure the W150 is charging (all I know is that Keith plugged it into the AC power strip at the back top of the enclosure)	T48-4 IMG		L18	WP12	12/29/22+			100%	20221228

## B71
Batteries: B71	A					20211001_4/4: Trojan T-105

Date/Time CST/CDT					Other Sources	Status	Location	Charger	Float Charged >24 hours	Electrolyte Level Checked	%SoC Low Point	%SoC High Point
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM	Description (All Voltages are Fluke 8000A or other calibrated reference except as noted)
				Sold	L18	WP12	12/29/22+	12/28/22	100%	100%
2021	Sep	28	Tu					B68-71	T48P	On Order					20210928
	Oct	1	Fr					EBC T48P	Prep.	Subaru					20211001
		13	We					Garage					20211013
		21	Th					B68-71; [B71] Electrolyte levels checked (~+3/8" above plates, ~3/8" below factory meniscus); OCV 6.36			L0				98%		20211021
		22	Fr	~	15:55	~	19:23	Individual initial charge: 7.41v BK Bulk and Absorption down to 2.9a BK (3.5 hrs); 6.75v BK Float down to ~1.25a (0.3 hrs); Electrolyte generous fill (meniscus top 1/2 way up the slot); Equalization 8.10v BK 19:38-20:08 (0.5 hr, highest voltage reached 7.91v BK); Brief Float; Removed from charge				S2		10/22/21		100%	20211022
		23	Sa	~	07:50			B70-71		Sold	L	BC3					20211023
		24	Su					B68-71	IMG				10/24/21-12/4/21				20211024
	Dec	3	Fr	~	03:30			B70-71	DORM		L0					20211203
		4	Sa		16:30				DRD Z17			-					20211204
		5	Su		09:09				DRD Z17 LIB					20211205
		6	Mo		09:30	~	21:55		DRD			BC3 S2			30%		20211206
		7	Tu	~	00:00	~	10:00					BC3	12/8-12/21			100%	20211207
		12	Su	~	07:50				DRD IMG Z0		L	-					20211212
2022	Feb	20	Su					TM22 TM48S L14		L0					20220220
		21	Mo					TM22 L14		Subaru			2/21/22			20220221
	May	11	We					TM22		L					20220511
		16	Mo			~	07:20				L0	BC3			88%		20220516
		17	Tu	~	16:35	~	16:36				L		5/18/22			100%	20220517
		24	Tu					T48S		L0	-					20220524
				T48S PLN			BC7			99%		20220524
				5/25/22		98%	100%	20220524
		26	Th					T48S PLN SSC IMG			BC7	5/27/22		100%		20220526
		28	Sa					T48S PLN SSC			BC7	5/29/22	5/28/22	100%		20220528
		31	Tu					T48S PLN			BC7	6/1/22		100%		20220531
	Jun	2	Th					6/3/22				20220602
		4	Sa					6/5/22				20220604
		6	Mo					6/7/22	6/6/22			20220606
		9	Th					6/10/22				20220609
		10	Fr					6/10/22			20220610
		11	Sa	~	09:28	~	09:35		T48S BC7		L	BC3					20220611
		16	Th					T48-3 IMG L17					100%	100%	20220616
	Oct	12	We					T48-4 EML SSC DBT SMS WP12					20221012
	Dec	28	We					T48-4 PLN L18 BC3		Subaru	-	-	12/28/22	100%		20221228
				12:00		14:00		T48-4 IMG		L18	WP12	12/29/22+			100%	20221228

## BC1
Chargers: BC1	A					TS_1: Trace Engineering TS812SB

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	MA2	B8/11
2001	May	3					Emails with ebay.com concerning search for "trace inverter" (I was looking, hoping)	EML				20010503
2002					The manufacturer label is punched for manufacture in the 2nd Quarter of 2002					20020503
2004 ?					Unknown date of purchase at bargain place in Richmond; I remember there were three of them for sale there (I should have bought them all); Purchased for about $78, a real deal considering how much this inverter/charger has been used; There is some felt tip marking on the top of the inverter that says "SSRW 9-11-06" but I think the date is when the accounting entry was made (to save on taxes)					2004 ?0503
	Nov	7					Photos of HAPS system in Honda Civic Wagon (file transfer dates 11/7/04 to 11/10/04); The Trace was used in the Honda Auxiliary Power System for many years after that (on the floor behind the driver's seat)	IMG	Applied	MA1	Deep Cycle	2004 ?1107
2008	Jun	22					Photos of Honda and HAPS: Estes Park, CO (1804 Ptarmigan, me, "Ready for church in Greeley"); In front of Grace Reformed Church, Greeley, CO / Trail Ridge Road, CO (interesting details of Honda interior showing full sized computer, LCD monitor, refrigerator and Trace on the right front floor)					20080622
2011	Dec	24					Photos of Honda and HAPS for CraigsList ad: The Honda had 278,000 miles on it, the head gasket leaked, and the Subaru was working fine (Trace removed, I did not include it in the sale of the Honda ~2/25/12)		Available	L		20111224
				[There are gaps in these history records concerning Batteries being charged, as this sheet was not created until 2018]					20111224
2015	Feb	21					Manual downloaded; Jumper settings checked and corrected; Tested	LIB	Applied			20150221
	Mar	30					Trace being used to charge Old_Honda under the bench	IMG			B0	20150330
	Apr	22	We					B1	20150422
	Jul	15	We					B2-3	20150715
		17					B1	20150717
	Aug	8	Sa					B4-5	20150808
		21	Fr					Looking for Battery Temperature Sensor for Trace (8/21/15 to 8/24/15); Shortcuts and downloads to Library	EML LIB				20150821
		24					Download "20150824 Old Listing Trace Inverters…"	LIB				20150824
	Sep	10	Th					B4-7 ?	20150910
		15					Duplex outlet replaced with GFCI; Sticker "Nuetral Bonded to GND" applied (done in preparation for SAPS)	MA2				20150915
	Dec	17	Th					B4-5	20151217
	Nov	30	Mo					B2-3	20151130
	Dec	27	Su					20151227
2016	Feb	19	Fr					B6-7	20160219
	Apr	21					Trace under bench charging Trojan batteries	IMG			B1,B6-7	20160421
		22	Fr					B4-5	20160422
		29	Fr					B6-7	20160429
	May	6	Fr					B4-5	20160506
		10	Tu		06:10					B8-11	20160510
		13	Fr					B6-7	20160513
		23	Mo					B4-5	20160523
		24	Tu					B4-5,B8-11	20160524
	Jun	1	We					B6-7	20160601
		13	Mo		14:05		14:33					B4-5	20160613
				16:25					B4-7	20160613
				B4-11	20160613
		16	Th				15:22					B1	20160616
	Nov	3	Fr					B8-11	20161103
		28	Mo			~	10:30					B4-7	20161128
		30					Jumpers checked (set for flooded)					20161130
	Dec	16	Fr			~	15:00					B8-11	20161216
2017	Jan	3	Tu				12:55					B4-7	20170103
		20	Fr	~	06:40					B8-11	20170120
	Mar	29	We			~	09:35					B4-7	20170329
	May	6	Sa					Loaned to Travis and Jen (with 27TMX)			Jen	B1	20170506
		7	Su	~	13:00	~	16:20	Returned to shop, 27TMX dead, charging …; Mostly charged, returned to Travis and Jen					20170507
		9	Tu	~	09:30	~	14:00	Returned to shop, 27TMX ~12.6 OC, charging …; Float			L		20170509
	Jun	27					CraigsList ad photos: Horizon Exercycle, Trace shown under bench	IMG				20170627
	Nov	28	Tu					B4-7	20171128
	Dec	22	Fr					B8-11	20171222
		29	Fr					B4-7	20171229
2018	Jan	15	Mo					B8-11	20180115
	Feb	24	Sa					B4-7	20180224
	Mar	13					W100 Testing (Trace used as CW load, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK); Jumper set for DEEP discharge	WRD IMG		L0	B1	20180313
		15					W100 Testing (Trace used as CW load, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)					20180315
		20					W100 Testing, calibration of C252 (WP2, Delta 200W, Genasun mounted under fan, BK, Trace being used as CW load)					20180320
	Apr	2		~	15:15			Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	WRD IMG EML			B8-11	20180402
	May	12					Shown in miscellaneous photos (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC)	IMG				20180512
	Jun	11					Installed in Mini SAPS: Will be used as inverter and to charge (2) T-105s in Right Rear foot well			MA2	B8,B11	20180611
		22					Photos; Inventory Sticker applied	IMG				20180622
		23					Rewired with ~51" of #4 AWG Stinger wire (Red and Dark Brown); Cleaned					20180623
	Aug	9	Th					Brought back from the garage and put on the bench as a CW load for testing W100_2 (it was never used to charge the T-105s in the Subaru, B8 & B11)	WRD		L0	B1	20180809
		12	Su					Removed from DR Test Setup		Available	L		20180812
		21	Tu			~	05:30	Charging set B4-7 (20150808_1/2, 2015080_2/2, 20150910_1/2, 20150910_2/2)		Applied		B4-7	20180821
	Nov	2		~	06:25			Trace removed from (4) T-105s and installed in Subaru/SAPS on (2) T-105s; Will usually be plugged in when Subaru is in the garage, but not always			MA2	B8,B11	20181102
2019	Mar	15	Fr	~	08:00			Trace inverter in use almost constantly during trip to Iowa (seek mode, Engel cooler, laptop and phone chargers)					20190315
		17	Su	~		~	22:30	Inverter in constant on mode during Sibley to Rayville run; Returned from Iowa					20190317
	Jun	22	Sa	~	05:00			Moved from Subaru to W100 test bench	WRD		L0	B54	20190622
		27	Th					Inverter integrated into W100 test setup with W100_3 and W100_4; Will be used to provide a Constant Wattage load					20190627
		28	Fr					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	WRD IMG				20190628
		29	Sa	~	08:10			Trace removed from W100 test setup; Not installed in Subaru yet (as I may need it for further W100 testing)	WRD	Available	L	-	20190629
	Aug	11	Su	~	02:45			Trace on UPS T1 charging T-105s from Subaru	WP5	Applied		B8,B11	20190811
	Sep	5	Th	~	12:15	~	12:30	Removed from T-105s	B8 B11	Available		-	20190905
2020	May	8	Fr		07:08	~	09:30	Initial charge new Trojan 27TMX	B56				20200508
		20	We	~	07:00			Topping charge, new Trojan 27TMX for LWT		Applied		B56	20200520
		22	Fr			~	04:25	Removed from 27TMX	B56	Available		-	20200522
		23	Sa	~	11:30			Reinstalled in Subaru	WP5	Applied	MA2	B8,B11	20200523
2021	Jul	16	Fr					Not charging; Stuck in bulk for days (medium flash 2-3/sec "Charger"); Slow flashing red "Status" (12.0-12.2v by manual); Set Trace on stool outside Subaru door and removed Engel; Now mysteriously charging / Monitered battery voltage with Micronta (corrected voltages down ~0.07v for Fluke equivalent) through Bulk (many hours), Absorption (14.8v) for an hour or so, then float 13.25v; While in Bulk removed cover, visual examination, stress tested with plastic rod; Unsure of diagnosis, as all I did was unplug the Engel and move the Trace and all appears to be OK; By all indications, battery was fairly severely discharged / Theories: (a) bad cap, (b) bad solder, (c) running compressor on inverter has damaged the relay (found GFCI tripped), (d) charger board logic/control goes inop, due to ground loop or noise; But I DON'T KNOW yet				B8,B11	20210716
		17	Sa					Reinstalled in Subaru; Further testing; Everything is working fine, running the compressor on the inverter is also OK; Somewhat mystified, as I don't know what happened or why					20210717
	Dec	25	Sa					Equalized with BK; Remained attached to batteries but unplugged and inverter off; Error (flashing red) due to high battery voltage cleared itself when BK output was turned off	S2			B8/11	20211225
2022	Apr	17	Su					Not charging again: Stuck for many hours with Slow Green Flash Status LED (12.3-12.4v by manual), this noticed yesterday / Battery is being drained -~0.4aE; 12.53vM (~12.4vF, complete agreement with Status LED, reading taken with push pins on the cables to the battery near the Trace); I cleared the wooden deck but didn’t remove it / I picked up the Trace and slammed it down on the wood deck (~15:00); Immediately Status Steady Green (>12.8v) CHARGING (the fault is probably a bad contact on a relay) / ~13.8vM climbing, ~16aE dropping Bulk (Charging Medium Flash 2-3/s) …; ~14.9vM Absorption (Charging Fast Flash) …; ~17:30 13.32-13.45vM Float (Charging Solid Green) with charge pulses >4aE					20220417

## BC2
Chargers: BC2	A					BTJ_1: DelTran 021-0123

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	Gravely
2015	May	24					Ordered from NewEgg.com ($24.99, free shipping)	EML	On Order			20150524
		29					Received: Probably placed in service within a few days, many different batteries		Applied	L	Many	20150529
				[Gap in these history records because I didn't create this sheet until 2018]					20150529
2017	Mar	19					Manual downloaded	LIB				20170319
				[Gap in these history records because I didn't create this sheet until 2018]					20170319
2018	May	12	Sa					Photos of front and rear (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC); Currently float charging old JC3#13 battery #20 (from TL6_5_B)	IMG	Applied		A21	20180512
		29	Tu	~	04:15					Subaru MAIN		20180529
	Jun	10					27TMX (and Old_Honda in parallel)				B1 & B0	20180610
		15	Fr	~	04:45			Charging 27TMX which is powering Wattmon_9 (DR Test Setup)	W9		L0	B1	20180615
		20					Inventory Sticker applied					20180620
	Aug	9	Th		04:05			Removed from charging and powering 27TMX and Wattmon_9		Available	L	-	20180809
		12	Su	~	06:55			Charging old battery (#20 from TL6_5_B) and powering Wattmon_9 (DR Test Setup, Lab Temp)	W9 WRD	Applied		A21 #20	20180812
	Nov	2	Fr	~	07:10			Removed from charging and powering Wattmon_9 …; Installed on Gravely starting battery				Gravely	20181102
2019	Apr	16	Tu	~	16:35			Removed from charging Gravely battery		Available		-	20190416
	May	18	Sa	~	04:50			Charging old Honda battery under bench		Applied		B0	20190518
				Reviewed this history sheet and entries are up to date					20190518
		19					Fluke, BK & UPS Battery Charging - shows Old_Honda and BTJ_1 underneath the bench	IMG				20190519
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1 (under bench)					20190708
		14					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)					20190714
2020	Jan	23	Th	~	10:10			Charging Gravely battery				Gravely	20200123
	Jun	1	Mo	~	19:15			Charging Subaru MAIN				Subaru	20200601
		7	Su	~	07:00			Charging Gravely battery				Gravely	20200607

## BC3
Chargers: BC3	A					ENC: Mean Well ENC-180-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2017	Jul	6					Datasheets downloaded	LIB	Research			20170706
		13					Ordered from TRC Electronics	EML TW1 WP1	On Order			20170713
		14					TRC Electronics Invoice rec'd	EML				20170714
		20					Approximate rec'd date; Library User Manual; Photos, Mean Well Power Supply Connector Problem; Not very happy with unit, but it can't be returned	LIB IMG EML	Available	L0		20170720
		21					20170721 ENC-180 Series Desktop Battery Charger.pdf, 20170721 Notes.txt; Abandoned use of ENC-180-12 (BC3) for WISPer (it will hang in Absorption with >10% load)	LIB		L		20170721
2018	Mar	17	Sa					Charging (4) T-105s on floor under bench		Applied		B4-7	20180317
		29	Th					Removed from (4) T-105s; Now charging 27TMX (and Old_Honda)			L	B1 & B0	20180329
	Apr	3	Tu					Removed from charging 27TMX (and Old_Honda); Applied to (4) T-105s				B8-11	20180403
	May	5					(2) T-105s (B9-10) removed from ENC for use in W100 testing (slated for WWT)	WRD			B8 & B11	20180505
		12	Sa					Photo of man'f label (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC)	IMG		L		20180512
	Jun	11		~	04:00			(2) T-105s removed (for Mini SAPS)	MA2	Available		-	20180611
	Nov	2	Fr			~	06:45	Charging (4) T-105s on floor under bench		Applied		B4-7	20181102
2019	Mar	29	Fr					Removed from charging (4) T-105s on floor under bench		Available		-	20190329
	May	19	Su					Reviewed this history sheet and entries are up to date					20190519
	Jun	8	Sa	~	09:30	~	17:30	Charging 27TMX (20190605/B54), flashing red, looking for 14.2v Absorption and 13.4v Float …; I noticed 14.22v, flashing orange (I don't know when the ENC switched to Absorption regulation)		Applied		B54	20190608
		9	Su	~	01:00			I noticed it is now 13.44v, flashing green (I don't know when the ENC switched to Float regulation)					20190609
		22	Sa	~	04:45			27TMX removed from ENC, moved to test bench and water levels checked	WRD	Available		-	20190622
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC (under bench, not applied), BTJ_1	IMG				20190708
2020	May	23	Sa	~	08:05			Float charging 27TMX		Applied		B57	20200523
	Jun	12	Fr	~	11:00			Removed from 27TMX	WP6-WP10	Available		-	20200612
2021	Jan	16	Sa					Seen in videos and photos of TurboNet/RHS bench testing	IMG				20210116
	Oct	24	Su					Video sent to Pavel via Viber					20211024
	Dec	6	Mo					DIP switch setting changed: DIP SW 1/2 OFF/ON->ON/ON; Was Bulk/Absorption 14.2v, Float 13.4v; Now Bulk/Absorption 14.5v, Float 13.5v (much better for Trojan FLAs); MikroTik Project	DRD	Applied		B70 & B71	20211206
				~	09:35	~	21:15	Observed 12.06aW in Bulk; This was at 12.26vWL (~148w); Note also that ENC was observed as holding >12a in bulk up to 14.5v (~175w) ...; Trip Point to Float observed as ~1.0a					20211206
		7	Tu	~	10:00			Float is 13.530vI (ITECH, 0.19aW, ~3w); This is perfect for Trojan FLAs at bench temperatures of ~22⁰C (my normal ambient HVAC result when thermostat at 73⁰F)					20211207
		12	Su	~	07:50			Batteries disconnected from ENC (to assemble Engel Battery Enclosure)	DRD IMG Z0	Available		-	20211212
2022	May	16	Mo	~	07:24	~	07:42	Observed 12.14aE in Bulk (14.22vI climbing, ~173w) ...; 9.15aE, 14.34vI (Absorption)	TM22 W10	Applied		B70/71	20220516
		17	Tu	~	16:35	~	16:36	"Trip Point" observed to be <=0.90aE; Absorption maximum 14.530vWL ...; ENC transition to Float, which eventually settled at 13.530vWL; Wattmon Log values are in perfect agreeement with ITECH / The (2) T-105s were in Absorption for ~33 hrs (ENC is not very suitable for use on 225AH, it takes a long time to transition to Float)	TM22				20220517
		24	Tu					Removed from (2) T-105s	T48S	Available		-	20220524
	Jun	11	Sa	~	09:28	~	09:35	BC7 BTS test setup broken down: B70/71 removed from Engel and placed on floor on ENC (T2 UPS)	T48S BC7	Applied		B70/71	20220611
		16	Th					Proof of Principle tests of Traco and ~54v power supply on output: Short discharges beyond ENC ability to supply but back to Float within minutes when load removed	T48-3 IMG L17				20220616
	Dec	28	We					Prep for installation at CFS: T-105s removed from ENC	T48-4 B70-71	Available		-	20221228

## BC4
Chargers: BC4	A					SCP_PS1: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	B26	WP1
2017	Mar	16					[BC4-5] Mean Well SCP-50 is the best T compensated power supply I've found in it's class/price range; Tprobe must be made from parts	WRD	Research			WP1	20170316
	Jul	28	Fr					[BC4-5] Ordered (2) Mean Well SCP-75-12 power supplies from Mouser	EML MOU	On Order			WP1	20170728
	Aug	1	Tu					[BC4-5] Received Mean Well power supplies (approximate date); Email to service@veteng.com "Temperature sensor for power supply"	MOU EML	Available	L0		WP1	20170801
		3					[BC4-5] WISPOWER #1 (WP1) Testing	IMG	Applied			WP1	20170803
		7					B26	WP1	20170807
	Sep	5					[BC4-5] WISPer #1 (WP1) Ready to Install at RCWT					WP1	20170905
		6					[BC4-5] Onsite at RCWT: Installed WISPer #1 (WP1) and battery		Sold	L3			20170906
2019	May	19					[BC4-5] Reviewed history sheet and entries are up to date					20190519
2021	Dec	16	Th	~	17:20	~	19:15	[BC4-5] Onsite at RCWT: AC power is ON; SLA 12.71vM not charging (due to blown PS1 fuse, but I thought it was "shot"); Removed SLA and W50 to take to shop	TM21F		Subaru	-	WP1	20211216
				[BC4-5] Unloaded Subaru			L0			20211216
		17	Fr	~	01:25	~	02:35	[BC4-5] Discovered and replaced W50 PS1 blown fuse; Charging; CONCLUSIONS Fuse was blown by load short on 8/4/21, battery has been resting and there has been no backup for 4.4 months				B26		20211217
		19	Su					[BC4-5] Engel W50 PS1 BTS Tests Concluded	TM21F LIB				WP1	20211219
		21	Tu					[BC4-5] Recovery against drained battery, PS1, 7.4aE MAX, no hiccups, charging at ~94wW and ~13vW; W50 temperatures measured during recovery (if both supplies are producing 95w the W50 case is too hot to touch for more than 1-2s); CONCLUSIONS; PS1 fuse did not blow because of initial charging into a drained battery; These power supplies are capable of providing ~95w, as hiccup does not start until load current rises above ~8.7a (as per datasheet); W50 may be useable at 95w continuous load, but it runs very, very hot (and in a warm ambient it could bake itself to death)	TM21F				WP1	20211221
		22	We					[BC4-5] Recovery Analysis	TM21F LIB					20211222
				~	08:04	~	11:58	[BC4-5] ITECH: Adjusted PS2 output down slightly 15.132v -> 15.01v (no load, shop ambient); Chart of PS2 Load Output Voltage vs. Load Wattage, 0 to 100w / See WP1 for further high power limit testing (PS1 fuse blown)	TM21F SSC IMG					20211222
		23	Th					[BC4-5] Removed PS1 FS2 fuse & melted fuse metal carefully (none inside power supply!); Replaced with another 10A/250V 5x20mm (last of the old stock Aug 2005, but there's still a spare taped to the W50) Attempted to remove the melted fuse metal on PS1 LF100, but it won't come off easily (not considered a threat, it's on coated magnet wire and the coating probably didn't melt through)					20211223
		27	Mo					[BC4-5] Recovery after 54 AH Discharge (low temperature), Analysis	TM21F LIB				WP1	20211227
2022	Jan	28	Fr					[BC4-5] Calc analysis of W50 BTS tests (data from 12/18-19/21) Conclusions (PS1 compensation average, wrong float voltage)	TM21F LIB SSC				WP1	20220128
		30	Su					[BC4-5] Calc analysis of W50/SLA Recovery (data from 12/21-22/21) Conclusions	TM21F LIB					20220130
	Feb	17	Th	~	11:30			[BC4-5] WP1 removed from bench, B26 removed from Engel (placed under bench on maintenance charge)	DRD		L		WP1	20220217
	Jun	28	Tu					[BC4-5] Prepared W50/B26 for installation at WWT: W50 cleaned (compressor) / [BC4] Set PS1 to Target 13.50v Float at BTS 25.0⁰C and load 100mA, without battery, 13.507vI	TM22		L0			20220628
				~	15:15	~	16:30	[BC4-5] Onsite at WWT: WP1 (W50) installed to replace WP2 (W100_1)			L6		WP1	20220628
	Jul	19	Tu					[BC4-5] Call from Keith: Ordered new site CFS; He removed the W50/SLA from WWT to take to CFS (sometime while I was in CO in the past two weeks); Partially and temporarily installed at CFS	T48-4		L18			20220719

## BC5
Chargers: BC5	A					SCP_PS2: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	B26	WP1
2017	Mar	16					BC4-5	WRD	Research			WP1	20170316
	Jul	28	Fr					EML MOU	On Order			WP1	20170728
	Aug	1	Tu					MOU EML	Available	L0		WP1	20170801
		3					IMG	Applied			WP1	20170803
		7					B26	WP1	20170807
	Sep	5					WP1	20170905
		6					Sold	L3			20170906
2019	May	19					20190519
2021	Dec	16	Th	~	17:20	~	19:15		TM21F		Subaru	-	WP1	20211216
				L0			20211216
		17	Fr	~	01:25	~	02:35					B26		20211217
		19	Su					TM21F LIB				WP1	20211219
		21	Tu					TM21F				WP1	20211221
		22	We					TM21F LIB					20211222
				~	08:04	~	11:58		TM21F SSC IMG					20211222
		23	Th					20211223
		27	Mo					TM21F LIB				WP1	20211227
2022	Jan	28	Fr					TM21F LIB SSC				WP1	20220128
		30	Su					TM21F LIB					20220130
	Feb	17	Th	~	11:30				DRD		L		WP1	20220217
	Jun	28	Tu					BC4-5; Checked PS2 Load Output at shop ambient ~23⁰C, 15.00v (14.995vI; 0.100aIS)	TM22		L0			20220628
				~	15:15	~	16:30	BC4-5			L6		WP1	20220628
	Jul	19	Tu					T48-4		L18			20220719

## BC6
Chargers: BC6	A					SBC_1: Schauer JAC2512B

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L14	B68/69
2021	Aug	11					I discovered these chargers by internet research; I was looking for a replacement for the W100 (which I won't make again); TurboNet had been mentioning the need for 48v systems (6/16/20 and 12/3/20 meetings) / Ordering and bench testing one of these became part of the MikroTik 48v systems research project; I called Scott Rammacher @ Schauer and asked questions	T48P LIB	Research			20210811
		12					20210812 Email 'Schauer Battery Chargers' from Scott Rammacher.pdf	LIB EML				20210812
		13					Lexington office discussion with Keith: They want a quote on a test system	T48P				20210813
		17					Emails from/to Scott Rammacher; Attachments include dimensional drawings, photos, catalog pages and adjustment explanations for internal pots	LIB EML				20210817
		23					Another general web search for battery chargers (I'm not completely satisifed with Schauer) ... but I convinced myself that the Schauer was the best bet for TurboNet's application	T48P				20210823
		25					Another phone discussion with Scott Rammacher @ Schauer; Questions answered about battery cable, Absorption timeout, new designs that may never come out					20210825
		27					Began drawing specifications together for the JAC2512, JAC2024H and JAC3024 chargers: 20210827 Schauer Charger Specifications, compiled @ DVS.doc	LIB				20210827
		28					Reevaluated Maximum Current Settings & Maximum Load Ratings for the Schauer Chargers; The Schauers will need to be adjusted from 25A to 15A for 27TMX use	T48P				20210828
		30					20210830 Email 'RE Schauer Battery Chargers' from Scott Rammacher, answers from factory.pdf	LIB EML				20210830
		31					20210831 Email 'Schauer Chargers settings update' from Scott Rammacher, correction.pdf					20210831
2021	Sep	2					20210902.1 Email 'RE Schauer Battery Chargers' to Scott Rammacher, 7 questions.pdf; Attached draft of specifications .doc					20210902
		3					20210903 Email 'RE Schauer Battery Chargers' from Scott Rammacher, 7 questions answered.pdf					20210903
		4					Sent Scott Rammacher the "finalized" specifications, with thanks; 20210904.0 Schauer Charger Specifications, compiled @ DVS.pdf					20210904
		22					Lexington Meeting with Keith and Mark (rec'd $2600 to begin orders for MikroTik 48v systems project)	T48P TPC1 TEDS TOI				20210922
		27					Ordered by phone call to Scott Rammacher @ Schauer: Install BTS (front panel hole cutout and jack); Factory settings (do not adjust)	T48P SBC	On Order			20210927
2021	Oct	2					Received; Box damaged (photos); Unpacked and s/b OK; They removed the front panel switch for FLA/SLA and covered the legends for it with black tape (something I didn't ask him to do, but that's OK, I'll probably never use the charger for SLA batteries); 20211002 Instructions and Warranty Papers rec'd with JAC2512 Scan_4pages.pdf	IMG T48P SBC LIB	Available	L0		20211002
		5					Invoice rec'd by email; For some reason he didn't charge $20 for adding the BTS, but S&H was higher than expected; 20211005 Invoice $285.11 rec'd by email, with notes, Scan.jpg	T48P SBC LIB EML				20211005
		24	Su					On the bench for testing	A32 W10	Testing		B68/69	20211024
				Video sent to Pavel via Viber	IMG				20211024
		25	Mo	~	13:15	~	17:40	First power up, no BTS, no load; Fan on immediately; Equalizer LED yellow; Bulk very short, 2-10secs (battery was sitting for 4 days, but OCV indicated 100%SoC), 310w peak (~21 amps), SSC / Absorption 20 mins, 14.70 to start, 14.81v at end; Trip Point ~2.95 amps (Wattmon/Extech); Float 13.48v (no fan, Equalizer LED green) ...; Hours later Float 0.22a 3w SSC; All according to specifications	SSC T48P			B68/69	20211025
		26	Tu	~	04:30	~	04:43	Short power "failures" (no load, no BTS), <=1s OFF no effect (lights don't dim), 2-3s OFF front panel lights dim, then Float, 5s OFF short 5w pulse in Float, 10s OFF Absorption stage ~2 mins SSC; All as expected	SSC				20211026
				~	05:12	~	06:15	Set up ~120w load (24hr max, 2xT-105s); This cannot be done w/o Schauer trip to Absorption; The APC causes voltage drop spikes so that the charge cycle starts again, even if I sneak up on power slowly / And once in Absorption above the Trip Point (~2.9a) it will not go back to Float (locked in Absorption); While in Float I saw ~3.5 amps charge, therefore it isn't the Trip Point that is causing the Absorption cycle [see We11/3]; Set Variacs/bulbs for ~120w load at Absorption ~14.7v; For now I'll power the Schauer or the APC load, but not both at the same time					20211026
				~	06:15	~	06:45	120w load for 5m (Schauer OFF); Bulk ~1m (I briefly saw 25.0a charge); Absorption ~2.5m; Bulk+Absorption ~3.5m					20211026
				~	06:45	~	11:15	120w load for 1h (Schauer OFF); Bulk ~8m (26.3a max Extech); Absorption ~33m; Bulk+Absorption ~40m / 20211026 Recovery; Schauer 2512, 9.7 AH, No Load, ~23.5º (No BTS, T-105s @ Ambient); Wattmon Data & Graphs.ods; 20211026,30 062838 Schauer 2512 Charge Profile 4.3% Discharge SSC.jpg	SSC LIB T48P				20211026
				~	11:15			Started discharge at highest wattage possible for APC/switch/Wattmon (~15a, ~184w, Variacs 46/75); Shooting for deepest discharge possible to test Schauer recovery from a very long power failure ...	T48P				20211026
		29	Fr		11:00	~	19:06	Started recovery from 0.10% WSoC (OCV SoC value may be slightly higher but didn't wait to see, which would have been another 24 hours); 26.41a max Extech (first 5 seconds) ... / Bulk-Absorption transition (Bulk 8.1h), Schauer maintained ~23.5a in most of Bulk, 328w max near end; Schauer 40°C (104°F) maximum seen on top	SSC LIB T48P				20211029
		30	Sa	~	00:29	~	04:10	Absorption-Float transitiion (Abs 5.4h), 14.8v max at 3.0a Trip Point; Bulk+Absorption 13.5h ...; Float at less than 4w / 20211029^30 Recovery; Schauer 2512, 225 AH, 0w, ~23.5º (No BTS, T-105s @ Ambient); Wattmon Data & Graphs.ods; 20211029,30 063016 Schauer 2512 Charge Profile 99.9% Discharge SSC.jpg					20211030
				~	09:27			Started BTS D&R tests; See FTR and B68/69 for details ...	T48P				20211030
		31	Su			~	05:41	Finished BTS D&R tests at 25, 20 and 10⁰C; The method I used is troublesome as at colder temperatures the battery voltage rises heavily into the gassing range (the batteries need to be cooled as well as the sensor) / Float V is easy to obtain, but Absorption V takes a long time (pushing >15v); However, some initial results were obtained, see analysis in 20211030^31 BTS; Schauer 2512, 10^20^25⁰ Float-Absorption (T-105s @ Ambient).ods; The compensation is on the low side, Float -2.8 mV/cell/⁰C (15% below Schauer spec -3.3), Absorption -3.2 mV/cell/⁰C (36% below Schauer spec -5.0); Note that the Trojan spec is -5 and the Genasun spec is -4.7 mV/cell/⁰C (Schauer Float is only 56% of Trojan spec, Schauer Absorption 64% of Trojan spec); This BTS testing will be much easier with the IT electronic load, which is not estimated to ship until Mo11/8 / I will postpone further BTS testing until after it arrives and I understand how to use it / Estimate of Schauer cable resistance 0.02 ohms [Note added 11/6/21: when considering all of the attachment resistances, including to the PCB, the value is probably more like 0.04 to 0.05 ohms]	T48P LIB SSC				20211031
				Schauer "Trip Point" (Amps for Absorption to Float transition) is much closer to 3.0 amps then Schauer's stated 2.9 amps	T48P LIB				20211031
2021	Nov	1	Mo					Updated 20210827 Schauer Charger Specifications, compiled @ DVS.doc: Endnotes added for Max Current, Trip Point and BTS Compensation					20211101
				Bench testing TODO priorities changed as per Su10/31 FTR and white sheets: Testing will be much faster and easier with IT Load (ETA ~We11/10) / BTS testing can be done without battery using the APC load, but easier yet with IT Load; Schauer can be set up for ONWT w/o IT Load, and that should be the number one priority / Priority considerations also involve finishing the Traco test and prep, invoicing the MikroTik testing project, finishing the Enclosure specs project/invoice and getting started on preparing the enclosure for ONWT / Therefore we will do as little Schauer testing as possible now until after the IT Load arrives and the other projects are finished or caught up	T48P WS				20211101
		2	Tu					Bottom cover removed and IMG_2142 PSE.jpg shows pot positions from factory; Cable measured as ~7.5' + 4" inside case (~7.8' total); Cut cable to 30" from case, 12" of outer jacket removed (now the cable is 2.8', or about 30% the ohmage drop = 0.006 ohms) [Note added Sa11/6: this is a low estimate, it's closer to 0.017 ohms]; 5/16" ring connectors soldered and shrink wrapped	T48P IMG			B68/69	20211102
				~	11:52	~	13:15	Played with VR2 (Float): Adjusted down "a very small nudge" (CW is Float down); 13.535->13.49vF; Decided it was better where it was and adjusted it back (13.53-13.54vF) / This should result in 13.48vF @ 120w [Note added Sa11/6: this estimate based on a cable resistance of 0.006 is wrong, the cable resistance was found to be closer to 0.017 ohms, at 120w this results in ~13.38v] / Factory setting AOK for our application [Note added Sa11/6, we should reconsider this decision]	T48P				20211102
				~	13:40	~	16:21	Considered VR1 (Max Current): Discharged to ~85%SoC and observed charging with ~120w load; 27.1a Extech max, 25.7, 25.3 and 25.0a Wattmon log for 2nd-4th min (these values are ~0.1a lower than Extech) / Did not change the factory setting, as we see >25a for ~5m (I think the factory knows best)					20211102
		3	We	~	07:15	~	09:00	Testing without battery: BK "as battery", BK 15.00v 5.1a, Schauer turned ON, then BK can be turned off (Schauer in Float); When APC load is brought to the 3.0a Trip Point the Schauer oscillates between Float and Absorption voltages (this is because the APC is a constant wattage load, and when the Schauer outputs Absorption V the amperage drops, it trips back to Float and the amperage increases, etc.) / The Schauer can be operated without the APC load connected but Float voltage will oscillate (SSC); When the APC load is increased above 3.0a Trip Point it stabilizes in Absorption (SSC) / I made a note on Tu10/26 that I thought the Schauer would not switch from Float to Absorption if the load current rises above the Trip Point, but it isn't true	T48P SSC			-	20211103
				~	09:00	~	10:15	VR3 Absorption adjustment: No battery, APC as load, Schauer ON in Absorption (>3.0a); APC adjusted to ~11.1aW (good agreement w/Extech); 14.75vF (low) / VR3 adjusted CW for 14.825vF, 25.0⁰C, 11.13aW; This was only "a small nudge" from the factory setting	T48P				20211103
				~	10:15	~	13:45	VR5 Trip Point adjustment: No battery, APC as load, Schauer ON in Absorption (>3.0a); I could not raise the Trip Point higher than ~5.7a * (VR5 fully CCW, this would work for a 40w maximum continuous load) / Also note that the fan is off and the FP LED is green for "Float" when the Schauer is obviously in Absorption (VR5 setting affects the fan and FP LED, see FTR) / Called Scott Rammacher @ Schauer, "Sometimes 'the resistor' needs to be changed", he can have the design engineer take a look at a circuit change, I said I need to modify this supply and install it next week, they may be able to tell me which resistor(s) need changing to what values, asked for at least 11.1a for this unit, but ultimately desire Trip Point adjustability from 1-19a (I wished later I'd asked for 0-20a), he'll get back to me, probably tomorrow; Determined the factory range of VR5 Trip Point is from about 0 to 5.7a but it can't be set in any meaningful way below about 0.5a (very light load); [* value of 5.7a is misleading, see Sa11/6 testing with battery]					20211103
		5	Fr	~	16:20			Reconnected battery and Schauer ON; I intend to verify the testing w/o battery was not causing an erroneous measure of maximum Trip Point setting of VR5, or the fan and FP LED anomalies	T48P SSC			B68/69	20211105
		6	Sa	~	08:29	~	12:00	VR5 full CW Trip Point is >0.3a but <1.6a; VR5 2nd mark CW Trip Point is ~8.2a; VR5 full CCW Trip Point is ~8.2a (testing to set Trip Point w/o battery does not work, 5.7a We11/3 value is misleading) / This allows for a "safe" maximum continuous load of ~77w (with a 3.0a "base"); I proved that in bench conditions a load of 110wW will come out of Absorption but it oscillates Float-Absorption-Float (see SSCs, 5-7 min period) and whether or not this will work in field conditions (different temperatures, different age of battery, etc.) is questionable, so I would not choose to apply the Schauer (Trip Point circuit as provided from the factory) with anything above a ~95w continuous load; Theoretically the load wattage could be increased slightly by lowering the Absorption voltage to where there is much less gassing wattage and so Trip is easier to realize, but if we get that desperate we might as well just run the Schauer as a "Float charger" (Bulk to short lowered "Absorption" ~14.0v then Float to finish) / With VR5 full CCW the fan and FP LED anomalies were observed again (fan runs slowly in Absorption and FP LED stays green) / The Tu11/2 estimated cable resistance of 0.006 ohms was very low, today it was roughly measured as 0.017 ohms (evidently there's printed circuit board and other parasitic connection drops not accounted for)					20211106
				~	12:00	~	23:30	Observed Schauer case temperature for 108-109w load in Float (no fan); Maximum seen 41⁰C / 106⁰F (Fluke IRT MAX); No bad smells, and stable / Therefore at an ambient temperature of 23⁰C the Schauer can safely maintain a 109w load in Float without overheating to destruction	T48P				20211106
		7	Su	~	01:27	~	01:34	Varied APC load and observed the fan and FP LED (VR5 full CCW): The "anomalies" only appear in Absorption slightly above the Trip Point; As such they can be ignored				B68/69	20211107
				~	02:07	~	03:17	Readjusted VR2 Float slightly higher (was 13.535vF no load 25.0⁰C) (VR2 was adjusted before on Tu11/2); No load 13.57vF, 50w load 13.515vF, 110w load 13.44vF, 120w load estimate 13.43v / Note that ending time of 03:17 is Wattmon time (which because of the DST change @ 02:00 was showing CDT not CST)					20211107
				~	03:07	~	03:50	Readjusted VR3 FLA Absorption CCW slightly lower (was 14.875vF @ 11.12aW Charge) (VR3 was adjusted before on We11/3); 14.81vF 11.12aW; 14.86vF 8.35aW (just above where Trip Point is now) / "Really cool" SSC showing Schauer oscillation Absorption-Float (20211107 034817 Schauer 2512 Absorption-Float Oscillation at the Trip Point SSC.jpg) / VR3 appears to be almost exactly where it was from the factory (it HAS been adjusted up since then, see T48P for considerations and explanations)	T48P SSC LIB				20211107
				~	14:30			Email to Scott Rammacher @ Schauer Battery Chargers: 20211107 143052 Email to Scott Rammacher 'JAC2512 Maximum Trip Point (attachments fixed)'.pdf; I corrected my statement that max Trip Point was 5.7a (actually 8.2a), I reiterated that we need at least 11.1a for this job, and in the future up to 19.9a, asked for 1-20a range as ideal (load up to 250w), addressed the question about overheating in Float with high load wattages (not a problem or run fan all the time from 12vdc rail), mentioned that the fan and FP LED anomalies are not a problem as they only occur immediately above the Trip Point, mentioned I had cut the battery cable, and stressed again that I hope we can come up with a modification that will allow the higher wattage loads; SSC attachments 20211026,30 062838 Schauer 2512 Charge Profile 4.3% Discharge SSC.jpg, 20211029,30 063016 Schauer 2512 Charge Profile 99.9% Discharge SSC.jpg, 20211107 034817 Schauer 2512 Absorption-Float Oscillation at the Trip Point SSC.jpg	T48P LIB EML SSC				20211107
		9	Tu					Email from Scott Rammacher @ Schauer Battery Chargers: It looks like we can get a Trip Point range of 4~13a (R31 change); Fan can be enabled continuously while power on by adding a resistor (R64) / He also gave information on how to disable Bulk/Absorption stages completely (Q12)	T48P LIB EML IMG				20211109
		10	We	~	06:45	~	09:05	Schauer powered down and removed from test setup; Added 100 ohm 1/2 watt carbon film at empty position R64; R31 removed (47K) and r/w 10K 1/4 watt metal film; Schauer reinstalled in test setup / Fan runs on low in Float, and on high in Absorption; VR5 Trip Point range is 3.6~14.4a	T48P SSC			B68/69	20211110
				~	10:06	~	10:28	VR3 Absorption adjusted again, CW=UP (see We11/3 & Su11/7): Target 15.0v @ 11.0a; See FTR for why (5 good reasons), but the clincher is that the numbers are "nicer" / Observed that at 14.99vF and 11.0aW the discharge "headroom" for gassing is ~1.3a (very fully charged T-105s), so with the Trip Point target being 11.0a we can only go ~25w higher than 120w before it would lock in or oscillate at Absorption (lab conditions) (later when setting the Trip Point I saw oscillation at ~146wW load in Float); 11.00aW, 14.99vF, 25.0⁰C; VR3 is visibly just above where it was at the factory	T48P				20211110
				~	10:32	~	11:40	VR5 Trip Point adjusted for target of 11.0a (best choice for ONWT for 120w max load): 11.2aW is the closest I could come; VR5 is extremely touchy, and slightly high is better than slightly low / Due to the rubber band nature of the APC load the Schauer will oscillate between Float-Absorption if the load is very close to the Trip Point (~146w in Float with fully charged T-105s)					20211110
				Float setting reviews: APC load adjusted for discharges of 120w (13.43vF, 8.93aW), 50w (13.51vF, 3.67aW) and disconnected, no load (13.57vF); I'm very happy with this					20211110
				Short no load "power failures": 1-2s no effect; >=3s LEDs go out; 3s, 4s, 5s, 6s, 7s, 10s, 20s, 30s, 1m short charging pulses; 10m I saw the EQUALIZE light briefly and there was a short 135w pulse; Everything AOK					20211110
		12	Fr	~	04:04	~	04:43	Short 50w load "power failures": 1s, 1m and 10m; All as expected; The 10m discharge test recovered completely to 100% charge in 10-15m (net charge 0.31-0.13a, 4-1w)	T48P SSC			B68/69	20211112
				~	05:25	~	07:23	Recovery from 95.7% SoC (215.325 AH) with ~50w load: 06:06 Schauer ON; Bulk ~23m; Absorption ~5.5m; Bulk+Absorption ~28.5m (previous test w/no load Bulk+Absorption was 40m) / Float ~48.5m to net charge 0.30a (4.1w) at 07:23 (previous test w/no load Float was 26m); Recovery total 77m (previous test w/no load total recovery was 66m) / As predicted, shorter Absorption due to high Trip Point, and full recovery in float took longer; 20211112 Recovery; Schauer 2512, 9.7 AH, ~50w, 25º (BTS, T-105s @ Ambient); Wattmon Data & Graphs.ods	T48P SSC LIB				20211112
		13	Sa					Detail photos of pot settings and R31/R64 mods	IMG				20211113
				Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup					20211113
				22:05			Started recovery with 120w load from deep discharge...	T48P			B68/69	20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)	IMG				20211114
				~	15:00	Recovery with 120w load from deep discharge completed; Total recovery 16.9 hrs; 20211113^14 Recovery; Schauer 2512, 191 AH, ~120w, 25º (BTS, T-105s @ Ambient); Wattmon Data & Graphs.ods / In subsequent analysis I became confident that the Trip Point is actually ~11.5a (see We11/10 entry where I determined it to be 11.2aW)	T48P SSC LIB			B68/69	20211114
				Applied labels Schauer 2xT-105 Loads.lbx and Schauer 2xT-105 Adjustments.lbx [but when I woke up later I realized I would have to redo them due to the Trip Point being higher than originally thought]	IMG LBX				20211114
				~	23:00	~	00:00	"Explanation / Thoughts - Discrepencies between Trip Point as set with fully charged battery and APC load vs. not so fully charged battery and APC load" [updated and improved Mo11/15 ~03:10] / The differences I'm seeing have to do with the significant ripple in the DC output of the Schauer and interactions with the "load" AC impedences (no battery vs. battery fully charged vs. battery mostly charged) and the "soft" characteristics of the APC load setup; I will modify the labels	T48P				20211114
		15	Mo					Labels modified, reprinted and applied over yesterday's labels; I left the date as 11/10/21, but modified the ideal load range to 50-130w (not 120w), maximum load 155w (not 150w) and Trip Point "~11.5a" (not "11.3a") / Schauer 2xT-105 Loads.lbx; Schauer 2xT-105 Adjustments.lbx	IMG LBX	Sold			20211115
		16	Tu					Front panel labels improved; Schauer STAGE 0.35.lbx; Schauer Yellow Bulk Absorption Green Float 0.47.lbx; Schauer BTS 0.47.lbx					20211116
				20211116 Email to Scott Rammacher 'RE JAC2512 Maximum Trip Point'.pdf	EML LIB				20211116
		18	Th			~	10:00	Concluded Recovery for D&R test at ~145w APC load (started Discharge Tu11/16); I started this D&R test hoping to test at ~155w (the maximum load on the label) but it locked in Absorption at ~155w, and would have oscillated at ~150w; Therefore the label needs to be changed (50-120w ideal, 145w maximum); Bulk 13.3h, Absorption 5h, Float wasn't needed (all under 0.3a/4w standard), Total Recovery 18.3h / At the maximum power the Bulk/Absorption is so long that by the time it trips to Float the battery is 100% / 20211117^18 Recovery; Schauer 2512, 181 AH, Load ~145w, 25º (BTS, T-105s @ Ambient); Wattmon Data & Graphs.ods	T48P SSC LIB			B68/69	20211118
				Label reprinted: Max ~155w -> ~145w; Ideal 50~130w -> 50~120w; Schauer 2xT-105 Loads.lbx	IMG LBX				20211118
		20	Sa	~	03:30			Disconnected from test setup for mounting to backplate of Mier enclosure	TOI		L	-	20211120
		23	Tu	~	12:20	~	15:40	Onsite at ONWT with Mark, Keith, Dakota and ?; Installed Mier enclosure with Schauer, T-105s, Traco and Dinico fan control system			L14	B68/69	20211123
2022	Feb	19	Sa					Mimosas stopped working; Keith onsite; Strange reports from Keith that "power was off" and that he had to cycle the Schauer	TM22 SMS		L14		20220219
		21	Mo	~	09:45	~	11:10	Onsite at ONWT with Keith and Dakota: Strange reports from Sa2/19 continue in careful questions/answers with Keith ("no lights", cycled power, short absorption, battery fully charged) / Float voltage high, something is wrong with observation, intrumentation, configuration of BC6 or BTS system; Future plans, power levels may double	TM22		L14		20220221
				~	11:10	~	14:00	Onsite Alone (after Keith departed): Power Level Measurements and Estimates / Calculations on what would happen if Keith doubles the antenna load at the top of the tower: Total continuous load on battery would be ~136w (OK for now, <145w max for BC6 Schauer configuration) / It is likely Keith could eventually increase the load above 145w; Many photos	TM22 IMG		L14		20220221
		22	Tu	~	12:55	~	13:40	Call to Keith 45m, discussing his onsite visit Sa2/19: I believe that Keith's observation of the Schauer state was in error (low fan is hard to detect, indicator lights are not very bright)	TM22				20220222
				~	18:53	~	18:59	Mark called 6m: ONWT is down again					20220222
		23	We	~	09:37	~	09:41	Mark called 4m: Last night Mark was on onsite, the Schauer had red and green lights, cycling the Traco output power to the top of the tower did not bring up the Mimosas					20220223
				~	12:46	~	12:48	Angry call from Keith: "... Schauer is off, and I'm still seeing power to the PBPs"; I mentioned that the Schauer has nothing to do with it, on or off; ... he got angry, cussed at me and hung up			L14		20220223
	Jul	23	Fr					[BC6-8] What I'd Like To Do with the Schauers: ONWT BC6 s/b r/w 165w Dual Supply	T48S

## BC7
Chargers: BC7	A					SBC_2: Schauer JAC2512B

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Prep	L	-
2021	Nov	11	Th					[BC7-8] Keith was here to plan the ONWT Power Cable Assembly; During "show and tell" we discussed concerns that we have no emergency spares for the Schauer and Traco units being prepared for ONWT / Verbal order for (2) each Schauers and Tracos	T48S	Sales			20211111
		15	Mo					[BC7-8] 20211115 Quote - Spare Parts for ONWT and Future.pdf emailed to Mark, Keith and Brad; Quoted Schauers, Tracos, Dinicos and reversing relays (fan control system) / Mark promised $1720 check ASAP	T48S DBT EML SMS	Quoted			20211115
		16	Tu					[BC7-8] Received $1,720 Check	TM48S	Advanced			20211116
		17	We					[BC7-8] 20211117 Email to Scott Rammacher 'Purchase Order (2) JAC2512'.pdf / Scott called, this time he will charge the $20 for the BTS; He said they'll probably ship Mo11/22	TM48S LIB EML	On Order			20211117
	Dec	1	We					[BC7-8] Called Scott Rammacher @ Schauer to follow up on the order: I was told he'll probably ship tomorrow Th12/2	TM48S				20211201
		8	We					[BC7-8] Shipped; Schauer invoice date	EML	Shipped			20211208
		10	Fr					[BC7-8] Received; Schauer invoice received; All the spares have been received; TurboNet Invoice Date (although spares have not been prepared yet) / 20211210 Schauer Invoice BC7 BC8 (SBC_2 SBC_3) Scan.jpg	TM48S EML LIB SBC SSC	Prep	L		20211210
2022	Jan	2	Su					[BC7-8] 20211210 Invoice - Spare Parts for ONWT and Future.pdf; 20220102 Email to Mark, Keith & Brad 'Invoice - Spare Parts for ON & Future (MikroTik 48v Systems)'.pdf	TM48S DBT EML				20220102
2022	Feb	20	Su					Attempted Schauer Preparation for ONWT Emergency: Unpacked 1 of 2 chargers received Fr12/10/21; Used ITECH and BK to verify Float, FLA and Gel/AGM Trip Points (no BTS)	TM22 TM48S L14		L0		20220220
				BTS attached and in Engel/Dinico @ ~25⁰C; Verified again Float 13.45vI and FLA Trip Point ~2.9aI; VR5 full CCW Trip Point ~7.3a (~106w) / Modifications: Cut cable 30" from case, 12" outer jacket removed, ring connectors, shrink; R64 100ohms 1/2w carbon film; R31 10K 1/4w metal film / Adjustments (ITECH, BK, BTS in Engel @ 25.0⁰C): VR2 Float 13.45vI at 150wI (measurements recorded for 6, 100, 113, 150 and 175w); Attempted VR3 and VR4 adjustment but could not reach target of 16.2v for VR4 / Front panel switch logic flipped (FLA/SLA), VR5 range is limited to VR3 setting and the pot only reduces it / Adjusted VR3 and VR4 at 13.0aI: VR3 FLA "Equalize" 16.2vI; VR4 SLA "Flooded" 15.0vI / Adjusted VR5 Trip Point to 13.15aI (as close as possible to target of 13.0a, FP switch set SLA "Flooded"); Trip Point with FP switch set FLA "Equalize" also 13.15aI	TM48S				20220220
				Reality check FAILED (T-105s and ITECH Sense): 150wI, Schauer will not start; 0wI, Schauer will not start; 12.0aI, Schauer will not start (power LED is red, stage LED is OFF) / See FTR for CONCLUSIONs: Schauer tech in China warned us (11/9/21 email from Scott Rammacher) that this might happen if Trip Point is adjusted above 13a; But this is probably not what happened to BC6 at ONWT / [Resolved, see Tu5/24]				B70/71	20220220
		21	Mo					T-105s loaded into Subaru to take to ONWT (in case they are needed); SBC_2 remains on the bench (TODO Redo adjustments for Trip Point 12a and test again)	TM22			-	20220221
2022	Mar	5	Sa					[BC7-8] Inventory Sticker 0.47.lbx applied; Invoice fully notated 20211210 Schauer Invoice BC7 BC8 (SBC_2 SBC_3) Scan.jpg	T48S LBX LIB				20220305
2022	May	24	Tu					ITECH with Sense and SBC_2 attached to T-105s; BTS in Engel @ 25⁰C; Discovered disconnected negative battery cable connection inside the Schauer / SBC_3 unpacked and opened to verify which post should be used; Crimped female 1/4" spade connection slightly and reattached; Schauer powered up OK / W10 to log battery voltage, Extech on SBC_2 positive output; Verified VR2 Float setting as only slightly higher than targeted 13.471vI @ 150.00w / 7m discharge and Schauer powered up OK; Verified VR5 Trip Point <=13.4aE and VR4 SLA "Flooded" as ~15.0vI before trip to Float / 22m discharge, FP switch to FLA "Equalize" and Schauer powered up OK / Verified VR3 as OK (~16.17vI, 16.5aE), but this of course was not measured close to Trip Point as Equalize will probably never trip to Float (this mode will have to be manually timed and aborted) / FP switch to SLA "Flooded" position and immediate Float	T48S Z19 Z0 PLN BC8 W10 Z17			B70/71	20220524
		26	Th					Instrumentation set up, T-105s in Engel with W10 current loops; 1m discharge @ 120w then Recovery, Trip Point and VR4 SLA "Flooded" OK, SSC; Extech, W10 and ITECH Current Comparisons "OK"; ITECH and W10 Voltage Comparisons (very good agreement); Photos of test setup; Stabilizing Battery to 25.0⁰C ...	T48S PLN SSC IMG Z0 W10			B70/71	20220526
		27	Fr					Engel is stable at 25.0⁰C; Verified VR2 Float setting as 13.458vI, 150.00w + 147mA Float charge; This is very close to target and setting of 13.450v Su2/20/22 / "Ideal" load where Float is 13.50v measured as ~122w [But see Sa5/28 where it is determined more carefully to be 120w, which is also a much nicer figure for the label] / Measured effective cable resistance as 0.0179 ohms; This compares well with the Sa11/6/21 value of 0.017 ohms measured for BC6 / Verified VR5 Trip Point and VR4 SLA "Flooded" setting <13.40aE at >=15.004vI	T48S PLN				20220527
		28	Sa					Engel is stable at 25.0⁰C; T Range BTS Tests Started; Float as a function of Load Watts: 0w 13.651vI, 40w 13.608vI, 80w 13.558vI, 120w 13.501vI, 160w 13.441vI / Maximum Possible Continuous Wattage (MPCW) 174w (short discharges, long Absorptions); Trip Point <13.30aE and VR4 SLA "Flooded" setting is 15.014vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 1.73a / CONCLUSION: A battery is not needed to trim up a Schauer, as the VR2/3/4/5 values set Su2/20/22 all look good with T-105s; FTR list comparing adjustments without battery with results with battery	T48S PLN SSC Z0			B70/71	20220528
		29	Su					Initial estimate of BTS Compensation (not very accurate, while battery cooling down): +25.0 to -1.0⁰C ~17.6mV/⁰C (~2.9mV/cell/⁰C); Measured compensation for BC6 10/31/21 was 17.4mV/⁰C	T48S PLN				20220529
		31	Tu					Engel is stable at -10.0⁰C; Float as a function of Load Watts: 0w 14.246vI, 40w 14.202vI, 80w 14.155vI, 120w 14.099vI, 160w 14.044vI / Maximum Possible Continuous Wattage (MPCW) 202w (short discharges, long Absorptions); Trip Point 13.29aE and VR4 SLA "Flooded" setting is 15.670vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 0.36a / NOTES on running Absorption Tests: Circulating fans OFF then gap Engel lid; Start Absorption tests when T=Target-0.1; Immediate 0w to 120w switch of ITECH can cause immediate Absorption (high surge) / OTHER CONCLUSIONs: MPCW is function of T, higher max possible at lower Ts; Therefore need to run tests all the way to 50⁰C in order to determine the MCW; For label should state MPCW at -10/20/50 ⁰C	T48S PLN Z0			B70/71	20220531
2022	Jun	2	Th					Engel is stable at 0.0⁰C; Float as a function of Load Watts: 0w 14.088vI, 40w 14.047vI, 80w 13.997vI, 120w 13.944vI, 160w 13.885vI / Maximum Possible Continuous Wattage (MPCW) 198w (short discharges, long Absorptions); Trip Point 13.27aE and VR4 SLA "Flooded" setting is 15.496vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 0.50a / CONCLUSION: Change approach to determining MPCW; Chase the wattage during test; If it looks like a short Absorption <15m bump the wattage up; If it looks like a long Absorption >30m bump the wattage down / The Trip Point is fairly consistent and well known, so this approach may obtain the MPCW in one Absorption of ~30m; The most important requirement is to obtain the MPCW at T=Target (to the nearest Watt)					20220602
		4	Sa					Engel is stable at +10.0⁰C; Float as a function of Load Watts: 0w 13.9125vI, 40w 13.870vI, 80w 13.821vI, 120w 13.769vI, 160w 13.706vI / Maximum Possible Continuous Wattage (MPCW) 189w (short discharges, long Absorptions); Trip Point 13.31aE and VR4 SLA "Flooded" setting is 15.299vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 0.95a					20220604
		6	Mo					Engel is stable at +20.0⁰C; Float as a function of Load Watts: 0w 13.734vI, 40w 13.690vI, 80w 13.642vI, 120w 13.584vI, 160w 13.523vI / Maximum Possible Continuous Wattage (MPCW) 180w (short discharges, long Absorptions); Trip Point 13.30aE and VR4 SLA "Flooded" setting is 15.104vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 1.38a / TFTP: Absorption Charge Current (ACC) and why we should be setting up the Schauers with 14.8v Absorption (not 15.0v)					20220606
		9	Th					Engel is stable at +30.0⁰C; Float as a function of Load Watts: 0w 13.5775vI, 40w 13.534vI, 80w 13.483vI, 120w 13.424vI, 160w 13.364vI / Maximum Possible Continuous Wattage (MPCW) 165w (short discharges, long Absorptions); Trip Point <13.32aE and VR4 SLA "Flooded" setting is 14.930vI (corrected to 13.0a by cable ohms) / Absorption Charge Current (ACC) 2.26a					20220609
		10	Fr					During Engel Stabilization of battery to +40.0⁰C I noticed we had a serious problem: Float voltage and charge current high, battery warming up due to internal heat / After doing some instrumentation checks I came to the CONCLUSION: Schauer BTS compensation is not correct; T-comp reverses above ~35⁰C / Unable to stabilize at +40⁰C without serious birddogging (explosion hazard, Engel cover must be gapped); We do have some isolated points but not at stable T / CONCLUSION: BC7 Schauer BTS T-comp is no good above ~+35⁰C; Abandoned attempts to get good data at +40⁰C; T Range BTS Tests Abandoned/Concluded; Sa5/28 to Fr6/10 Procedure and Results in FTR / TODO ASAP: Change setup and test BC8 (SBC_3) without battery to determine if it exhibits the same problem, focusing on higher Ts first / Paradigm Shifts TFTP: Mark & Keith contacted me this day about the new exposed site LSWT (new FTR T48-3) which they want ASAP and I can't deploy a Schauer there with this problem / Therefore started working on developing new design with Float Only Battery Charger and Dual Supply with Traco isolation					20220610
		11	Sa					BC7 BTS test setup broken down: / SBC_2 OFF/disconnected, reassembled (115/230 switch and bottom cover) and placed in box on floor	T48S W10 Z0 B70/71 BC3 S2 B0 S1		L	-	20220611
		28	Tu					[BC7-8] Labeled BTSs (to avoid accidently swapping them); Wire Label 0.5 BTS.lbx	T48S LBX				20220628
2022	Jul	23	Fr					BC6-8; BC7 should be setup for a new indoor site where Ts do not go above 35degC and power levels are not expected to go above ~120w	T48S				20220723
2022	Oct	6	Th					W150_1 Bench Testing (~25⁰C): Schauer Equalize Test (B58 27TMX, W150 powering 180wI Traco load, Engel open, 1h); Procedure and performance notes; BC7 returned to box on the floor underneath E window	T48-3 PLN WP11				20221006

## BC8
Chargers: BC8	A					SBC_3: Schauer JAC2512B

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Prep	L
2021	Nov	11	Th					BC7-8	T48S	Sales			20211111
		15	Mo					T48S DBT EML SMS	Quoted			20211115
		16	Tu					TM48S	Advanced			20211116
		17	We					TM48S LIB EML	On Order			20211117
	Dec	1	We					TM48S				20211201
		8	We					EML	Shipped			20211208
		10	Fr					TM48S EML LIB SBC SSC	Prep	L		20211210
2022	Jan	2	Su					TM48S DBT EML				20220102
	Feb	21	Mo					Preparations to go onsite for ONWT Emergency; SBC_3 loaded into Subaru (unopened in box); [Not needed/used at ONWT]	TM22 L14				20220221
	Mar	5	Sa					BC7-8	T48S LBX LIB				20220305
	May	24	Tu					SBC_3 unpacked and opened to verify which post s/b used for negative battery cable connection; (Repacked)	T48S PLN BC7				20220524
	Jun	11	Sa					Assembled BC8 Schauer BTS test setup: BC8 unpacked and on the bench, totally factory (except for inventory label) / Bundled BTS and Dinico sensor T2 together in center of enclosure in 3/4" electrical conduit 7.5" long (zinc steel pipe); Factory cable and SB50 connector to ITECH input (Sense OFF); FB switch to FLA; BTS attached / Powered from T1 UPS; BK in parallel to ITECH input (Schauer output), set 12v/5.1a; 2wI, Schauer ON / Could not get Schauer to remain stable with only 2w load; Tried CC but no better; Starts reliably to stable voltage at 17.00wI (but can't get anywhere near 100-200mA Float charge range) / Added capacitance, (6) 47uF @ 35v (assembly that was used on APC load) / This is much better, 0.500aI is stable through startup (to 13.450vI, 6.69wI), close enough to minimum charge current when battery is fully charged that it won't matter for the purposes of this test, which is to determine BTS T-Comp at -15 to 50⁰C; Stabilizing BTS to +25.0⁰C ...	T48S PLN Z0 S2 Z17 IMG		L0		20220611
		12	Su					BC8 Schauer BTS Tests Started: Engel stable at +25.0⁰C; "As From Factory" Effective Cable Ohms (ECO) 0.037 ohms (measured at 0.500-1.500aIR) / For comparison: the BC7 ECO measured Fr5/27/22 was 0.0179 ohms (Factory ECO is 2.1x higher than modified BC7) / Float Vs will be measured at 1.00aI and ECO corrected to 100mA; Absorption Vs will be measured at 3.00aI (just above factory set Trip Point); Values here rounded to 2 decimal places (FTR has full resolution) / +25.0⁰C: Float 13.46v; Absorption 14.80v / +30.0⁰C: Float 13.38v; Absorption 14.72v / +35.0⁰C: Float 13.31v; Absorption 14.64v / +40.0⁰C: Float 13.41v; Absorption 14.97v; T-comp is reversed above ~+35⁰C as it was for BC7	T48S PLN Z0				20220612
		13	Mo					Stabilization at +45.0⁰C was interrupted/delayed by troubleshooting and replacement of bad reversing relay on Dinico T control (D2D_2)	T48S PLN Z0 Z19				20220613
		14	Tu					BC8 Schauer BTS Tests continued, see Su6/12 / +45.0⁰C: Float 13.94v; Absorption 15.46v; T-comp is reversed above ~+35⁰C as it was for BC7 / +50.0⁰C: Float 14.11v; Absorption 15.55v; T-comp is reversed above ~+35⁰C as it was for BC7 / -10.0⁰C: Float 14.03v; Absorption 15.44v / -5.0⁰C: Float 13.96v; Absorption 15.36v	T48S PLN Z0				20220614
		15	We					BC8 Schauer BTS Tests continued, see Su6/12 / 0.0⁰C: Float 13.88v; Absorption 15.27v / +5.0⁰C: Float 13.80v; Absorption 15.18v / +10.0⁰C: Float 13.71v; Absorption 15.08v / +15.0⁰C: Float 13.63v; Absorption 14.99v					20220615
		16	Th			~	15:55	BC8 Schauer BTS Tests continued, see Su6/12 / +20.0⁰C: Float 13.54v; Absorption 14.89v / +25.0⁰C: Float 13.46v; Absorption 14.80v; Rounded values are identical to start of run on Su6/12; BC8 Schauer BTS Tests Completed; BC8 OFF and disconnected from ITECH	T48S PLN Z0 Z19 IMG				20220616
		28	Tu					BC7-8; SBC_3 cleared from bench (boxed on floor)	T48S LBX		L		20220628
	Jul	23	Fr					BC6-8; BC8 should be setup for general utility use (ideal CW load 0w)	T48S				20220723

## BC9
Chargers: BC9	A					SCP_PS3: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L17	B58	WP11
2022	Jun	10	Fr					[BC9-10] Birth Date of new project "MikroTik 48v System LSWT": Mark and Keith called to order preparation of Wiegmann enclosure for exposed outdoor site that is not expected to go above 50w / Due to problems with Schauer chargers (T-comp reversed above ~35⁰C) I needed a new battery charger / power supply design ASAP / Therefore decided to pursue a Float Only Battery Charger design I soon called "Dual Supply with Traco Isolation"	T48-3 L17	Research				20220610
		16	Th					[BC9-10] Quick Dual Supply "Proof of Principle" test of V11 Traco and S13 ~54v power supply on output: / Initial results promising and decided to pursue this approach for LSWT using the SCP-75-12 or perhaps a 150-200w version	T48-3 L17 IMG					20220616
		20	Mo					[BC9-10] Researched Availability of a higher powered Battery Charger for Dual Supply Design (Mean Well): Desired specifications ~150~200w, BTS -5mV/cell/degC, Bulk CC + Float CV; SCP-75-12 (in stock MOU/DKE) is the highest power seen in that series (no 150 or 200w versions); Mean Well has nothing as simple as SCP series above 75w (many other offerings investigated briefly) / TFTP: For LSWT we can propose using SCP-75-12 (order), 27TMX (RCWT/WWT), LRS-150F-48 (stock)	T48-3 L17	Sales				20220620
		23	Th					[BC9-10] 20220623 Email to Mark & Keith 'Proposal - Lexington South Water Tower Installation'.pdf; Calls and SMSs Mark & Keith: Mark will pay $1,600 advance Mo-Tu next week and "go ahead and order"	T48-3 L17 DBT EML SMS					20220623
		24	Fr					[BC9-10] / DigiKey order placed for battery chargers and NTCs	T48-3 L17 EML DKE	On Order				20220624
		27	Mo					[BC9-10] DigiKey order received / Library > Mean Well AND Vishay > 20220624 DigiKey Invoice, Annotated; Battery Chargers and NTCs; T48-3 (LSWT) WP11-12 BC9-10 (SCP_PS3-4); 20220906 Scan.jpg	T48-3 L17 DKE SSC LIB	Available	L			20220627
	Aug	18	Th					[BC9-10] Prep of Supplies/Chargers for LSWT and Spares: L/N/G AC Plugs, BC9 12", S13 24" and (2) longer utility plugs for bench use, Battery Charger - Wire Label 0.5 in.lbx / Printed and applied Inventory Sticker 0.47.lbx; Battery Charger.lbx printed (to be applied to Wiegmann back plate) / Assembled BTSs with 18-20 AWG stranded (discarded cutoff 30"); Soldered BTS to CN2 connector pins (plastic shell removed, zip ties to cover for strain relief), BC9 photos / Epoxied BC9 BTS sensor into 5/16" lug and covered with shrink [Note added Su8/21: I should have added another layer of shrink!]; To be mounted on Wiegmann back plate for LSWT	T48-3 LBX IMG L17		L0			20220818
		19	Fr					[BC9-10] Further Prep of SCP-75-12 Chargers for LSWT and Spare: / Fabricated battery connections: Cut (5) wires coming from board at 4" (shrink on unused wires) / Extended B+ (fused 10A) and B- (same as V-) red/blk (16 AWG) with 30" #14 stranded red/blk (pigtail splice, zip ties to hold it all together and provide some strain relief) / 5/16" ring connectors with shrink / Decided not to put spare FS2 fuse with BC9 (or BC10) onsite (if it blows the unit will have to be disassembled to get to it, in which case it will probably be best to bring it back to the shop) / Tested to be sure BTS active / Adjusted BC9 and BC10 for target of 13.500vI at 25.0⁰C (Z19 T2, no battery, BTS metal pipe in Engel, ITECH CC 150mA): BC9 13.494vI, slated for LSWT	T48-3 PLN L17	Sold	L			20220819
		20	Sa					Dual Supply Bench Testing Setup Assembled: Wiegmann Back Panel on bench, BC9 mounted with heat sink compound; BTS on 27TMX negative post in Engel	T48-3 L17 IMG			B58		20220820
		21	Su					Test setup dissasembled briefly, added shrink to BC9 BTS (+1 layer) and Z20 T2 (2 layers); Stable at +25.0⁰C, Float 13.495vF, which agrees with 13.494vI from Fr8/19 adjustment to target 13.500vI @ 25.0⁰C BTS	T48-3 PLN L17					20220821
		30	Tu					[BC9-10] "W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; BC9 is slated for WP11 slated for LSWT	T48-3 L17	R&D			WP11	20220830
	Sep	3	Sa					Considered possible paradigm shifts for the prototype to obtain full redundancy, faster charging, and elimination of Load Supply: (2) SCP-75-12 in parallel?; Eliminate Load Supply, Diode and Relay? / Examined load regulation figures from datasheet and test report: The datasheet specifies +/- 2.0% and Note 5 "Load regulation is measured from 0% to 100% rated load" / "rated load" is the current spec of 5.4a or the power spec of 74.5w (they are equivalent at 13.8v output) / 2% of 13.5v = 0.27v (not very encouraging for our proposed application to eliminate Load Supply) / 8/4/09 Test Report result was -0.08% (FULL LOAD) to +0.12% (~MIN LOAD), at 13.5v this is ~-0.01v to ~+0.02v, which is a lot tighter than I thought, a lot tighter than spec, and would be very useable for our proposed application to eliminate Load Supply / [Note added Tu9/6: They probably didn't measure at the end of the battery cables provided, but on the board, maybe even at a PCB test point] / Library > Mean Well > 20220903 SCP-75-12 Test Report 20090804 SCP-75-12-RPT.PDF: Studied very carefully, very helpful information for Tcomp results and overload burn-in test at 132% load (99w) / The idea of eliminating the Load Supply looks promising, but the possible paradigm shift questions need to be decided after measuring the SCP-75-12 load regulation performance ...; / Modified test setup to measure SCP-75-12 load regulation 0~105w: Disconnected V11 and S13; ITECH on battery; Started measurements at 0w …	T48-3 LIB PLN				WP11	20220903
		4	Su					Measured BC9 Load Regulation 0~105w: Float Voltage and Charge Current data with ITECH loads from 0 to 105w / Conditions: Battery 25.0⁰C; BC9 Bench Ambient (~23⁰C); ITECH on battery; BC9 cables as constructed Fr8/19; See Sa9/3 T48-3 for Modified Test Setup and complete Test Conditions details / Results: 0w 13.479vI; 75w 13.187vI (0.3v lower than 0w); 95w 13.076vI (0.4v lower than 0w); At 100w and 105w BC9 cannot handle the load and keep the battery charged (runaway discharge); / Droop is about 3-5mV/Watt from 0 to 75w, than 5~7mV/Watt from 75 to 95w; Droop from 0 to 75w is -2.2%	T48-3 PLN					20220904
		7	We					We have stock on metric screws for blind mounting of supplies: For the SCP-75-12 they should be M3x4 and we have many M3x5 bought for W50	T48-3					20220907
		17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG					20220917
		18	Su					Disassembled Bench Test Setup and Wiegmann Backplate: Removed BC9 and cleaned thermal grease	T48-3 PLN				WP11	20220918
		19	Mo					Indirect Comparison of Z19 T2 with Z20 T2, CONCLUSIONs: I think it is safe to state that Z20 T2 reads ~-0.5 degC lower than Z19 T2 / This explains why I thought BC9 needed to be adjusted again for target 13.500vI at 25.0⁰C (because it was adjusted w/o battery using Z19 on Fr8/19, then I made observations using Z20)					20220919
				Cardboard template made for visualization / brainstorming on backplate layout: Photo shows layout of BC9, S17, V11 and other components (mostly considered, will finalize later)	T48-3 IMG					20220919
		30	Fr					Parts Assembled Onto Backplate: Photos / Started Point to Point Wiring and Cabling: Planned battery cable lengths; BTS cable is short but OK for Wiegmann (and maybe OK for any installation)		Assembly			WP11	20220930
	Oct	2	Su					[BC9-10] Bench Testing Started, BTS/27TMX (+25⁰C): BC9 Float 13.51vF, not adjusted; (BC10 also probably won't need to be adjusted)	T48-3 PLN				WP11	20221002
		3	Mo					Photo of W150_1 on bench next to Engel	T48-3 PLN IMG					20221003
		4	Tu					Bench Testing (stable at -15⁰C): Float 14.30vF, 0.02aE; Tcomp +25 to -15⁰C -20mv/⁰C; During discharge testing I noticed that LED1 is not lit; I was surprised, because BC9 sees the battery, but perhaps this is as designed (there might even be a diode in there somewhere so that battery V does not light the LED); This is a great indicator for the guys that there's no AC	T48-3 PLN					20221004
		5	We					Bench Testing (stable at +50⁰C): (Battery is still in recovery); Float 12.85vF, 0.38aE, Tcomp +25 to +50⁰C -26mv/⁰C; BTS Compensation Estimates (CONCLUSIONS) / W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 PLN IMG					20221005
		7	Fr					W150_1 Final Assembly and Invoice Date: Labels applied; [Invoice emailed to Keith and Mark Fr10/21]	T48-3 LBX	Sold			WP11	20221007
		8	Sa					Photos of W150_1: Product line and orthogonal photos	T48-3 IMG					20221008
		11	Tu					Loaded Subaru for onsite installation at LSWT	T48-3		Subaru			20221011
		21	Fr					Onsite at LSWT: Windy but warm; Photos; Installed B58 and WP11; Power levels measured, Traco Input 32.6w, Output 27.5w	T48-3 IMG		L17		WP11	20221021

## BC10
Chargers: BC10	A					SCP_PS4: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	B70-71	WP12
2022	Jun	10	Fr					BC9-10	T48-3 L17	Research				20220610
		16	Th					T48-3 L17 IMG					20220616
		20	Mo					T48-3 L17	Sales				20220620
		23	Th					T48-3 L17 DBT EML SMS					20220623
		24	Fr					T48-3 L17 EML DKE	On Order				20220624
		27	Mo					T48-3 L17 DKE SSC LIB	Available	L			20220627
	Aug	18	Th					BC9-10; (BC10 BTS Sensor not epoxied into connector)	T48-3 LBX IMG L17		L0			20220818
		19	Fr					BC9-10; BC10 13.501vI, slated for Spare, boxed on N bench	T48-3 PLN L17	Sold	L			20220819
		30	Tu					BC9-10; BC10 is slated for WP12 (W150_2) slated for CFS	T48-3 L17	R&D			WP12	20220830
	Oct	2	Su					BC9-10; (BC9 Float 13.51vF, not adjusted); BC10 also probably won't need to be adjusted for use in WP12	T48-3 PLN WP11					20221002
	Dec	13	Tu					WP12 Charger Configuration and Burn-In: As per WP12-13A; 13.493vI (no adjustment made); Burn-In 90wI 1.2 hours (procedure spec is 12 hours but I need to move on as CFS installation is still pending)	T48-4 PLN	Assembly			WP12	20221213
		14	We					WP12, as per WP12-13A: Configuration and Testing finished; Labels finished; Ready to be installed at CFS		Install	Subaru			20221214
		28	We		12:00		14:00	Onsite at CFS: Installed W150_2, vertical on left side of enclosure (side panel is removeable); Photos	T48-4 IMG	Applied	L18	B70-71	WP12	20221228
2023	Jan	30	Mo					1st Production Run Completed: (WP13 Completed); WP12-13 Invoice Date	T48-4 WP13	Sold			WP12	20230130

## BC11
Chargers: BC11	A					SCP_PS5: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L		WP13
2022	Nov	25	Fr					Production Run #1 Orders Completed: Ordered (1) Charger; Also ordered (2) Contactors	T48-4 EML SSC MOU	On Order			WP13	20221125
		29	Tu					Received (delivered by UPS)	T48-4 MOU	Available	L0		WP13	20221129
	Dec	1	Th					Inventory Sticker 0.47.lbx / Mean Well and Omron > 20221125 Mouser Invoice, Annotated; Charger, (2) Contactors; T48-4 (CFS) WP12-13; BC11 (SCP_PS5); 20221201 Scan.jpg	T48-4 LBX SSC LIB MOU	Assembly	L		WP13	20221201
2023	Jan	7	Sa					As per WP12-13A: Wiring and Cabling finished (BTS); Started Configuration and Testing; Target 13.500vI @ 25.0⁰C, achieved 13.509vI; Started 90wI Burn-In ...	T48-4 PLN	Testing	L0		WP13	20230107
		8	Su					As per WP12-13A Configuration and Testing: BC11 Burn-In completed (17.1h); BTS removed from Engel		Assembly	L			20230108
		30	Mo					1st Production Run Completed: WP13 Completed; WP12-13 Invoice Date	T48-4 LBX SSC	Sold			WP13	20230130
		31	Tu					Photo of WP13	T48-4 IMG					20230131

## BC12
Chargers: BC12	A					SCP_PS6: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	L		WP14
2023	Mar	8	We					[BC12-13] Ordered; Supplier MOU chosen because preferred supplier DKE out of stock (since before 11/25/22)	DWP MOU	On Order			WP14	20230308
		10	Fr					[BC12-13] Received		Available	L0		WP14	20230310
		11	Sa					[BC12-13] Summary entries and History sheets; W150 Inventory Sticker 0.47.lbx / MeanWell, Omron and TE Connectivity AMP Connectors > 20230308 Mouser Invoice, Annotated; DWP WP14-15; (2) Chargers BC12-13, (2) Contactors, (10) Ring Connectors; 20230311 Scan.jpg	DWP LBX SSC LIB MOU	Assembly	L			20230311

## BC13
Chargers: BC13	A					SCP_PS7: Mean Well SCP-75-12

Date/Time CST/CDT					Description	Other Sources	Status	Location	Batteries	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	L		WP15
2023	Mar	8	We					BC12-13	DWP MOU	On Order			WP15	20230308
		10	Fr					Available	L0		WP15	20230310
		11	Sa					DWP LBX SSC LIB MOU	Assembly	L			20230311

## C1
Controllers: C1	A					Genasun_1: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L7	WP4
2015	Apr	22					Ordered from altEstore.com	EML	On Order			20150422
		27					Received	TSP	Available	L		20150427
		29					Jumper installed for floaded battery (and sticker applied); Photos of bench testing	IMG		L0		20150429
		30					Installed at RW; Photos of initial installation with Mark Webb and Keith Jones		Applied	L1		20150430
	Jul	11					20 Amp Fuse Replaced (and sticker applied)					20150711
	Sep	3					Onsite at RW with Juliya	IMG				20150903
		16					Onsite at RW with Juliya (Sasha's iPhone)					20150916
2016	Mar	16					Onsite at RW (to install web relay)					20160316
	Jun	16					Onsite at RW (to install 3rd panel)					20160616
	Aug	27	Sa	~	15:55			Sudden drop to zero solar charge several hours before the end of the solar day; Restarts (software & webrelay) didn't fix it; SMS to Mark Webb for access …	SMS				20160827
		28	Su					… solar charge is normal. I suspect another Genasun "fart".					20160828
	Sep	1	Th	~	13:45	~	17:10	Zero solar charge again at a time when it should not be zero: I suspect a Genasun fault …; Some solar peaks through at end of solar day.					20160901
		2	Fr	~	11:50	~	14:20	Obvious signs of regulation at 13.3v (but could be malfunctioning Genasun) …; Sudden drop to zero solar charge again					20160902
		3	Sa	~	11:50	~	14:10	Obvious signs of regulation at 13.3v (but could be malfunctioning Genasun) …; Sudden drop to zero solar charge again					20160903
		10	Sa	~	10:55	~	13:25	Entered float (13.3v strong @ ~86W net) …; Dropped to zero solar again (Genasun?) @ net 65W					20160910
		17	Sa	~	14:10			Dropped to zero solar again (Genasun?); ~17:20 to 19:00 small spurt of solar but no more than 10W (as seen before when this happens)					20160917
	Oct	4	Tu	~	15:50	~	16:50	Dropped to zero solar again (Genasun?)					20161004
	Dec	16					Onsite at RW	IMG				20161216
2017	Jan	19					Onsite at RW to install 3rd Genasun_5 (C6)					20170119
2018	Apr	24					Onsite at RW (to remove W8 for a few days of correction on the bench): Photos of current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery)					20180424
	Aug	13	Mo					Onsite at RW 09:15; AC OK; Photos (before); Removed Genasun_1 and Genasun_2; Photos (after)		Available	L		20180813
2019	Jun	8	Sa					Chosen for WP4		Assembly	L0	WP4	20190608
		18	Tu					2 partially assembled W100 units side by side	IMG WP5	Applied			20190618
		28	Fr					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG WRD				20190628
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG				20190708
		9			12:45	~	17:25	Installed at OSWT		Sold	L7		20190709

## C2
Controllers: C2	A					Genasun_2: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L10	WP5
2015	May	4					Ordered from AltEstore.com; Slated for spare for RW (before the days of RN)	EML	On Order			20150504
		15					Approximate date received	TSP	Spare for RW	L		20150515
		20					Sticker applied for "Jumper Installed"			L0		20150520
		31					On bench	IMG				20150531
	Jul	6					Onsite at RW	TSP IMG		L1		20150706
2016	Jun	28					These records up to date, and sticker "Genasun #2" applied		Spare	TurboNet Toolbag		20160628
	Dec	16					Installed at RW as 2nd unit of 2 on lower P_3 (flexible monocrystalline)	IMG	Applied	L1		20161216
		22	Th	~	13:30			Onsite at RW and fixed loose connection on solar panel wire nut: (Since the 16th we've only been getting about 2/3 of the available solar).					20161222
2017	Jan	19					Onsite at RW to install 3rd Genasun_5 (C6)	IMG				20170119
2018	Apr	24					Onsite at RW (to remove W8 for a few days of correction on the bench): Photos of current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery)	IMG W8				20180424
	Aug	13	Mo					Onsite at RW 09:15; AC OK; Photos (before); Removed Genasun_1 and Genasun_2; Photos (after)	IMG	Available	L		20180813
2019	Jun	8	Sa					Chosen for WP5		Assembly	L0	WP5	20190608
		18	Tu					2 partially assembled W100 units side by side	IMG WP4	Applied			20190618
		28	Fr					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG WRD				20190628
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG				20190708
		14					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)					20190714
		17					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, A10, 6-pack (Heathkit)					20190717
2020	May	8	Fr		10:00		13:45	Travel, onsite in Lexington, AB and USB deposits; Plans are to install W100/B56 at LWT next week (kept in Subaru for now); Rec'd $690 payment	WP5	Sold	Subaru		20200508
		22	Fr	~	14:00			Installed at LWT	TW4-5		L10	WP5	20200522

## C3
Controllers: C3	A					TriStar_1: TriStar TS-MPPT-60 with TS-RM-2 Morningstar Meter

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Returned	-
2015	May	22					Ordered from WholeSaleSolar.com ($677.98)	EML	On Order			20150522
		29					Approximate date received	TSP	Available	L		20150529
	Jun	19					Returned (way too big and power hungry, was hoping to get monitoring capabilities, but changed direction towards using the Wattmons instead); Return S&H $42.84	EML	Returned	-		20150619
		24					WholeSaleSolar.com refunded $537.20					20150624

## C4
Controllers: C4	A					Genasun_3: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L	WP2
2015	Aug	16					Ordered from AltEstore.com; Slated for SAPS	EML MA2	On Order			20150816
		23					Approximate date received	TSP	Slated for SAPS	L		20150823
2016	Jun	28					Noticed that sometime in the past (when we were working on the SAPS in Sep 2015) that the backplate/mounting plate has the left end cut off (to make it fit in the SAPS box on the rear of the Subaru) so there may be a warranty issue (but could swap plates with another unit, except man'f stickers on rear would not match properly)	MA2	Modified for SAPS	SAPS Box		20160628
				These records up to date, and sticker "Genasun #3" applied					20160628
				"Flooded" jumper setting has been applied (but no sticker)					20160628
2018	Feb	25					Sticker for Flooded battery applied; Initial test for WISPer #2 (BK Precision for "Solar Panel" input) / Photos	WRD IMG	Testing WISPer #2	L0	WP2	20180225
	Mar	2					Delta 150W power supply rec'd, began testing for WISPer #2	WRD				20180302
		4					Testing WISPer #2 with 150W Deltec power supply continues; Now working on modeling a design with cover removed and fan above (cover and screws are in Wattmons box)	WRD TW2-3				20180304
		5					WISPer #2 test setup (no cover, fan temporarily taped to bench)	IMG				20180305
		11					Delta 200W power supply rec'd, testing for WISPer #2	WRD				20180311
		12					Genasun and fan mounted on top of Delta PS					20180312
		13					Better load and battery connections (final for RW); Photos 'W100 Testing' (Trace used as CW load, B1, Delta 200W, Genasun mounted under fan, W9, C252, BK)	WRD IMG	Slated for RW			20180313
		15					W100 Testing (Trace used as CW load, B1, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)					20180315
		20					W100 Testing, Calibration of C252 (WP2, Delta 200W, Genasun mounted under fan, B1, BK, Trace being used as CW load)					20180320
		24					WISPer #2 is now being called the W100	WRD	W100 Slated for RW			20180324
	Apr	2		~	15:15			Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	IMG EML				20180402
	May	2					Mark Webb wants WISPer #2 installed at Wellington Water Tower	EML	W100 Slated for WWT			20180502
		8					Labeled input connector; Finished product photos (L0, W100_1, DE_2, Genasun_3); Installed at WWT, photos and video (W100_1, DE_2, Genasun_3, 20160421_2/4, 20160421_3/4)	IMG WRD	Sold	L6		20180508
2022	Jun	28	Tu	~	15:15	~	16:30	Onsite at WWT: WP2 (W100_1) removed to take to shop	TM22		Subaru	WP2	20220628
		30	Th					W100_1 boxed, labeled and on North bench			L		20220630

## C5
Controllers: C5	A					Genasun_4: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L2
2015	Sep	10					[C5-6] Ordered from AltEstore.com; C5 slated for spare for RN	EML	On Order			20150910
		15					[C5-6] Received	TSP	Slated for RN	L		20150915
		19					Approximate date of installation at RN		Applied	L2		20150919
2016	Mar	16					Onsite at RN (to install web relay)	IMG				20160316
	Apr	30					Possible Genasun Failure: But it resolved itself on the next day (inconclusive)	AED				20160430
	Jun	28					These records up to date, and sticker "Genasun #4" printed but not yet applied					20160628
	Jul	16	Sa					Sticker applied	IMG	Sold			20160716
2019	Jan	22	Tu					Onsite at RN; Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)					20190122
2020	Aug	11	Tu	~	12:05	~	13:45	Onsite at RN with Keith; Photos TurboNet Onsite @ Swafford Tower; Keith Jones			L2		20200811

## C6
Controllers: C6	A					Genasun_5: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L1	WP3
2015	Sep	10					C5-6; C6 slated for "Extra"	EML	On Order			20150910
		15					C5-6	TSP	Available	L		20150915
2016	Jun	28					These records up to date, and sticker "Genasun #5" applied (still in the original box)					20160628
2017	Jan	19	Th					Jumper installed for floaded battery (and sticker applied); Installed at RW	IMG	Applied	L1		20170119
2018	Apr	24					Onsite at RW (to remove W8 for a few days of correction on the bench): Photos of current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery)					20180424
	Jul	20	Fr					Removed from RW, slated for W100_2		Available	L	WP3	20180720
	Aug	5	Su					Cover removed; Inventory sticker on base; Installed in W100_2 (WP3)		Applied	L0		20180805
		13	Mo					Finished product photos; Installed at RW	IMG	Sold	L1		20180813

## C7
Controllers: C7	A					Genasun_6: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L11	WP6
2020	May	26					[C7-11] Ordered	EML	On Order			20200526
	Jun	2	Tu					[C7-11] Received	TW6-10	Available	L0		20200602
		5	Fr					[C7-11] WISPer		Assembly…		WP6	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP6				20200612
		15	Mo					[C7-11] Assembly completed	WP6-10A	Float	L		20200615
		16	Tu	~	10:30	~	11:00	Onsite at RWWT with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix); Rec’d $1450 TurboNet check	TW6-10	Sold	L11	WP6	20200616

## C8
Controllers: C8	A					Genasun_7: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L3	WP7
2020	May	26					C7-11	EML	On Order			20200526
	Jun	2	Tu					TW6-10	Available	L0		20200602
		5	Fr					Assembly…		WP7	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP7				20200612
		15	Mo					C7-11	WP6-10A	Float	L		20200615
		16	Tu	~	11:10	~	11:30	Onsite at RHST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L12	WP7	20200616
2021	Dec	16	Th	~	16:25	~	16:45	Onsite at RHST: Met Mark in parking lot and 27TMX to Subaru ...; Finished pulling W100 from RHST; B58 and WP7 to be installed at RCWT	TM21F SMS		Subaru		20211216
				~	17:20	~	19:15	Onsite at RCWT: Installed (see L3 for details)			L3	WP7	20211216

## C9
Controllers: C9	A					Genasun_8: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L13	WP8
2020	May	26					C7-11	EML	On Order			20200526
	Jun	2	Tu					TW6-10	Available	L0		20200602
		5	Fr					Assembly…		WP8	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP8				20200612
		15	Mo					C7-11	WP6-10A	Float	L		20200615
		16	Tu	~	11:50	~	12:35	Onsite at ST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L13	WP8	20200616

## C10
Controllers: C10	A					Genasun_9: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L14	WP9
2020	May	26					C7-11	EML	On Order			20200526
	Jun	2	Tu					TW6-10	Available	L0		20200602
		5	Fr					Assembly…		WP9	20200605

		15	Mo					C7-11	WP6-10A	Float	L		20200615
	Jul	6	Mo	~	12:00			Installed at Odessa North Water Tower (ONWT) / Photos and videos TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb	TW6-10 IMG	Sold	L14	WP9	20200706

## C11
Controllers: C11	A					Genasun_10: Genasun GV-10-Pb-12V

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L15	WP10
2020	May	26					C7-11	EML	On Order			20200526
	Jun	2	Tu					TW6-10	Available	L0		20200602
		5	Fr					Assembly…		WP10	20200605

		15	Mo					C7-11	WP6-10A	Float	L		20200615
	Aug	14	Fr	~	10:15	~	17:10	Onsite at New Tower [OT] 2x; Installed box, electrical service, WP10 and B61; Photos	IMG	Sold	L15	WP10	20200814

## H0
HomeSolar: H0	A					KT: Karen Thomas

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$59.63	80.30	Cancelled	L8
2019	May	28	Tu		10:12			Initial contact, VM from 816-630-9138	KTD					20190528
				15:44		15:46	Called KT			0.03		0.03				20190528
				15:57		16:06	KT called and then we got disconnected			0.15		0.18				20190528
				16:08		16:51	KT called again: We should start with assessment of needs and expectations; New house location (SSC); Primary desire is to pay no electric bill; Old and hew houses are the same size; Offered my services; She'll contact me	KTD SSC		0.72		0.90	Research	L8		20190528
		29	We					Research on Tax Credits & Rebates for Solar; energysage.com Solar Calculator; Questions for her and topics of discussion if she calls back	KTD		2.00		2.90				20190529
	Jun	4	Tu		09:48		10:36	KT called, we discussed my questions (everything in green); More things to consider (yellow)			0.80		3.70				20190604
				13:19		13:45	Called KT; Set appt. for We6/5 2pm for me to visit her in Liberty (agenda)			0.43		4.13				20190604
		5	We	~	14:00	~	16:30	At her house in Liberty (18012 NE 84th ST, Liberty, 64068, driveway concrete, tall grass, across from culdesac Kara Lane): Long varied discussion; I s/b General Contractor for the Solar System; Rec'd originals for me to copy and return; Set appt. for Fr6/7 9am for her to come to Rayville and go visit the new house site; Mentions Bob Reynolds for site preparation; Mileage one-way 23 miles @ $0.58 and +30 travel time (I was in KC on other errands)		$13.34	3.00	$13.34	7.13				20190605
		6	Th	~	13:00	~	15:15	Scans of her originals partially completed (done while cooking, 1/5 the time)	KTD SSC		0.45		7.58				20190606
		7	Fr	~	03:25	~	06:55	Scans of her originals completed to D:\Documents\Business Management\Data Vision Services (JAK)\Thomas, Karen: 20180212^20190514;0607 KCP&L Karen Thomas, Scans of 36 Pages.pdf; (6) other scans of Platt & Cadastral Map, Commodore Homes catalog			2.00		9.58				20190607
				08:24			KT called, leaving Liberty, ETA 09:10; Preparation (estimated)	KTD		1.00		10.58				20190607
				09:10		10:20	w/KT @ DVS: Discussion, explained difference between best long term value and best 10 year value			1.17		11.75				20190607
				10:20		12:20	Onsite at KT w/KT driving: Met Robert & Roger (816-522-4345) Reynolds			2.00		13.75				20190607
		11	Tu	~	05:00	~	08:45	General Research: Inverters/chargers and Generacs			3.75		17.50				20190611
		12	We	~	05:15	~	05:45	Thoughts, TODO (+30)			1.00		18.50				20190612
				~	06:00	~	07:45	Started spreadsheet KTX sheet 'KCP&L Liberty'	KTD KTX		1.75		20.25				20190612
		13	Th	~	05:45	~	06:00	Thoughts, TODO	KTD		0.25		20.50				20190613
		14	Fr	~	00:15	~	01:15	Completed KTX sheet 'KCP&L Liberty': Baseline average is about 1.3kW or 30.1kWh per day	KTD KTX		1.00		21.50				20190614
				~	01:15	~	06:45	Researched solar controllers/monitors, discovered Victron (-60)	KTD		4.50		26.00				20190614
				~	22:00	~	00:30	General Research (-45)			1.75		27.75				20190614
		15	Sa	~	01:30	~	02:45	Thoughts and Questions TODO: Lots of details here in KTD			1.25		29.00				20190615
				12:28			Missed call, VM from KT					29.00				20190615
				~	13:15	~	14:15	Thoughts, Prep, Call to Karen Thomas, Thoughts			1.00		30.00				20190615
		16	Su	~	01:15	~	06:15	RN Baseline, Battery & Supplier Research: Started sheet 'Trojan and HUP'; Discovered TheSolarBiz.com			5.00		35.00				20190616
		19	We	~	04:45	~	05:30	Completed Acct Registration @ SolarBiz, Browsed site (comment posted), +06:15-07:15			1.75		36.75				20190619
				~	23:05	~	02:35	Browsed Blog on TheSolarBiz.com; Important Battery Considerations (KTD); Discovered Solar One HUP batteries (KTD, calculations and formulas); Improved sheet 'Trojan and HUP'	KTD KTX SSC		3.50		40.25				20190619
		21	Fr	~	10:30	~	12:45	Prep. & Call Karen Thomas, Long Discussion: Her present heat pump is 4 ton; Explained hopelessness of meeting the Winter and Summer maximum electric needs; Agreed to a $50,000 budget for solar; Very rough preliminary estimate for Minimum Average	KTD		2.25		42.50				20190621
		26	We	~	12:30	~	13:45	w/KT in Liberty: Data from outside condensor, KCP&L 6/13/19 Billing Date, Air Handler and Evaporator coil; TODO; 23 miles +30 travel time (in KC also to go to Lowe's)	KTD KTP	$13.34	1.75	$26.68	44.25				20190626
	Jul	2	Tu	~	08:14	~	09:15	KT called: Liberty/Clay Zoning 1st mtg. is 8/6, probably can sell starting 8/19-25; Commodore doesn't want to share plans, but Lovejoy will build as a Champion; She found the Liberty house plans	KTP		1.02		45.27				20190702
				18:23			Missed call, VM from KT: She has all the electric bills for 2017; A/C in sun room was installed Dec 2017; If interested let her know			0.10		45.37				20190702
		19	Fr		13:50			Missed call			0.10		45.47				20190719
		20	Sa	~	09:15	~	12:00	Called KT: She's given up on pre-fab builders and is having Bob Reynolds give her a price on the house; I mentioned the Amish; Zoning is in process, 3 lots 10/10/20 acres can be sold soon	KTD		2.75		48.22				20190720
		23	Tu					Surprise visit from KT, some discussion of project			0.75		48.97				20190723
		28	Su					Calls From/To KT: Bob Reynolds will be building the house; They are going to apply for a construction loan, trying to include solar; Needs something from me to show to the bank; Th-Fr next week	KTD SMS		1.00		49.97				20190728
		30	Tu	~	04:50	~	08:15	Set up sheets and entries needed in this workbook for KT in HomeSolar; Created KTD from TODO	KTD		3.42		53.38				20190730
	Aug	1	Th		16:04		16:06	VM from KT …; Missed call			0.10		53.48				20190801
		2	Fr	~	05:00	~	07:10	Quote draft 90% finished			2.17		55.65				20190802
				~	07:10	~	08:10	Called KT: Info on problems with getting Construction Loan that will cover solar, she's still searching for financing; Need to finish Quote and print some other stuff to show the bankers			1.00		56.65				20190802
				~	08:10	~	08:30	Further thoughts and wrap up for today			0.33		56.98				20190802
				12:35			Missed call from KT					56.98				20190802
				~	18:00	~	18:15	Repaired KTD for subsequent updating			0.25		57.23				20190802
				19:13		19:15	VM from KT …; Missed call			0.20		57.43				20190802
		3	Sa	~	07:30	~	11:45	Finalized 20190803 Initial Quote for Construction Loan.doc; 2 copies printed with Attachments from KTX; Prep; KT @ DVS, detailed discussion of Quote (typo fixed), we are in agreement, printed 3 copies	KTD KTP		4.25		61.68				20190803
		5	Mo		10:18		10:35	KT called when I was in the driveway having just returned from town			0.28		61.97				20190805
				~	14:15	~	15:25	Called KT: She wants me to do the site plan, and will pay me for that (jokes about amount) / Appt. to meet her and Reynolds onsite Sa8/10 08:00; VM and text followed to confirm OK with Bob Reynolds	SMS		1.17		63.13				20190805
		9	Fr	~	02:45	~	07:10	Updated this sheet, L8 and KTD formatted for subsequent recording of details not included here; TODO organized	KTD		4.42		67.55				20190809
				~	10:00	~	10:30	Phone calls to find and price stakes needed for going onsite			0.50		68.05				20190809
				~	10:30	~	10:45	Called KT to confirm she wants stakes bought and that we're still on for tomorrow; I mentioned that perhaps she could ask Bob Reynolds if he has a laser level; She got extremely angry and started yelling "you will show that man respect" and "you are being arrogant"; I said I was "just pointing out tools that were going to be needed to do the job," and "I've never once yet ever shown disrespect for Bob Reynolds; She said "be there tomorrow," "I want receipts" and hung up on me; Phone call lasted 6 min 13 secs			0.25		68.30				20190809
				~	10:45	~	11:00	Thoughts: "Make no friendship with an angry [wo]man, and with a furious [wo]man thou shalt not go."; She took offense when she didn't need to; "Her fuse is too short and she lights it when I'm just trying to get the job done."; Out of respect for Bob Reynolds (and her) I should be onsite at 08:00 (can start by asking Bob in her presence if I have ever shown him any disrespect); Wait and see if she apologizes, but even if she does I should "eject stage right"; At this point she is going to have to try very hard to convince me to be involved in her project (my price just got higher, I can't work with her if she blows up over things she doesn't understand)			0.25		68.55				20190809
				~	11:40	~	13:00	Further thoughts: Go buy the stakes and flags (At the very least I can give them to Bob Reynolds as a token of respect); Drove to Richmond Derstler ($20.19, 22 miles, -15 for WM)	KTF	$32.95	1.00	$59.63	69.55				20190809
		10	Sa	~	06:15	~	07:25	Prep. to go onsite: 20190810 Site Map Template Google Maps SSC 7.834x9.711.jpg; 5 copies printed; Loaded Subaru	SSC KTF		1.17		70.72				20190810
				~	07:45	~	09:45	Travel & onsite at KT: KT once again angry with me when she showed up (as to how she thinks I am disrespecting Bob Reynolds) / Stakes for general house location and solar farm (5 total); Discussions with KT and BR, agreement for a battery bunker like a root cellar; CC/AT&T signal is nonexistent onsite / I had a good long talk with BR, during which I asked him if I had every shown him any disrespect (NO) and we talked about transits and laser levels / BR invited me to visit him in Excelsior Springs (816-654-2422); I invited him to visit me in Rayville; White sheet '8/10/19-8/11/19'	IMG KTF WS		2.00		72.72				20190810
				~	10:00	~	10:15	Bob & Roger Reynolds at DVS for quick tour; White sheet '8/10/19-8/11/19'	KTF WS		0.25		72.97				20190810
				~	10:15	~	11:30	Thoughts on battery bunker design; White sheet '8/10/19-8/11/19'			1.25		74.22				20190810
		11	Su	~	04:15	~	04:45	Further thoughts on battery location (s/b house bsmt.); White sheet '8/10/19-8/11/19'			0.50		74.72				20190811
				~	06:00	~	10:05	KT VM & Missed Call; Called KT (06:20-09:54, 2 Hrs 34 Mins); KT is a very disturbed woman who has suffered a lot of abuse and doesn't recognize when she is abusing others; She quotes the Golden Rule but then violates it constantly; Blindness; Irrationality; I explained the technical and cost issues concerning the location of the batteries (s/b basement, not bunker); When we hung up we were in agreement and all looked good to continue the project, as she agreed I should contact BR to discuss change to not build bunker, meet her at her house in Liberty to see her basement layout and discuss her vision for the new house basement; See notes on bank slip 'Su 8/11'			4.08		78.80				20190811
				11:38			SMS from KT: 'I think it will be better for all concerned to table this project indefinitely. As you so eloquently remind everyone that I don't know what I want I am going to prove you right so you can win and I can walk off. Best wishes and good luck in your solar endeavors.'; I'm not surprised; All work on the project halted; I won't call or go to Liberty on We8/14; Will visit BR but for future possibilities of business (he would be a good choice as contractor for the HVAC concrete work I need, or might be interested in my services for home solar)	SMS EML		0.25		79.05				20190811
		12	Mo	~	03:30	~	04:45	Photos transferred from phone; .xlsm updates; TODO moved to KTD; Notes filed; Case closed (I'm done with KT project)	KTD KTF		1.25		80.30	Cancelled			20190812

## H1
HomeSolar: H1	A					DF: David C. Fuller

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$71.23	90.62	Operational	L9	(8) L16RE-B
2019	Aug	21	We					I rec'd his business card during my Wednesday visit to Opportunity Café: / 20190821;22 DF Business Card Scan 1.jpg; 20190821;22 DF Business Card Scan 2.jpg; 816-536-7729 (c)	DFP DFD SSC		0.08		0.08	Sales			20190821
				11:08		11:09	Called DF while in the parking lot: He has purchased solar stuff and wants help hooking it up; I promised I would contact him later after I returned to the shop	DFD		0.08		0.17				20190821
				14:43		14:53	Called DF and LMVM			0.17		0.33				20190821
				15:40		16:30	From DF …; To DF …; From DF (we'll talk in the morning)	SMS DFD		0.25		0.58				20190821
		22	Th		09:55	~	10:55	Missed call & VM from DF; Immediate call to DF (some particulars, home address by SMS) / He wants to pay me for a few hours @ $80 (advice, counsel, help with final assembly); Agreed to meet onsite Fr8/23 08:00; 20190822 Google Maps SSC.jpg; TODO	DFD SMS SSC DFP		1.00		1.58	On Order	L9		20190822
				~	23:00	~	00:35	Created file David Fuller Solar.docx (DFD); Other Sources Codes DFD and DFP (started paper file); This sheet and L9 created; Scanned business card; Printed Google Maps Satellite View (these records are now caught up); TODO	DFD DFP SSC		1.58		3.17				20190822
		23	Fr	~	07:30	~	10:45	Prep. and onsite at DF; Panels don't face S, and there's trees shading them in the morning, derate to 1/3 (9*365w*0.3=~1000w, see MMS from DF) / (8) Trojan L16RE-B (C/20 370AH), he wants 24v for the fridge/freezer so will run 2 strings of 4 (740AH @ 24v); Battery bank interconnections and spacing set / Panel wires pulled (they were damaged); Panel combiner location set; Backwoods Solar Kit; Magna Sine MS4024PAE Inverter/Charger; MMP250-30D (Disconnect/transfer) / MNPV6 (Panel Combiner); Midnite Solar Classic 150 (MPPT Charge Controller/brains); TODO (he wants me back this afternoon after I put shrink tube on the panel wires and bring back tools); I agreed to $80/hour not counting travel or prep. (onsite expertise time only, so far $160); 17 miles; 20190823;24 1 Onsite Notes Scan.jpg	SMS SSC DFP IMG	$9.86	3.25	$9.86	6.42	Assembly		(8) L16RE-B	20190823
				~	11:15	~	13:00	Call from DF (meet back onsite at 13:00); I called to discuss panel blocking diodes, battery cables, T-105s … but we'll discuss it later (TODO) / TODO; R&R and shrink on panel cables ($20); Prep. (loaded Subaru, filled out Sales Order)			1.75		8.17				20190823
				~	13:00	~	16:30	Travel and onsite; DF wasn't done with conduit for panel wires, so while waiting I studied the manuals; Inventory of parts and overview of TODO; Re-installed panel wires / $170 for this visit; Sales Order completed and rec'd $350 cash; Return travel +15; Follow up thoughts & TODO +30; 17 miles / 20190823;24 2 Onsite Notes Scan.jpg; 20190823;24 3 Sales Order $350 Scan.jpg	SMS SSC DFP	$9.86	4.25	$19.72	12.42				20190823
		24	Sa	~	04:25	~	06:35	Recordkeeping; Thoughts and TODO; Scans; 20190823;24;0904 Invoice.doc; Photos transferred	SSC DFP		2.17		14.58	Research			20190824
		25	Su	~	05:30	~	09:45	Downloads for his equipment; 20190825 L16REB_TrojanRE_Data_Sheets.pdf; Datasheets and manuals studied; Notes (DFD); TODO; Discovered bad design choice for Classic 150 (it won't turn on when panel Voc >150, which is any time the temperature is below 53°F) …	LIB DFD SSC		4.25		18.83				20190825
		26	Mo	~	04:45	~	09:00	… More downloads and research; 20190826 David Fuller Classic String Sizing Tool.pdf (Classic 150 is marginal on VOC); Thoughts on pole mount for his panels; TODO; Called DF (NA, LMVM)	LIB DFD SSC DFP		4.25		23.08				20190826
				09:26	~	09:50	SMS from DF "Jeff I'll call you if I need any further help thank you."; SMS to DF "I spent 11 hours studying your system design over the weekend. With what I know about your capabilities, you are going to need my help. But that's okay, I'm happy with whatever you decide to do. However I thought the goal was to get your system up and running properly. And that you wanted me to help finish it. That is why I devoted my time this past weekend to your project, seemingly at no charge. Now I did find out some things that you should be interested in knowing. I would be glad to share this with you over the phone, or if you are concerned about your budget, you should come here for a visit. You're welcome to come out and see the shop! And I'll make you coffee, pour over. Please don't cut me off."	SMS		0.40		23.48	On Hold			20190826
				~	10:30	~	11:00	I've heard nothing from DF; Decided to mail invoice, sizing tool results, screenshots of TODO and this .xlsm; $0.47 stamp	SSC DFP	$0.47	0.50	$20.19	23.98				20190826
2019	Sep	3	Tu					Mail sent 8/26 returned as undeliverable			0.10		24.08				20190903
		4	We	~	08:30	~	09:30	Tools put away; Nicad on charge; 20190823;24;0904 Invoice.doc modified to remove statement about total time and put something helpful on it; Invoice and Classic Sizing Tool to Opportunity Café for them to give to "Doc" (discarded printouts of screenshots of TODO and this .xlsm); TODO moved to DFD; To DF "Paid invoice and other information was mailed 8/26 to the address you gave me (12696 Cave Lane 64024), but it came back as undeliverable. I'll take and leave it at the Opportunity Cafe."; From DF "No worries I don't have to have a receipt thank you"	DFP DFD SMS		1.00		25.08	Cancelled			20190904
				09:59			Call from DF while driving; "No hard feelings"; Can't afford $80/hr; He has electrician who asks for $15-20/hr and he usually pays him $20-25/hr; SMS From/To DF, has $200 more he can pay me; Onsite 12:30-12:45 (3 miles, sidetrip only), gave him sealed invoice/report, discussed 150/200 choice, scheduling; I agreed to $20/hr (but "we start early" and don't work past noon); Tentatively agreed to Th9/5 07:00 ... upon arriving back at shop SMS To/From DF concerning scheduling, agreed upon Friday 07:30, he has already ordered the Classic 200	SMS	$1.74	0.50	$21.93	25.58	Research			20190904
		5	Th	~	05:15	~	07:45	TODO (mostly from DFD but updated); Loaded Subaru; Continued downloading/studying datasheets and manuals for his equipment; Printouts DFP	LIB DFD DFP		2.50		28.08				20190905
		6	Fr	~	04:45	~	07:00	Continued downloading/studying datasheets and manuals for his equipment; Preparation to go onsite	LIB DFD		2.25		30.33	Assembly			20190906
				~	07:00	~	12:00	Travel and onsite at DF 07:30-11:45 (17 miles); Solar panel combiner box completed except for ground; Reviewed cables/wire needed and specified wire, grounds, clamps and strain reliefs needed (DF will procure); Discussed incident he had when he hooked up the fridge (reverse polarity, may have damaged fridge control circuit); I recommended massive pole mount for the remaining panels; Generator is pull start, but he's going to replace w/starter type and install ME-AGS-N (Auto Generator Start); $60 cash; Appointment for Tu9/10 07:30	DFP	$9.86	5.00	$31.79	35.33				20190906
		8	Su	~	02:25	~	03:45	Recordkeeping; TODO; 20190906;08 Invoice.doc	DFD DFP		1.33		36.67	Research			20190908
		9	Mo		08:57		11:52	From DF "UPS is supposed to deliver the park [sic] tomorrow so Wednesday would be great if that works for you" …; To DF "OK, Wednesday 07:30 )))"	SMS		0.10		36.77				20190909
		10	Tu	~	06:30	~	07:00	Created and printed 20160616;20190910 RW Photo and Metadata Description.docx (to share with DF concerning his choice of where to put the solar panels)	DFP		0.50		37.27				20190910
				~	17:54	~	19:16	Missed call & VM from DF; Classic 200 did not come in, ETA tomorrow by end of day; Thursday?; To DF "OK, Thursday 07:30" …; From DF Thumbs Up	SMS		0.20		37.47				20190910
		11	We		16:54			From DF "I got the part"			0.10		37.57				20190911
		12	Th		03:12		03:13	To/From DF "Great! Let's generate some electricity today, if we can."; [smiley face]			0.10		37.67				20190912
				~	05:30	~	07:15	Continued downloading/studying datasheets and manuals for his equipment; Printouts; Preparation to go onsite	DFP		1.75		39.42	Assembly			20190912
				~	07:15	~	13:45	Travel and onsite 07:30-13:30 (6 hrs, 17 miles): Discussed 24vdc run to fridge and other upstairs needs including lights and water pump; Existing sub panel ground screw installed and wired sub panel for split phase 120/240; MMP ground partially installed (DF); Inverter/charger removed, reinstalled and wired up to MMP (split phase 120/240 in/out/nuetral/ground); Installed clamps/strain reliefs for battery, AC input/output and PV cables; Cables to sub panel and from generator prepared; Breakers for PV input (60A) and Classic 200 output (100A) installed; Panels wired to MMP (breaker and DC negative busbar); Classic 200 solar charge controller mounting planned/partially completed		$9.86	6.50	$41.65	45.92	Research			20190912
		13	Fr	~	02:30	~	06:30	Recordkeeping; TODO; 20190912;13 Invoice.doc; Further research; Battery Vent specs for DF (printouts)	DFP DFD		4.00		49.92	Assembly			20190913
				~	06:55	~	12:45	Prep. and onsite 07:30-12:30 (5 hrs, 17 miles): DF routed the generator cable through the wall and finished the main ground for the MMP; Classic 200 mounted on the wall and wired up to the MMP including #4 wire I provided; Battery bank to MMP connections finished and all connections TIGHT; BTS (Battery Temperature Sensors) installed; MMP to existing sub panel finished; Generator to MMP finished including male plug; Agreed to meet back at or before 15:30 to turn the system on	DFP	$9.86	5.83	$51.51	55.75				20190913
				~	13:50	~	20:00	Recordkeeping; TODO; Prep. to go onsite again; Labels for MMP printed / Onsite 15:30-~19:45 (4.25 hrs, 17 miles): Connected battery; Started inverter; Applied labels for breakers on MMP; Connected Classic 200; Started Generator / Drank wine ($10 added to income) while charging the batteries (system is operational); Rec'd $225 check and agreed to call it even now		$9.86	6.17	$61.37	61.92	Operational			20190913
		15	Su	~	03:50	~	04:30	Recordkeeping; TODO			0.67		62.58				20190915
				~	06:20	~	07:10	TODO; 20190913;15 Invoice.doc; Scrap wire from DF put away	DFP		0.83		63.42				20190915
				11:44		12:24	To/From DF: "Has it reached float yet?"; "Yesterday, for a while, will run gen today to hit it hard"; "Good idea. The batteries need another 2 hour absorption."; "I'd like to stop by Wednesday 11-12 am, I can help you fine tune if you let me shoot some high quality photographs for my website gallery."; "I have to see if Wednesday works but yeah I think you should shoot some pictures"; "After I get my errands done in Excelsior Springs I can swing by and might be able to help you out for a little while (as a friend)."	SMS		0.33		63.75				20190915
		18	We	~	12:15	~	16:00	Onsite at DF (I stopped by on my way back from errands in Excelsior Springs, where DF bought me coffee at Opportunity Cafe, $4 added to income) / Checked tightness of clamps MMP and main ground; Reviewed Classic 200 daily logs (system has been reaching Float every day since 9/13); Installed battery monitor / Accidently shorted battery and destroyed brass screw on shunt; Round trip to shop with DF to get screw (17 miles) / Finished installing battery monitor and remote is working; Checked to be sure Classic 200 DC GFP is enabled (it is, jumper is installed, default from factory)	DFP	$9.86	3.75	$71.23	67.50				20190918
				~	17:10	~	17:25	TODO			0.25		67.75				20190918
				17:00		19:38	To/From DF: "That was a lot of fun --- Sparky" and admonitions to use more electricity or free solar is wasted	SMS		0.20		67.95				20190918
		19	Th	~	08:45	~	09:15	Recordkeeping; TODO			0.50		68.45				20190919
		23	Mo		08:36		08:53	Missed call & SMS from DF "Do you have any desire to help hook up the refrigerator and battery box fan"	SMS		0.10		68.55				20190923
				~	09:25	~	10:05	Research, PVC Flanges, best found is online '2" Schedule 80 PVC Slip Flange" $6.62 each; TODO; Call to DF, told him about flanges, agreed to meet at his house Tu9/24 @ 07:30; TODO			0.67		69.22				20190923
		24	Tu	~	04:10	~	06:35	Created and printed 20190924 EXPECTED LIFE VS. TEMPERATURE as per Trojan.docx; Research (battery monitor, ME-RC ...)	SSC DFP DFD		2.42		71.63				20190924
				~	07:15		13:50	Prep., travel and onsite 07:47-13:35 (17 miles, +15 return): Examined Classic 200 logs (last Float was on 18th); Battery room vent system installed and operational, 27.2v Fan High (tested, Generator and Solar, doesn't run in Float); Vent system relay replaced (RS Relay $20 value my cost ca. 1988 $5.99+tax, let's call it $15 now as that is the least I can expect to replace it for); Upstairs 24vdc circuit installed (50A DC breaker, #8 jacketed); Refrigerator operational; ME-RC, set AH Capacity 700, Charge Efficiency is Auto [default]; Shared and discussed 20190924 EXPECTED LIFE VS. TEMPERATURE as per Trojan.docx; $80 Cash Rec'd (added to total income)	DFP	$24.86	6.58		78.22				20190924
				15:06		16:54	From/To DF: MMS with screenshot of fuse block for upstairs circuit, etc.	SMS		0.20		78.42				20190924
		25	We	~	05:30	~	06:45	NiCd charged; Recordkeeping; TODO; 20190918;24;25 Invoice.doc	DFP		1.25		79.67				20190925
2019	Oct	9	We	~	06:45	~	08:45	20191009 Key Battery Parameters.doc created, printed draft (not complete yet, but can review it onsite); Called DF, LMVM			2.00		81.67				20191009
		11	Fr		06:02		08:23	From DF "Good morning"; To DF "Good morning" (in Russian); From DF "Right"; To DF "You need to set the battery vent control to 26.4 volts. 27.2 volts is a little high. (Aux1 on Solar Classic 200)."	SMS		0.20		81.87				20191011
				~	11:00	~	11:10	Call to DF: He was busy, not interested in battery vent control, but he said to come next week on a sunny day (call him after 6am)			0.17		82.03				20191011
		17	Th	~	14:00	~	14:25	Planned possible onsite visit; Call to DF, noon tomorrow is good, call him before leaving @ ~11:45 to confirm			0.42		82.45				20191017
		18	Fr	~	09:40	~	14:25	Continued working on 20191009;18 Key Battery Parameters.doc (still only a draft); Call from DF, rescheduled for later today or Sunday/Monday			4.75		87.20				20191018
		23	We	~	06:30	~	08:40	Finalized 20191009;18;23 Key Battery Parameters, ME-RC.doc; Started draft 20191023 Key Battery Parameters, Classic 200.doc			2.17		89.37				20191023
2020	Jun	4	Th	~	21:30	~	21:55	TODO for 12:36 Missed call and 12:37 VM “Questions, please call”; SMS to David “… I’ll call you in the morning around 9 am, okay?”; From David “Great”	SMS		0.42		89.78				20200604
		5	Fr	~	09:00	~	09:50	Reviewed files; Called David; Notes in .docx; TODO	DFD		0.83		90.62				20200605

## I1
Inverters: I1	A					PS_4: PowerStream INV1224

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Sep	8					Ordered from PowerStream: $100.00 + $6.15 S&H	EML	On Order		20150908
		18					Received	Slated for SAPS		L0	20150918
2018	Jun	9					This sheet created	MA2		SAPS Box	20180609
		22					This history sheet moved from Summary 'Converters'				20180622
		29					Package opened and discarded; Inventory Stickers applied; User's Guide scanned; Bench test; Quiscent current 0.193 Amps @ 13.00v (2.5w), 0.224 Amps (2.9w) powering DI_1 (Z11); Inverter shuts off below 9.8v, restarts above 10.7v	LIB		L0	20180629
	Jul	1					Decision made not to use in SAPS project (MA2): stored near center door with stuff for hot water heater control	MA2	Available	L	20180701

## L
Locations: L	A					Shop: 202 W 3rd ST, Rayville (also used if in storage somewhere in the building)

Date/Time CST/CDT					Description	Other Sources	Status
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active
2000	Aug	1					[L L0] Property purchase closing date (202, 204 & 206 W Third ST); Construction of the shop began almost immediately with the demolition of the old house at 202 W 3rd ST			20000801
2001	Oct	16					[L L0] Shop construction mostly completed (benches finished, approximate date); Bench work begins, focused on monitor repair (which DVS had been doing in Colorado since 1997)		Active	20011016
2002	Jan	30					[L L0] Although the shop was constructed to continue monitor repair (as DVS had been doing in Colorado since 1997), monitor repair is mostly dead, so we began moving into computer repair (see email from Nathan Van Duyn)			20020130
	Apr	30					Rayville Baking Company and Hallard Station Pizza begin operations in 'Bakery' (NW corner of building) (see email 'We are under way!') (approximate, sometime in April 2002)	EML		20020430
	Jun	24	Mo					Hallard Station Pizza opens (see HS Sales.xls)			20020624
2004	Nov	7					Honda Civic Wagon in W side Garage (file transfer date)	IMG		20041107
	Dec	23					Hallard Station Pizza closes (soon after this the Van Tills begin to make plans to move to their own facility S of town)			20041223
2005					Rayville Baking Company moved out of the building sometime in early 2005 (before 4/29/05 email where I state "… the Rayville Baking Company is no longer here …")	EML		20051223
	Nov	10					"DE Building" (shot with Tom's camera)	IMG		20051110
2006	Jan					Missouri Woods begins meetings and operations in the building			20060110
	Sep	26					"MW Truck and trailers" parked in front of the shop	IMG		20060926
2008	May					Disagreements begin with Tom and Art: locks changed (to keep the DE and MW equipment intact until dissolution of the partnership)			20080526
	Oct	15					Main shop room	IMG		20081015
	Dec	20					Missouri Woods moved out of the building: Art picked up his equipment that was in the NW room; Dynamic Enterprises is in the process of being dissolved on paper			20081220
2009	Oct	18					Photos in early morning of the Rayville homestead showing the porch on the shop	IMG		20091018
		24					Building and DVS sign			20091024
	Nov	21					Photos on the roof of the building (StarBand repoint)			20091121
		26					Photo shoot in the old bakery space (NW room): Anytime Fitness MSI VGA shots (11/27/09)			20091126
2012	Aug	29					Photos at Rayville Folk Dance party: This shows that the remodeling of the W side was completed			20120829
2013	Jan	20					My home at 204 W 3rd burns: W side used to store what we could salvage			20130120
	Mar	13					[L L0] Plane leaves Denver for trip to Ukraine (shop and benches are idle, but Joe Coleman and Mark Hall keep an eye on things)		Idle	20130313
2014	Dec	25					[L L0] I return from Ukraine after spending about ten days in Colorado (approximate date); What a mess, I'm depressed, not much gets done for a few months		Active	20141225
2015	Jan	29					[L L0] I started to clean up the mess; Photo of stuff on the bench in the main shop	IMG		20150129
	Apr	9					Trees cut down that were surrounding the shop			20150409
		10					More photos of trees being cut down around the shop			20150410
		29					StarBand antenna on roof (no longer in service, soon to be removed to make way for TurboNet)			20150429
	Jun	25					Back yard with Sasha			20150625
	Aug	28					Juliya, Mark Hall & Red Porsche			20150828
	Nov	10					Juliya Dudar on her throne			20151110
2016	Jan	4					Juliya's throne after the first winter snow			20160104
		21					Building from NE showing antenna mast with SureCall omni and TurboNet link			20160121
		27					Sunset at the shop: Looking SW towards the Rayville PWSD Water Tower and the burnt house, photo from W side porch of the shop			20160127
	Feb	5					Photos on roof: SureCall cellphone booster directional antenna mounted on antenna mast			20160205
		12					Photos: Sunset from the porch showing Subaru, PWSD #2 tower and jet trails in the sky			20160212
	Mar	29					Butch on Juliya's throne			20160329
	Dec	25					Website Hosting Hardware (shared with Yevgeniya)			20161225
2017	Jan	27					Building shown in photos of Wood for Sale			20170127
	Jul	20					Subaru and EZ-Tow Dolly: Shop East side lawn; Porch (accessories)			20170720
	Sep	24					TearDrop sold: Buyers in front of shop, Subaru parked to the East (damaged battery box)			20170924
2018	May	25					T450s setup in rear room			20180525
	Jun	8					East side mushrooms (photos of building)			20180608
	Jul	22					Burn pile (house demolition) showing shop building			20180722
		27					House demolition, dumpster, with shop building in background			20180727
		28					House demolition, shop building in background			20180728
	Aug	10					Rayville to Excelsior Springs video showing exit from garage (and Rayville Baking Company sign)			20180810
				Squash plants germinating, just off the porch			20180810
		13					Rayville to Corner Store video showing exit from garage			20180813
		14					Rayville to Richmond video showing exit from garage			20180814
		21					House Demolition and Porsche, showing many views of the building and porch			20180821
		22					Squash plants growing, just off the porch			20180822
		24					House demolition, various views of W side of shop			20180824
	Sep	8					Squash plants reaching maturity, just off the porch			20180908
		27					Moon over RW, shot from the porch			20180927
2019	Jan	12					Julia's Throne, 9 Inches of Snow			20190112
		31					Photo from shop porch: Snow, cold, water tower, Triton, Julia's Throne			20190131
	Feb	1					Shop Porch Cooking	IMG L0		20190201
	Mar	19					Subaru in Garage THE STATE IS NOT GOD, DEFYTYRANTS.COM	IMG		20190319
	Apr	12					Russian Tomato Plants have germinated, E shop window			20190412
	May	16					Tomato and Pepper plants growing in E window			20190516
		17					Wireless Thermometer, N Outside Main Shop; Porch Garden, Tomatoes, Peppers & Onions			20190517
		23					UPS stack, W Storage; Network UPSs, PowerCom, Liebert, Delta, Trojan T-105s			20190523
		29					Pepperoncini Baby off the porch			20190529
	Jun	1					[L L0] Defrosting Refrigerator			20190601
		2					Vagrant Wearing Stacey's Cap on the porch			20190602
		18					Porch Garden, Front Trellis, Tomatoes, Peppers			20190618
	Jul	1					Sandblasting curtain raised, as seen from shop porch			20190701
		2					20190702
	Aug	13					[L L0] Porch Tomatoes and Peppers; Tomatoes on the Bench			20190813
	Oct	28					Porch: Final Fall Tomato Harvest			20191028
	Dec	4					Video of tree being cut down to improve TurboNet internet service "line of sight" to RW (204 W 3rd ST): Jeffrey's Tree Service, with Jake & Marcus			20191204
2020	Jan	7					204 and 202 W 3rd, Tree Down; Shop building			20200107
		14					Garage: Subaru Gasoline Tank Repair			20200114
	Apr	23					Tomato Starts in E Window			20200423
	May	1					20200501
		3					Porch: Tomato Starts			20200503
		7					Pepper Starts in E Window (Calvary Baptist Church)			20200507
	Jun	23					Plants in E Window; Tomatoes and Peppers (Calvary Baptist Church); Photos and videos from front porch of Art True Mowing 202/204 W 3rd, Rayville Water Tower, Julia's Throne, flatbed trailer	IMG L0		20200623
		29					Porch garden photos and video: Tomatoes and Peppers Transplanted	IMG		20200629
	Jul	7					Porch Garden Irrigation, Peppers and Tomatoes Reviving From Recent Transplant Abuse			20200707
		18					'Ukrainian' House Slippers (socks, my American version)			20200718
	Sep	26					Rear room T450s computer setup (for Sasha D.)			20200926
	Oct	5					Snowshoes in West Storage (for Sasha D.)			20201005
		15					Photos and videos, Marcus: Bobcat, Burnt House Cleanup			20201015
		26					Front porch, First Snow (for Sasha D.)			20201026
		30					From front porch: Moon and Mars (shared with Sasha D.) (Julia's throne, Rayville Water Tower)			20201030
	Nov	2					Jetstreams From The Porch At Sunset			20201102
		13					Video in E Window at Sunrise (Calvary Baptist Church), Wall of Memories (for Sasha D.)			20201113
		15					From Porch, Sunny & Clear, Water Tower, Julia's Throne (for Sasha D.)			20201115
		21					Garage: Subaru new plates installed (The State is Not God)			20201121
		27					Photos and videos: Old house lot, shop building, Calvary Baptist Church (shared with Sasha D.) 204-202 W 3rd ST; Mailbox	IMG L0		20201127
	Dec	5					Church and Third Street View From Calvary Baptist (Shop, 202 W 3rd ST)	IMG		20201205
		20					Slo-Mo Video From Porch of Horses and Riders			20201220
2021	Jan	12					Network UPSs and Batteries in Rear Room			20210112
		14					Network UPSs AC Power Distribution T1 and T2 (Rear Room)			20210114
	Feb	27					A single photo of cartoon on Wall of Memories	IMG L0		20210227
	Mar	1					Shop building from basement of old house Burn Pile			20210301
	Apr	2					Tomatoes (East Window), Porch Sunset, Time Lapses	IMG		20210402
		6					Maytag washer Laundry Room (Sent to Yevgeniya)			20210406
		8					East Window: Tomatoes & Peppers (Sent to Yevgeniya)			20210408
		13					Tomatoes and Peppers, East Window			20210413
		15					Burn Pile, Time Lapse			20210415
		27					Tomatoes and Peppers, East Window, Porch Garden			20210427
	Jul	8					[L L0] Kitchen bench: First Harvest, Tomatoes; Suddenly Salad Pasta dinner			20210708
		16					From porch: Calvary Baptist, Marcus New Truck			20210716
		23					[L L0] Shop Home, Inside & Outside			20210723
		28					Garden, Tomatoes and Peppers			20210728
		30					Gravely PTO Switch Temporary Hack			20210730
	Aug	15					Garden, Tomatoes and Peppers			20210815
		24					20210824
	Sep	17					Me! (FaceBook to Sasha Olynik)	IMG L0		20210917
		30					Garden, Tomatoes and Peppers	IMG		20210930
	Oct	2					Garage-Shop Video, Viber, Pasha, T-105s, Schauer JAC2512 Received (Box Damage)			20211002
		5					Garden, Tomatoes and Peppers			20211005
		10					[L L0] QED100, Quick Easy Defroster 100W, Prototype			20211010
		17					Horses and Riders, From the Porch, Water Tower, Julia's Throne, Tom McConnell Residence			20211017
2022	Jan	5					[L L0] SureCall Cellphone Booster Power Supply Adapter Replaced			20220105
2022	Feb	9					20220205;09 MO, Rayville, Bathroom Cleaned by Jennifer McGaugh, Before and After, Time Lapse Videos			20220209
2022	Mar	8					20220304;08 MO, Rayville, Porch Garden Before Clearing, East Window Pepper Starts			20220308
		28					Porch Sunrise	IMG L0		20220328
2022	Apr	4					20220328;0404 MO, Rayville, East Window, Kitchen; Pepper & Tomato Starts	IMG		20220404
		6					Kitchen: Tie-Dyed T-Shirt; Dubious Claims Brewing Company (DCBC)			20220406
		12					Porch Chicken, Calvary Baptist Church, +Video, To Gem			20220412
		28					Porch Garden, Soil Turned			20220428
2022	May	16					Porch Garden, Tomatoes and Peppers Transplanted			20220516
2022	Jul	2					Porch, Sunrise, Garden			20220702
		3					Shop and Subaru at CO Trip Departure		Idle	20220703
		18					Returned from CO Trip (very early AM)		Active	20220718
2022	Aug	9					Garage, Subaru	IMG		20220809
		31					20220831
2022	Sep	5					West Propane Tank Leak			20220905
		7	We					Visit from Brandon and Dakota 13:30-14:10: They just showed up while I was on the porch with Caleb; They came to swap my DVS rooftop equipment from Ubiquiti to Mimosa; I told them "not now!"; Appointment for Th9/8 10:30	T48-3 WP11		20220907
		8	Th					DVS TurboNet rooftop equipment upgraded by Brandon and Dakota: Photos taken on the roof show deteriorated flashing/seal for the furnace vent and the antenna mast before they removed the Ubiquiti dish and installed the Mimosa dish / They gave me the mount and parabolic antenna from the Ubiquiti (but they took the feed horn as they can still use those at sites with Ubiquiti equipment) (antenna assembly stored on Gray Rubbermaid cart lower shelf) / Service was restored within minutes after they swapped the equipment (NetWorx CM printed and annotated for TM22 and L1 records) / T450s/FireFox/Speedtest.net (12:34) 93ms, 12.37Mbps down, 12.24Mbps up; Ping is a bit high, but these are great speeds / Photos after antenna swap; There's no Mimosa labeling or model number on the new antenna / [General discussion with Brandon and Dakota (see T48-3): TurboNet Orders Pending List (see TM22 and sites linked from L17); I tried to get them interested in power systems maintenance)]	IMG SSC EML L1 T48-3 TM22 L17		20220908
				Re aimed directional cellphone booster antenna (SureCall): For months now I'm only getting 1-2 bars (out of 4) with iPhone 12 feet from the inside antenna, and many dropped/failed phone calls / The SureCall booster LTE bands are overloaded, flashing red "too strong, auto shut-down" or solid red (OFF) / Tried rotating the directional antenna about 20⁰ more to the East but no improvement / I need to do some research and go on the roof when it's cool or cloudy	IMG		20220908
		9	Fr	~	05:45			SureCall: LTE bands solid red (OFF); / Turned booster off and observed iPhone signal strengths inside & outside building (4 bars total): / Main computer station 1 / NE, EN, ES, SE, WS, WN windows 2 / NW window 1 / Outside on W porch 2 / Outside on S porch 3, but in the SE corner of the porch 4/4 bars / Evidently our strongest signal is coming from the SE / Research: CellMapper.net site is very good information / Map focused on Rayville, Provider AT&T Mobility - 310410, Network 4G - LTE, All Bands / There are four towers surrounding Rayville within 4-6 miles, directions NE, ESE, S and W; SSC of map / Conclusions: The only way I can see to reduce my incoming signal strength with the directional antenna is to aim it NNW / There are no towers out that way for 12 miles or more, and the nearby Verizon tower is SSE / When I was using the omni I had problems most likely from the Verizon signals overloading the input preamp and washing out the weaker AT&T signals I needed (see 1/21/16 pencil notes in warranty file for call to SureCall tech support) / Next I will rotate the directional antenna to NNW (as it is the easiest solution now if it works)	SSC		20220909
				~	09:20			SureCall: Rotated directional antenna to point NNW; Tightened mounting bolts; Zip tie on mast/wires; Photos / LTE-A is no longer too strong (no red flashing LED) but LTE-V overloads immediately (solid red) / iPhone 2/4 bars at computer station (improved slightly, but not LTE); On porch it's 3/4 (even 4/4 seen earlier) and LTE	IMG		20220909
				Examined and shot photos of deteriorating seal on AC electrical mast; It's probably not leaking yet, but the flashing seal for the furnace vent must be leaking into the attic and needs to be covered			20220909
				~	09:50			SureCall: Turned up dB gain for LTE-A from almost off (<39) to 49 / No improvement, iPhone is 1-2/4 bars and no LTE / Called SureCall 510-770-0469 and LMVM with technical support ...			20220909
				~	10:10			SureCall: CELLULAR band is sometimes solid yellow (normal operation, AGC operational); Turned up gain from 40dB to 50dB; No noticeable improvement, iPhone 2/4 bars and no LTE			20220909
				~	10:40			SureCall: iPhone rebooted in ES window and it shows LTE for about 30s, then no LTE; It does this with or without SureCall booster on, but I think it's better w/o booster; LTE comes and goes, so it's right on the edge there in the ES window			20220909
				SureCall: Decided not to wait for information from SureCall Tech Support, and went looking for SureCall 5/10/20dB Attenuators / I found them and some sources, but in doing so I found a great review on amazon.com for the SureCall 20dB Attenuator: / "Only attenuate what is necessary to keep your amplifier from going into overload and shutting down. Again, if your amplifier is going into shutdown and you have easy access to your outside antenna, you should try moving and/or de-tuning antenna first. I recommend using this or any attenuator only as a last resort." / This review made me realize that before I decide what and where to order anything I should talk to the SureCall tech and try the Omni again: / I've tried some detuning (by changing aim of Yagi) but I'm still getting gain from the NNW direction, and those are the bands I need / The Omni will reduce the signal strength (but also increase Verizon tower signal strength) / It may well work now that the AT&T tower situation has improved (since 2016) and we have stronger LTE band signals / And if it does work, I don't need to buy an attenuator			20220909
				~	17:22	~	17:55	SureCall: Call from Kevin at SureCall (from 510-344-8644, Fremont CA, 33m); Notes prepared and updated for call: / Metal building, antenna mast above peak of roof, inside antenna centrally located; My main provider is Consumer Cellular (AT&T network) / iPhone 11 sees great signal strength outside metal building (LTE, 4/4 bars) but w/o the booster it sees only 1/4 bars inside the building, 2/4 if in a window / There is a hugely high and powerful Verizon tower less than 1 mile away (SSE); I am surrounded by good LTE towers but they are all 4-6 miles away / When I first installed the SureCall Fusion5 in November 2015 I was not getting good results, and tech support recommend switching to a Yagi instead of the Omni / (because they said perhaps the Verizon bands were over-powering the AT&T bands I needed) / I installed the directional antenna in February 2016 and aimed it off to an AT&T tower about 6 miles to the NE; This worked OK until recently, when evidently AT&T upgraded their towers/antennas / My iPhone was purchased several years ago and can use the LTE bands; Lately I've been getting only 1-2/4 bars and no LTE on the iPhone inside the metal building: Marginal to poor performance and many dropped calls / Today I rotated the directional antenna to point directly away from the Verizon tower nearby, it is now aimed to a region where there are no cell towers (or they are more than 15 miles away) / This improved the LTE-A band which was overloading (flashing or solid red) - now no LED; But the LTE-V band is solid red; iPhone sees 2/4 bars and no LTE / Should I go back to the Omni? I'm going to try this next (Kevin agreed with me); I'm still concerned about that strong close Verizon tower, but we might be OK with Omni and/or attenuator now that AT&T signals are stronger / Attenuator? 5/10/20dB? Attenuator is installed inside at the Fusion5, directly at the outside antenna input / Measure RSRP (Reference Signal Received Power) for AT&T LTE signal at mast using iPhone Apple Field Test Mode: *3001#12345#* / RSRP ~ -80dB to -85dB is good for Fusion5 amplifier; RSRP -60 to -70dB is VERY STRONG (too strong); Buy attenuator based on RSRP seen with iPhone, smaller dB is better if it works / Results for iPhone in ESE window (Kevin yet connected): RSRP -107 "weak but OK"; iPhone seeing 2/4 bars; Band 66 / Can buy multiple dBs and return the ones I don't use (I think Amazon.com has 30 day free returns, no return shipping)			20220909
		23					Porch Garden; Tomatoes and Peppers	IMG		20220923
2022	Oct	25					Porch Sunset Video (To Ukraine Friends)			20221025
	Dec	3					Clausing Mill Dial Indicator Setup, WP12-13			20221203

## L0
Locations: L0	A					Bench: 202 W 3rd ST, Rayville, being worked on (various devices)

Date/Time CST/CDT					Description	Other Sources	Status
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active
2000	Aug	1					L L0			20000801
2001	Oct	16					Active	20011016
2002	Jan	30					EML		20020130
2008	Oct	15					Main shop	IMG		20081015
2009	Jan					Benches used mostly for computer repair since 2002, with the exception of some work for Hallard Station and Missouri Woods; Computer repair was "on again / off again" depending on travel / In January 2009 I finally settled the disagreements with Tom and Art and restarted serious computer repair work, and the ESJCC contract began			20090115
2011	Aug					ESJCC contract ended			20110815
2013	Feb	25					Last recorded computer repair job: I was preparing to go to Ukraine			20130225
	Mar	13					L L0		Idle	20130313
2014	Dec	25					20141225
2015	Jan	29					IMG	Active	20150129
	Mar	28					I really start to get moving again: JAK2 being rebuilt			20150328
	May	16					Stacey Blackshear using the "kitchen" bench area for extracurricular activities			20150516
		31					Preparation and testing of Genasun and convertor for one of the towers			20150531
	Jun	21					DVD mounting rail, for Mark Hall			20150621
	Jul	3					Monitors for Mark Hall			20150703
	Aug	1					Fluke DVM repair and calibration			20150801
		13					T1 and T2 Bench circuits in main shop wired up to Liebert GXT2 UPSs	A5 A6		20150813
		28					Mark Hall and Juliya Dudar (SAPS parts in background on bench)	IMG MA2		20150828
	Dec	25					Christmas Dinner on the bench	IMG		20151225
2016	Jan	8					Bryce Jones, Ship's Cook & Machinist Mate: Photos 1/8/16 to 2/2/16 of cooking on "kitchen" benches and sorting tools on garage bench			20160108
		20					Photo of D1C T1/T2 double-duplex outlet: Part of Liebert UPS bench circuit system			20160120
	Mar	31					Machine tools being sorted on the garage bench			20160331
	Jun	6					Bench calibration of Wattmon_8 using BK_1			20160606
	Sep	5					Kitchen sink bench			20160905
	Nov	1					Tools Loaned to Butch			20161101
2017	Apr	19					Gravely fuel pump			20170419
		25					CraigsList ad: New End Mills for Sale; Consolidated End Mills for Sale			20170425
		28					CraigsList ad: Weldon End Mill For Sale			20170428
		29					CraigsList ad: Mitutoyo Caliper For Sale			20170429
	May	15					CraigsList ad: Jabra Freeway For Sale; Roughing Mills For Sale			20170515
	Jun	16					CraigsList ad: Drill Bits For Sale, Precision TDC .625			20170616
		19					CraigsList ad: Drill Bits For Sale, (118) Tap Sizes			20170619
		27					CraigsList ad: Horizon Exercycle			20170627
	Jul	12					CraigsList ad: Hancock Watch			20170712
		20					Mean Well Power Supply Connector Problem			20170720
	Aug	3					WISPOWER #1 Testing	IMG WRD WP1		20170803
		7					20170807
	Sep	5					WISPer #1 Ready to Install at RCWT			20170905
	Oct	31					Preparing to go camping (which I later chose to abort): Subaru in garage and stuff to load on the garage bench	IMG		20171031
2018	Feb	16					Nikon MB-D10 + For Sale			20180216
		25					WISPOWER #2 Testing	IMG WRD		20180225
	Mar	5					W100 Testing (WP2, Delta 150W, Genasun no cover, fan taped to bench, BK, W9, B1)			20180305
		11					FedEx lost box (WP2, 1st Delta 200W)			20180311
		13					W100 Testing (Trace, B1, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK)			20180313
		15					W100 Testing (Trace, B1, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)			20180315
		20					W100 Testing, Calibration of C252 (WP2, Delta 200W, Genasun mounted under fan, B1, BK, Trace being used as CW load)			20180320
	Apr	2		~	15:15			Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	IMG WRD EML		20180402
	May	8					WISPer#2 product photos (L0, W100_1, DE_2, Genasun_3)	IMG		20180508
		12					Miscellaneous photos (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC)			20180512
	Jul	15					1995 Temperature Monitor by Jeffrey A. Klute: Resurrected, serviced, in service			20180715
	Sep	29					Main shop video, 360 degree pan to the music "Here I am Baby" (while working on the SAPS)			20180929
	Oct	7					Old Computer Stuff (main shop E shelves)			20181007
2019	Feb	1					Breakfast on the kitchen bench: Eggs, potatoes and sausage	IMG L		20190201
	Mar	19					Subaru Bumper Stickers THE STATE IS NOT GOD, in garage, SAPS	IMG MA2		20190319
		30					Network UPS Setup on Rubbermaid Cart, CP_1, B4-7, Fluke	IMG		20190330
	Apr	9					Security Camera, Main Shop Test, Dancing to the music of "Don't Worry Be Happy"			20190409
		12					Russian Tomato Plants have germinated, E shop window			20190412
	May	16					Tomato and Pepper plants growing in E window			20190516
		19					Fluke, BK & UPS Battery Charging (BK_1, A30/TL3_6)			20190519
	Jun	1					L L0			20190601
		4					NiCd Charging, BK_1, Wattmon_9			20190604
		18					(2) W100	IMG WP4 WP5		20190618
		28					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG WRD		20190628
	Jul	8					W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG		20190708
		11					APC_1 BR500 (A32) Circuit Board			20190711
		14					W100 DR Test Setup, APC_1, Filter Caps			20190714
		17					20190717
	Aug	4					W100 DR Test Setup, CC with Ballast			20190804
		13					L L0			20190813
		29					On the bench: Tomato Harvest (39), 1.5# Tomato			20190829
	Dec	14					On the bench: Class C Hitch Loaned to a Stranger			20191214
2020	Feb	7					On the rubbermaid cart at the bench: Power Strip Repair for Keith Jones of TurboNet			20200207
	Apr	13					Kitchen sink: Interesting Faucet Drip, Videos			20200413
	Jun	23					DR Test Setup photos; Main shop video with music playing and computer speaking "I love you Jeffrey, and I don't want to be a nag, but have you fixed the problem?" (old sync system error)	IMG L		20200623
		30					Art True reminder note (iPhone iCloud Testing)	IMG		20200630
	Jul	1					Lavender Oil			20200701
	Sep	15					Large tomato on bench: Tomato and Pepper Harvests			20200915
		17					Large tomato on cutting board on kitchen bench: Tomato and Pepper Harvests			20200917
	Oct	1					Peppers on kitchen bench: Tomato and Pepper Harvests			20201001
		2					Tomatoes on kitchen bench: Tomato and Pepper Harvests			20201002
		25					On cutting board on kitchen bench: Taco Salad			20201025
	Nov	10					On kitchen bench: Stairway to Heaven album (for Sasha D.'s father)			20201110
		11					On kitchen bench: French Toast (for Sasha D.)			20201111
		15					On kitchen bench: Favorite T-shirt (for Sasha D.)			20201115
		19					On kitchen bench: Dinner, Suddenly Salad (for Sasha D.)			20201119
		26					Blurry photo: JAK2 Sound of Music Bench			20201126
		27					The Rat Traps Swing Band	IMG L		20201127
2021	Jan	7					Kitchen bench: Ukrainian Borsch	IMG		20210107
		8					Bench Testing for Turbonet and Richmond High School (RHS) UPS Battery Contract			20210108
		15					Photos and Videos: TurboNet Richmond High School (RHS) Battery Cable Fabrication (Butt Splicing)			20210115
		16					Photos and Videos: RHS Load Testing "Do You Remember Dancing in September?"			20210116
		18					TurboNet RHS Bench Testing, UPS Damage (MOV)			20210118
		25					Russian Standard at Main Shop Computer Station Sent to Pasha via Viber			20210125
	Feb	9					Photos and Videos 2/2/21 to 2/9/21: RHS Boost Charger Assembly and Completion +Video; Clausing and Main Bench			20210209
		27					Note to Marcus & Sharon About Pavel & Varta	IMG L		20210227
	Mar	1					Bachelor Dinner (for Lisha)			20210301
	Apr	21					Cooking Burritos, Yevgeniya	IMG		20210421
	Jun	2					Photos on Bench 6/1 and 6/2/21: Lord of the Rings Book, For Yevgeniya			20210602
		21					First Harvest, Peppers			20210621
	Jul	8					L L0			20210708
		20					Kitchen bench: Dinner, Pavel, Ludmila; Bug Zapper			20210720
		23					L L0			20210723
	Aug	1					Garden, Tomatoes and Peppers			20210801
		17					20210817
		30					20210830
	Sep	6					20210906
				Oil Mousetrap			20210906
		7					Nikon Micro Nikkor 105mm			20210907
		13					Garden, Tomatoes and Peppers			20210913
		17					IMG L		20210917
	Oct	9					IMG		20211009
		10					L L0			20211010
		24					(Pavel and Gem Sharing); Bench Videos (Schauer #1, APC Load, Extech, Engel, QED100)			20211024
		27					20211027
		28					TurboNet Power Cable, Wrong Type			20211028
	Nov	2					(Pavel and Gem Sharing); Bench Videos (Schauer #1, APC Load, Extech, Engel, QED100)			20211102
		9					20211109
		13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup: TurboNet, General Bench Testing Photos; Schauer #1, Traco #1, Dinico #1, Last Use of APC Load Setup (ONWT)			20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark); (Pavel and Gem Sharing); Bench Videos (Schauer #1, APC Load, Extech, Engel, QED100)			20211114
		15					TurboNet Power Cable, Belden Assembly (ONWT)			20211115
		18					20211102;13^16;18 MO, Rayville, Bench; TurboNet Schauer Charger #1, Adjustments and Labels (ONWT)			20211118
		22					20211113;22 MO, Rayville, Bench; TurboNet Dinico #1 (ONWT)			20211122
	Dec	4					ITECH Electronic Load Initial Testing			20211204
		23					20211221^23 MO, Rayville, Bench; TurboNet, W50 Testing (WISPer Prototype #1 from RCWT), Blowing The Fuse Video (Engel)			20211223
		29					20211212^14;29 MO, Rayville, Bench; TurboNet, Engel Battery Enclosure Assembly, T-Sensor Rack, Dinico #2 (W50 & SLA from RCWT)			20211229
2022	Jan	5					L L0			20220105
	Feb	4					Sharp Tools 27 Grams			20220204
	Mar	4					20220304 0812 IMG_2398.JPG accidental photo of bench at main computer station, bluetooth headset			20220304
		28					20220328;0404 MO, Rayville, East Window, Kitchen; Pepper & Tomato Starts	IMG L		20220328
	Apr	7					Kitchen; Pepper & Tomato Starts	IMG		20220407
		14					Preparations on the bench: TurboNet LWT 48v Install, BK, ITECH			20220414
		15					On the bench: 20220415 1014 To Gem 1023 Neil Wilkerson DCBC Refrigerator Magnets; IMG_2543.JPG			20220415
	May	4					On the bench: 20220504 2021 To Gem, Pizza I Made 'Lamb, onion, black olives, mushrooms, cheddar cheese. Очень вкусно!'; 1651713553215269; viber_image_2022-05-04_20-21-07-645.jpg			20220504
		26					TurboNet Bench Testing; Engel, Dinico, ITECH; Schauer Chargers, Dual Supply Proof of Principle			20220526
	Jun	7					Miscellaneous (accidental shot of kitchen and middle door)			20220607
		11					TurboNet Bench Testing / Engel, Dinico, ITECH; Schauer Chargers, Dual Supply Proof of Principle			20220611
		16					20220616
		18					Mulberries			20220618
	Jul	22					Power Cable Assembly for CFS			20220722
		23					Engel Circulating Fans Cover Switch			20220723
	Aug	10					Power Cable Switches (WP11-14), Wiegmann Backplate Assembly (LSWT)			20220810
		11					20220811
		12					20220812
		15					Tomatoes, Peppers			20220815
		17					Wiegmann Backplate Assembly (LSWT); Dinico Assemblies (Z19-20); BC9, V11, S13			20220817
		18					20220818
		20					20220820
	Sep	8					TurboNet PowerBox Pro (PBP); New Ukraine T-Shirt			20220908
		17					TurboNet; Bench Setup, Dual Supply, Wiegmann Backplate (LSWT), Battery Post Caps, W150_1 Cardboard Template #1; BC9 S13 S17 V11 B58			20220917
		18					20220918
		19					20220919
		20					20220920
		29					W150_1 Fabrication, Assembly, Testing (Hard Day's Night video), Product Shots			20220929
		30					20220930
	Oct	3					20221003
		5					20221005
		8					20221008
		10					Wiegmann and Power Cable Assemblies for LSWT			20221010
		11					20221011
		29					$2000 Precision Beer Cooler, Video			20221029
	Dec	6					Meter Samples WP14-15			20221206
		8					Shrink Tubing Cutting Block			20221208
2023	Jan	10					Trim R Assemblies			20230110
		31					W150_3 Completion (WP13)			20230131

## L1
Locations: L1	A					RW: Rayville Water Tower					Panel 1	Panel 2	Panel 3	Controller	Controller	Controller	Battery 1	Battery 2	Battery 3	Battery 4	Converter	Load Device	Wattmon	Module	WebRelay	OneWire	WISPer

Date/Time CST/CDT					Description	Other Sources	Status	Solar Panel Total Watts	Tilt Angle	Charge Controller Maximum Watts	Battery AH	Battery C-Rating	Charge Efficiency	Peukert Constant	7 Day Average Load Watts
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	-	-	-	105	C/20	-	-	-	-	-	-	-	-	-	B54	-	-	-	-	Netonix WS-12-250-DC	-	-	-	-	WP3
2005	Nov	3					White sheet notes on initial contact with TurboNet and Mark Webb	TSP WS					20051103
2015	Mar	13					White sheet notes on contact with TurboNet and Mark Webb					20150313
		17					20150317
		23					20150323
		24					White sheet notes on contact with TurboNet and Mark Webb: Mark and Keith came to shop					20150324
2015	Apr	8					Call to Mark, LMVM "Status?": Still waiting AmerenUE; Suggested solar, didn't seem interested, but could be / Draft of TODO for solar system pitch/installation	TSP	Design					20150408
		10					Water tower as seen from home and through the fence	IMG					20150410
		22					Ordered solar panel pole mount from Northern Arizona Wind & Sun	TSP					20150422
		29					Water tower as seen from the point on the roof where DVS TurboNet link will be located	IMG					20150429
		30					Initial installation (without Wattmon); Photos of initial installation with Mark Webb and Keith Jones	IMG AED	Active	100	45	140					12.8	P1			C1			B1				V1	Ubiquiti TS-5-POE					20150430
2015	May	27					Email to Mark Webb "Photo", 20150430 Mark and Keith next to initial installation	EML					20150527
2015	Jul	1					Email from Keith Jones "static ip" (for Data Vision Services): / 12.133.21.140, 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML CPSN					20150701
		2					Email from Keith Jones "ip for solar": 12.133.21.146, 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML					20150702
		6					Converter #2 (spare) installed at RW / [records are incomplete, but sometime before July 9th 2015, when unit #1 was at the shop and was repaired]					V2					20150706
				[Wattmon_1] and [C252_1] installed; Photos; Adjusted capacity of battery from 105 to 70 AH	TSP AED IMG					70.00	C/40	100%	1.00	14.8				C2					W1	M1				20150706
		10					Copied key from Mark/Keith from PWSD for gate in fence surrounding the water tower	TSP					20150710
		11					Probable date of onsite visits to replace Genasun (not certain)					C1					20150711
		12					Observations: Accessible by web interface since firmware downgraded / Intermittently rebooting itself, 4 times in the past 32 hours / Graphs are still a mess with missing holes and whole days gone / Changed the log interval to 5 minutes, which will mean less glitches in case of a reboot	AED					20150712
		16					Approximate date when I began to study Peukert's Law and so by this date I believe I adjusted the Battery and Charge Settings for [Wattmon_1] to use a calculated C/40 capacity and a Peukert Constant of 1.17 for the Trojan 27TMX battery					116.26		90%	1.17					20150716
		17	Fr					Approximate date of installation of [P_2] at RW; Trojan 27TMX replaced with (2) T-105s / Records are incomplete, but I probably used calculated values for C/40 AH Capacity and Peukert Constant			200			235.45			1.07			P2					B2	B3					20150717
		19					[Wattmon_1] replaced with [Wattmon_2] but using [SD Card #1] so Battery and Charge Settings continue as set					W2					20150719
		21					Changed Battery Charge parameters met time from 5 to 30 minutes					20150721
		22					Changed Battery Charge parameters met time from 30 to 60 minutes; Changed Return Amps to 1% / Gaps in data collection (short, @ 09:57 & 12:53)					20150722
		23		~	09:12	~	09:32	Data gap					20150723
		27					[Wattmon_2] removed for bench work (RW without any Wattmon)					20150727
2015	Sep	3					Onsite with Juliya	IMG					20150903
		16					Onsite with Juliya (Sasha's iPhone)					20150916
				[L1-2] SMS from Keith Jones --> Email from phone "IP Addresses from Keith Jones": / 12.133.21.141 (for RN Wattmon), 12.133.21.146 (already received for RW Wattmon)	SMS EML					20150916
		19					[Wattmon_2] reinstalled; [C252_1] replaced with [C252_2]	AED					W2	M2				20150919
				[L1-2] Emails to and from Keith Jones "Re: IP Addresses": / This is what I have now: 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon) / Keith responds with "You can use .147 if you need another one"	EML CPSN					20150919
		20					I climbed to the top of the water tower while Keith and Juliya watch from the bottom	IMG AED					20150920
		26					[L1-2] Increased Charge Efficiency from 90 to 95%; Increased Charge parameters met time from 120 to 180 minutes	AED					95%					20150926
2015	Oct	9					Sasha onsite twice to reset W2					20151009
		15					[L1-2] Increased “Charge parameters met time” from 180 to 240 minutes / (Rayville N has been resetting itself almost daily, about 1-2 hours before fully charged)					20151015
				~	12:40	~	12:40	Data logging stopped and unit inaccessible for ~24 hours after that …; Sasha onsite to reset					20151015
		17					Inaccessible; To/From Akash (who wants me to try http logging)	EML					20151017
		20		~	13:40		18:20	Logging stopped; Resumed by itself	AED					20151020
		24					[L1-2] Attempted changing "Charge parameters met time" from 240 to 300, but "error saving changes" / (I was still working on the Battery SoC algorithm to adjust the parameters to what was needed to reflect a more accurate Battery SoC %)					20151024
		25					[L1-2] Wattmon Online Portal initiated and configured by Akash	AED EML					20151025
2015	Nov	8					Locked up for three days …	AED					20151108
		11					I went to the tower and manually reset the Wattmon					20151111
		14					[L1-2] Charge efficiency 95% --> 90%					90%					20151114
		15					[L1-2] Return Amps set to “Not Used” & Battery Full Voltage set to 16 volts					20151115
		27					Batteries charged with Subaru from ~14:45 to ~19:00					20151127
				Later, Inaccessible, TelNet (Putty) used to reconnect					20151127
		30	Mo					Swapped T-105s					B4	B5					20151130
2015	Dec	7					Inaccessible, TelNet (Putty) won’t connect; Butch to the tower to reset; No portal gap, but a short gap on SD card					20151207
		10					Inaccessible, TelNet (Putty) would not connect; Butch onsite to reset; Logging gap from ~14:50 to 17:50 (3 hours) / Battery SoC adjusted to compensate					20151210
		11					Inaccessible, TelNet (Putty) won’t connect; Manual reset @ tower / Portal logging gap from ~12:35 to ~20:55 (8hrs 20mins); Battery SoC adjusted to compensate					20151211
		17	Th					Swapped T-105s					B2	B3					20151217
		18					Inaccessible, TelNet reboot OK, curious symptom (0.0 V and Live Energy not working) / Reboot from web interface and now OK					20151218
		19					Inaccessible, TelNet reboot OK					20151219
		20					Inaccessible, TelNet won’t connect; Logging stopped yesterday 12/19/15 @~22:18 / Butch & Bryce manually reset @ tower; Battery SoC adjusted to compensate @ 16:00					20151220
		26	Sa	~	23:25	~	00:35	Battery SoC 0%; Logging stopped …; Battery SoC corrected to compensate					20151226
				Swapped T-105s					B4	B5					20151226
		30					Http interface non-responsive, TelNet Reboot					20151230
2016	Jan	1		~	11:20	~	12:55	Logging gap; Http inaccessible; Telnet won't reboot … / Butch to tower to manually reset; Battery SoC corrected to compensate					20160101
		2					Inaccessible, TelNet reboot OK					20160102
		3					[L1-2] Charge efficiency 90% --> 85%					85%					20160103
		5					Inaccessible, TelNet reboot OK					20160105
		18		~	22:20			Akash had problems accessing http	EML AED					20160118
		20					Changed sun angle of panels to 30 deg above horizon	AED			60					20160120
		27					Sunset at the shop: / Looking SW towards the Rayville PWSD Water Tower and the burnt house from W side porch of the shop	IMG					20160127
2016	Feb	2					Inaccessible, TelNet reboot OK	AED					20160202
		4		~	15:20		08:18	Logging gap; Http inaccessible; Telnet won't reboot … / Manually reset (Butch, me and the water company guy at the tower)					20160204
		5			10:20			Corrected Battery SoC					20160205
				14:22			Inaccessible, TelNet reboot OK					20160205
		12					Sunset from the porch showing Subaru, PWSD #2 tower and jet trails in the sky	IMG					20160212
		23					[L1-2] Email from Keith Jones "Ip's for Jeff Klute": 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay), both are 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML					20160223
		24					[L1-2] Email to Keith Jones "Re: Ip's for Jeff Klute" which summarizes static IPs: 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay)	EML CPSN					20160224
		26		~	12:25			Logging gap starts; Inaccessible, TelNet reboot NOT OK (Spider Bite, can't get to tower to reset now) …	AED					20160226
2016	Mar	16					R_2 installed at RW; Correction to battery SoC postponed (logging stopped for 19 days, need to watch and see) / Set [UTC-5] Eastern Standard Time (because of DST change)	AED IMG					15.7					R2			20160316
		17					Corrected Battery SoC 93% --> 99%	AED					20160317
		20					[L1-2] Battery Capacity rounded down 235.449996 --> 235 AH					235.00					20160320
2016	Apr	9					Logging gap corrected: 50 minutes, battery SoC 96% --> 95.7% (minor)					20160409
				[L1-2] Modified logging and portal reporting intervals: / To see changes on the portal before they disappear off the left side of the 5 min "Live View"					20160409
		14					Onsite with Mark and Keith; Photos of Mimosa B5-Lite box and power supply (this is when I found out they were going to upgrade the equipment at RW)	IMG TSP					20160414
		16					Battery SoC went to Zero - Again; 04:08: 96.9% --> 0%; System Log: No entry near this time (except “Exec SOC-070” and “Exec SOC-060”); Battery voltage logging and Solar/Load logging did not stop; Correction was quickly estimated by guestimate: 09:04: Set Current Battery AH = 221 (94%)	AED					20160416
		19					Increased power needs: Ubiquiti switch r/w Netonix switch; Converter V2 removed	AED					25.1					-	Netonix WS-12-250-DC					20160419
		22	Fr					Swapped T-105s	AED					B6	B7					20160422
		29	Fr					AED					B4	B5					20160429
2016	May	4		~	09:40		11:46	Battery SoC 49.04% --> 0% …; Battery SoC corrected to 53%	AED					20160504
		6	Fr					Swapped T-105s	AED					B6	B7					20160506
		13	Fr					AED					B4	B5					20160513
		14			07:38		07:55	Battery SoC 88.1% --> 0% …; Battery SoC corrected to 88.1%	AED					20160514
		23	Mo					Swapped T-105s	AED					B6	B7					20160523
2016	Jun	1	We					Swapped T-105s; Wattmon_2 r/w Wattmon_6; C252_2 r/w C252_1 / Portal logging gap starts due to MAC# change …	AED					B4	B5					W6	M1				20160601
				20160601 TurboNet MO Quote - RW Solar Upgrade.pdf emailed to TurboNet	DBT EML TSP					20160601
		2					Akash changed MAC# and portal logging resumes	AED					20160602
		9					Email to Mark Webb "Re: Upgrade for Rayville Water Tower (RW)": attached 6/1/16 quote again / Discussed battery swapping and need to resolve situation since they increased the power requirements	DBT EML					20160609
		13	Mo		14:05			Trojan 27TMX installed at RW	AED					B1					20160613
				Email from phone "16:55 SMS from Mark Webb": "We're not going to put up more solar. It's too expensive. We can't afford it. We're going to have electric brought in. We'll figure it out next week. Sorry. Been busy. I'm in Florida til Monday."	SMS EML TSP					20160613
		16	Th	~	10:40			Trojan 27TMX replaced with (4) T-105s, 2 of them on the ground	AED					498.00			1.17					B4	B5	B6	B7					20160616
				>	11:10			Wattmon_6 r/w Wattmon_8; Portal logging gap begins …	AED EML					W8					20160616
				>	12:30			Installed 3rd solar panel: Flexible mono-crystalline; Photos (inside box, outside, site)	AED IMG		300					P3					20160616
		17				~	00:10	Akash changed MAC# and portal logging resumes	EML					20160617
		20					Email to Mark Webb "Re: Upgrade for Rayville Water Tower (RW)": 20160616 Rayville Water Tower Solar.JPG / 20160620 RW Battery Status Graph June.jpg; Also see 20160620 RW May Battery Status.jpg	EML IMG TSP					20160620
		27	Mo	~	06:15			It is obvious from studying the graphs since the 16th that the SoC algorithm needs adjustment / RW is reaching "100%" hours before it has had time to float into a 5% or less Net Charge Watts to AH Capacity / This is due to the recent change to a higher Peukert Constant. Changed Battery Charge Efficiency to 80%.	AED					80%					20160627
2016	Jul	1	Fr	~	18:30			Changed Battery Charge Efficiency to 75%					75%					20160701
		5					Details on Re-Analysis of 7 Day Average Total Load Watts: I adjusted the historical data due to now known calibration errors; [NOTE ADDED 8/12/16: I probably didn't notice at the time that the firmware updates beginning on 6/25/16 had clobbered the 6/6/16 A1 Calibrations in NVRAM. Therefore, all of the data after 6/25/16 and the adjustments to these figures based upon the 7/5/16 analysis is not to be relied upon.]					20160705
				[L1-2] Completed reorganization of spreadsheets and this file; I started this work on 6/20/16, and worked on it almost daily since then; Location Specific Information now current					20160705
		19	Tu		08:12			[L1-2] Modified Peukert Constant, Battery AH Capacity and Charge Efficiency: Details on the analysis and decision / RN set to use the same parameters except for 1/2 the Battery AH capacity, so an analysis of SoC algorithm should be possible in the next few days or weeks	AED					493.00		80%	1.15					20160719
				08:52			Corrected Current Battery AH to reflect change in capacity 493/498*480.963684=476.135 (set 476)					20160719
				~	12:05		12:10	Wattmon reaches "100%" but still in bulk (13.6v, Genasun power limit, looking to try to reach absorption voltage of ~14.3v) …; Adjusted Battery SoC downward ~1% (493-->488AH)					20160719
				~	13:40		13:48	Wattmon reaches "100%" but still in bulk (13.0v) …; Adjusted Battery SoC downward ~1% (493-->488AH)					20160719
				16:23		16:27	Wattmon reaches "100%" but still in bulk (13.4v) …; Adjusted Battery SoC downward ~2% (493-->483AH)					20160719
		20	We	~	08:15			[L1-2] Details on "RW & RN: Comparisons of Battery % SoC Drop for the past two nights"					20160720
				09:36			[L1-2] Modified battery parameters to use C/20 instead of C/40 and adjusted Battery SoC to compensate for the change					450.00	C/20					20160720
				14:28		14:33	Wattmon says "99.5%" but since Genasun is still in bulk it is obvious that Wattmon will reach "100%" early … / Adjusted Battery SoC downward ~2% (447.8-->439AH)					20160720
		21	Th	~	08:30			[L1-2] Details on "Battery SoC Drops measured to compare with the previous night"					20160721
				~	11:00			[L1-2] Latitude and Longitude recorded on Portal					20160721
				~	12:02		12:07	Wattmon says "99.6%" but Genasun still in bulk and it is obvious that Wattmon will reach "100%" early … / Adjusted Battery SoC downward ~4% (448.4-->430AH)	AED					20160721
				12:28			[L1-2] Lowered Peukert Constant 1.15 --> 1.13					1.13					20160721
		22	Fr		07:32		07:42	NVRAM Actions System Completed: Roles & Actions modified (SoC and A1) / Graphing glitches caused by my testing by modifying Current Battery AH (10 minutes)					20160722
				~	14:30			[L1-2] Details on "Battery SoC Drops measured to compare with the previous night"					20160722
				~	14:48		14:54	Wattmon says "99.1%" but Genasun still in bulk and it is obvious that Wattmon will reach "100%" early … / Adjusted Battery SoC downward ~4.1% (446.1-->428AH)					20160722
				15:14			[L1-2] Lowered Peukert Constant 1.13 --> 1.11					1.11					20160722
		24	Su	~	12:40		14:33	Observations: Short peak of 14.2 volts …; Wattmon hits "100%" but still in bulk; EARLY					20160724
				~	15:10	~	15:25	Observations: Absorption period on/off for about 15 mins (14.3v); This is the highest voltage we've seen since the batteries were installed on June 16th (solar conditions have been positive during the past week or so)					20160724
				16:07		16:23	Observations: SoC<100% …; SOC=100%					20160724
				17:25			Observations: SOC<100%; Wattmon spent a total of 2 Hrs and 56 Mins pegged at 100%, which did well to correct the overall trend of hitting early					20160724
				18:30			Decreased Charge Efficiency 80 --> 75%					75%					20160724
		25	Mo		16:53		16:57	Observations: Highest voltage seen today 13.8v for no more than 15 mins; Currently 99.1% @ 13.6v variable / Genasun has not triggered Absorption today and won't; It is obvious that we are at least a couple of percent high … / Adjusted Battery SoC downward 2.0% (446.107635 --> 437 AH)					20160725
		26	Tu			<	17:07	Observations: Although we saw the highest voltages today since the batteries were installed on 6/16 (14.5v for about 5 mins), the Genasun did not ever switch from Bulk to Absorption (or Equalize); Current SoC 99.68% / It is obvious that we are still a couple of % high, and that the Charge Efficiency needs to be reduced even more / See AED for a bunch of realizations as to WHY? (Akash Peukert Constant Algorithm is Flawed)	AED					20160726
				17:18		17:27	Adjusted Battery SoC downward 2.0% (448.856964-->440 AH) …; Decreased Charge Efficiency 75-->70%					70%					20160726
		27	We	~	12:25	~	12:40	Observations: Period of "absorption like" voltage (14.5v) but I'm fairly certain that the Genasun did not switch out of Bulk (this period was right up against the Genasun power limit of 170W to 160W, which caused a "declining" power curve that looks like Genasun Absorption, but isn't)					20160727
				~	17:15			Observations: Battery SoC 98.63% and we've lost the sun for the night; No SoC% adjustment or change in Charge Efficiency seems called for, as we still haven't seen Absorption or Float for any significant amount of time					20160727
		28	Th		15:00			Increased Peukert Constant 1.11-->1.17; Decrease Charge Efficiency to minimum allowed by Wattmon 70-->60%					60%	1.17					20160728
				Subsequent color coding: / 100% but not 3%; Neither 3% or 100% OR 100% and 3%; 3% but not 100% (should/did correct SoC at least +x%)					20160728
		29	Fr	~	17:40			Observations: Battery SoC peaked at 99.74%; Earlier between about 15:15 to 15:50 we saw some spikes at 14.7v (highest voltage seen since June 16th), but Genasun was probably not regulating and still in Bulk / It seems obvious that we are still high on % charge and that the Charge Efficiency s/b reduced even more					20160729
		30	Sa		03:43		03:45	Adjusted %SoC downward <1% (437.048309-->433 AH) … / Decreased Charge Efficiency 60-->55% (by editing config/battery.ini)					55%					20160730
				~	17:45			Observations: 98.98% maximum %SoC for the day (very slight gain over yesterday) / Maximum 14.8v battery voltage @ ~12:30; My "gut feeling" is that our %SoC is still too high, but I don't want to drop the Charge Efficiency any more now until I see a "float"					20160730
		31	Su		08:51			Adjusted %SoC downward ~1% (428.386474-->424 AH)					20160731
2016	Aug	2	Tu	~	16:15			Observations, review: since the C.E. was adjusted down on 7/30, there have been no clear signs of regulation (we've had a lot of cloudy weather); We've been losing ground: 86.3% low this morning / No adjustments can be made, because we're not anywhere near 100%					20160802
		5	Fr					Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / [8/12/16: I probably didn't notice at the time that the firmware updates beginning on 6/25/16 had clobbered the 6/6/16 A1 Calibrations in NVRAM; Therefore, all of the data after 6/25/16 is not to be relied upon]	AED					25.6					20160805
		12	Fr	~	05:00	~	08:06	Firmware updated 1.1015-->1.1025; This clobbered the NVRAM values (see AED for details) … / Restored 6/6/16 calibration values					20160812
		27	Sa	~	15:55			Sudden drop to zero solar charge several hours before the end of the solar day / Restarts (software & webrelay) didn't fix it; SMS to Mark Webb for access …	SMS					20160827
		28	Su					… solar charge is normal; I suspect another Genasun "fart"					20160828
		29	Mo	~	11:50	~	14:30	Obvious signs of regulation at Absorption/Equalization 14.2 v					20160829
				~	15:30	~	17:30	Obvious signs of regulation at Float 13.5 v …; Ratio dropped to 24W/450AH=5.3% by 17:30 / Battery SoC at this time was 76.4%: Obviously LATE!!!					20160829
		30	Tu	~	09:30	~	17:10	Obvious signs of regulation at Float 13.3v to 13.5v …; Battery SoC 75.1% (15:15) ... / Ratio 25W/450AH=5.6% (17:10); Obviously very LATE, I need a SoC correction and a change to the Charge Efficiency; Watching for Float at 13.5W Net (3% Ratio) …					20160830
				15:37		15:39	Adjusted %SoC upward to 97.1% (338.399017-->437 AH) ...; Increased Charge Efficiency 55-->70%					70%					20160830
2016	Sep	1	Th	~	11:30	~	13:40	Obvious signs of regulation at "Float" 13.4v …; Lowest ratio 51W/450AH=~11.3% …; Battery SoC 97.15% (~13:50)					20160901
				~	13:45	~	17:10	Zero solar charge again at a time when it should not be zero: I suspect a Genasun fault … / Some solar peaks through at end of solar day					20160901
		2	Fr					[L1-2] Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate	AED					24.8					20160902
				~	11:50	~	14:20	Obvious signs of regulation at 13.3v (but could be malfunctioning Genasun) … / Sudden drop to zero solar charge again					20160902
		3	Sa	~	11:50	~	14:10	Obvious signs of regulation at 13.3v (but could be malfunctioning Genasun) … / Sudden drop to zero solar charge again					20160903
		5	Mo		15:56			"100%": No obvious signs of regulation; 14.0v peak seen for about 30 mins but at Genasun limit; Obviously EARLY					20160905
		6	Tu	~	04:27			Reduced Charge Efficiency 70-->65%; Corrected SoC -2.2% (436.747497-->427AH)					65%					20160906
				~	14:00	~	17:30	Absorption ends (14.2v spotty) …; Float (13.4v spotty) and 5.1% Ratio (23W/450AH) / Highest SoC seen for the day 99.72% @~18:00; Hard to say exactly, but several hours early					20160906
		7	We	~	09:50		10:37	Entered float (13.3v spotty @ ~120W solar) …; Adjusted %SoC downward 1.0% (438.578247-->434 AH) / Stayed in float (13.3-13.4v spotty) until ~17:30 when 98.67% and Ratio ~5.2% (23W net/450AH) and the curve downwards looked like it would reach ~3% ratio at about 2 more hours of float which we didn't get					20160907
		10	Sa	~	10:55	~	13:25	Entered float (13.3v strong @ ~86W net) …; Dropped to zero solar again (Genasun?) @ net 65W					20160910
		17	Sa	~	14:10			Dropped to zero solar again (Genasun?) / ~17:20 to 19:00 small spurt of solar but no more than 10W (as seen before when this happens)					20160917
		20	Tu					SoC peaked at 97.6% but no signs of regulation (13.7v at Genasun limit, and it should go up to absorption because we've had multiple drops below 12.5v since the last time it regulated) … / Adjusted SoC downward 1.9% (436.388671-->428 AH)					20160920
		22	Th					Absorption (14.3v spotty) then clear signs of float (13.5v) but the best ratio seen was 8.1%; Obviously approaching full charge, but 99.5% SoC peak is too high; Adjusted SoC downward 2.0% (446.97467-->438 AH)					20160922
		23	Fr					Absorption (14.4v spotty and short) then clear signs of float (13.5v spotty) but the best ration seen was 7.2% / Obviously approaching full charge, but 99.3% SoC peak is a little high.					20160923
		24	Sa				13:52	Absorption (14.3v spotty) …; 100%, then clear signs of float (13.5v spotty) but the best ratio seen was 6.1% / Obviously approaching full charge, but obviously early.					20160924
		27	Tu				16:26	Genasun limited, can't say for sure it reached absorption, 14.3v peak …; 100%, early					20160927
		28	We		11:42	~	16:50	100% near start of absorption/equalization 15.1v …; Float started @ ~12:50; Ratio at end of solar 4.9% / At least 4 hours early					20160928
		29	Th		12:31	~	16:50	100% near end of absorption 14.6v …; Float started @ ~13:00; Ratio at end of solar 5.7%; At least 4 hours early					20160929
		30	Fr	~	08:45			Reduced Charge Efficiency 65-->60%					60%					20160930
				13:18	~	16:45	Absorption; 100% …; Ratio 5.3% at end of solar; At least 4 hours early					20160930
2016	Oct	1	Sa		00:50			Corrected SoC -0.7% (440.281799--> 437AH)					20161001
				[L1-2] Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / RW using 37.9 W solar in float as 3% ratio (not seen yet)	AED					24.4					20161001
				[L1-2] Color coding reminder / 100% but not 3%; Neither 3% or 100% OR 100% and 3%; 3% but not 100% (should/did correct SoC at least +x%)					20161001
		4	Tu	~	15:50	~	16:50	Dropped to zero solar again (Genasun?)					20161004
		9	Su				19:19	100% has not been seen since 9/30; 3% ratio has never been seen since the power levels went up (and so we have no idea what SoC correction is necessary); Increased Charge Efficiency from 60-->65%					65%					20161009
		25	Tu	~	14:10	~	14:40	Maybe float regulation (13.5vdc, 87% SoC)					20161025
2016	Nov	3	Th					[L1-2] Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / RW using 37.8 W solar in float as 3% ratio	AED					24.3					20161103
		21	Mo	~	11:40			[L1-2] Adjusted Time and Date Settings [UTC - 5] Eastern Standard Time --> [UTC - 6] Central Standard Time (I forgot to do this when DST ended a short while ago) / Also adjusted portal UTC Offset; This caused a glitch in the logged data (an hour got overwritten)					20161121
		23	We		19:14			SoC<50%					20161123
		26	Sa		04:24		08:32	Battery Voltage A1<11v …; Battery voltage >11v					20161126
		27	Su		06:21	~	09:50	Battery Voltage A1<11v …; Battery <10.6v, ~37°F (Wattmon tally says 38.08% SoC, but this is my definition of "0%")					20161127
				~	10:40	~	12:15	Netonix load started shutting itself off (8.9-9.0v) then on (10.6-10.7v) (cycling, internet lost) … / Onsite and replaced batteries					B8	B9	B10	B11					20161127
				12:38			Corrected SoC to 99.8% (449 AH)					20161127
				Screenshot of today's Battery Status	SSC AED					20161127
2016	Dec	1	Th	~	18:00			No clear signs of regulation seen in past 53 solar days					20161201
		2	Fr	~	12:00			Decreased Charge Efficiency 65-->60%; Corrected SoC by -1.42% (~5/65 of gains since 11/27)					60%					20161202
		4	Su		08:54			SoC<75%					20161204
		5	Mo		13:49		16:59	SoC>75% …; SoC<75%					20161205
		11	Su		09:14			SoC<50%					20161211
		16	Fr					Onsite; Panels, adjusted tilt; Could not clean (too icy); Stickers applied; Photographs & dimensions recorded / Genasuns: Installed Genasun #2; Sticker added to Genasun #1; Photographs / Installed battery box; Batteries swapped and set 99.8% SoC; Wattmon SD card copied	IMG			54	280					C2		B4	B5	B6	B7					20161216
		19	Mo					[L1-2] Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / RW using 37.1 W solar in float as 3% ratio	AED					23.6					20161219
		22	Th		03:55		13:50	SoC<75% …; SoC>75%					20161222
				~	13:30			Onsite and fixed loose connection on Genasun #2 (solar panel wire nut): Since the 16th we've only been getting about 2/3 of the available solar; Photos of 3 panels and new battery box installed 12/16/16	IMG					20161222
				15:44			SoC<75%					20161222
		26	Mo		04:25		11:56	SoC<50% …; SoC>50%					20161226
		27	Tu		00:28		12:02					20161227
				23:49	SoC<50%					20161227
		28	We		12:44		20:00	SoC>50% …; SoC<50%					20161228
		29	Th		12:55		20:12					20161229
		30	Fr		13:00		19:57					20161230
		31	Sa		13:02		19:38					20161231
2017	Jan	2	Mo					[L1-2] Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / RW using 37.8 W solar in float as 3% ratio	AED					24.3					20170102
		3	Tu	~	11:30		12:14	Onsite, batteries swapped …; SoC corrected to 99.8% (449 AH)					B8	B9	B10	B11					20170103
				14:05			100% but not 3%					20170103
		10	Tu		02:16		13:55	SoC<75% …; SoC>75%					20170110
				18:35			SoC<75%					20170110
		15	Su		11:08			SoC<50%					20170115
		18	We		22:23			Battery Voltage A1<11v					20170118
		19	Th		00:38		04:47	SoC<25% …; Internet went down (battery voltage ~9.1v)					20170119
				14:40	Onsite; Power components rewired for better wire routing, hanger clips and organization (see photos) / Batteries swapped and set 99.8% SoC (power restored @ 14:40) / Installed Genasun #5 (C6), all three panels have their own dedicated Genasun	IMG				420					C6	B4	B5	B6	B7					20170119
		20	Fr					Email to Mark Webb "Rayville Water Tower Power System Photos": 20161222 and 20170119 photos	EML IMG TSP					20170120
		21	Sa					Details on "Testing of Action to save a Logs backup file once per day": This caused some logging gaps, and the SoC dropped to 0%; I corrected the SoC to 87.33% at 08:05 (I wanted 87.318%, so this is a pretty good correction).	AED					20170121
		24	Tu		02:25			SoC<75%					20170124
		27	Fr					Superb solar day, 0.81 KwH					20170127
		30	Mo					Superb solar day, 0.83 KwH					20170130
		31	Tu					[L1-2] Email to Mark & Keith "Static IPs: conflicts? Known Hosts?": / List of IP addresses not using DHCP 12.133.21.146 (RW Wattmon), 12.133.21.157 (RW WebRelay), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.147 (DVS WAN #1), 12.133.21.140 (DVS WAN #2), all 255.255.255.128, 12.133.21.129 / Also inquired about the possibility of adding those addresses to his router's Known Hosts table / 5/7/19 I have not yet to receive a response to these inquiries	EML CPSN					20170131
2017	Feb	1	We		22:51			SoC<50%					20170201
		2	Th		10:34	~	17:00	SoC>50% ...; End of a superb solar day, 1.02 KwH					20170202
		3	Fr		06:54		10:04	SoC<50% …; SoC>50%					20170203
		4	Sa		06:50		08:37					20170204
				10:12		11:18					20170204
				21:01			SoC<50%					20170204
		5	Su		11:59				AED					20170205
		6	Mo		02:42					20170206
		12	Su		06:31		08:47	SoC<25% …; SoC>25%					20170212
		15	We					Superb solar day, 1.05 KwH					20170215
		17	Fr					Dan Paige, onsite troubleshooting of network problems; East of Rayville, he uses RW/TurboNet / Mileage 19 miles @ $0.54					20170217
		24	Fr		06:00			SoC<25%					20170224
		25	Sa		12:59		21:34	SoC>25% …; SoC<25%					20170225
		27	Mo		12:41		20:18					20170227
2017	Mar	3	Fr		12:18	~	17:40	SoC>25% …; End of a superb solar day, 1.08 KwH, but yet no signs of regulation (heavily in bulk with a peak of 13.5v, this is the highest voltage seen since before this set of batteries was installed 1/19/17, and for reference, absorption/equalize at these temperatures is about 15.2v)					20170303
		4	Sa		01:11		09:39	SoC<25% …; SoC>25%					20170304
		5	Su		12:18			SoC<25%					20170305
		8	We					Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / Using 39.3 W solar in float as 3% ratio; Sharp increase from the data on 1/2/17 is probably due to warmer temperatures causing an increase in the amount of fan cooling needed in the Netonix load.	AED					25.8					20170308
				[L1-2] Email to Mark & Keith "Re: Static IPs: conflicts? Known Hosts?": I've heard nothing about this since over a month ago; 5/7/19 I have not yet to receive a response to these inquiries	EML CPSN					20170308
		10	Fr		12:44		23:45	SoC>25% ... Peak 14.2v is the highest seen since before this set of batteries was installed 1/19/17 (but absorption at these temperatures is about 15.5v) ... Superb solar day, 1.15 KwH …; SoC<25%					20170310
		11	Sa		05:32			Increased Charge Efficiency 60->70%: studying the graphs it looks like we're much higher state of charge than 22%; I'd like to avoid a SoC correction discontinuity; I don't have a calculated reason why but my "gut feeling" says over and over again "we're low."					70%					20170311
		18	Sa		16:55		19:09	SoC>25% …; SoC<25% [CDT]					20170318
		19	Su		13:32			SoC>25%					20170319
		20	Mo		00:28		10:51	SoC<25% …; SoC>25%					20170320
		22	We					Peak 14.2v (highest seen since March 10th) (brief 258w peak near solar noon)					20170322
		25	Sa		04:07			SoC<25%					20170325
		29	We		05:35			Battery Voltage A1<11v					20170329
				~	08:20	~	08:38	Onsite: Swapped batteries; set 99.8% SoC (449AH); Placed (2) ant traps / Lower two panels were sagging ~5deg, I adjusted them ~10deg above the top panel				48					B8	B9	B10	B11					20170329
2017	Apr	3	Mo		20:52			SoC<75%					20170403
		6	Th					Superb solar day, 1.20 KwH, +6.8% SoC gain					20170406
		7	Fr		12:02			SoC>75%					20170407
				Turbonet, rec'd referral fee $50, I can't remember who this was for, maybe Butch	TSP					20170407
		11	Tu	~	10:50	~	18:05	Obvious signs of regulation in absorption/equalize (14.8v, ~175-160w) and float (14.0-13.9v, ~115-100w): The last time we saw obvious regulation at RW was 9/1/16 to 9/3/16 (7-1/2 months ago). 95.2% SoC at end of solar.					20170411
		12	We	~	10:30	~	14:30	Regulation in float (13.8v, ~125-90w, ~15% ratio); 96.3% SoC at end of solar					20170412
		13	Th	~	10:00	~	17:00	Regulation in float (13.6v, ~145-70w, ~10% ratio); 98.2% SoC at end of solar					20170413
		17	Mo		17:53		18:09	100% but not 3% (8.0% minimum at end of solar)					20170417
		18	Tu		14:21		18:06	100% but not 3% (7.6% minimum at end of solar)					20170418
		19	We		15:05		18:12	100% but not 3% (7.1% minimum at end of solar)					20170419
		20	Th		14:51		18:04	100% but not 3% (5.2% minimum at end of solar); Signs that one controller was trying to hold absorption (14.4v) while others at float (13.7v)					20170420
		22	Sa		16:14		17:53	100% but not 3% (6.7% minimum at end of solar)					20170422
		23	Su	~	12:10			Decreased Charge Efficiency 70->65%					65%					20170423
				14:16		17:58	100% but not 3% (7.1% minimum at end of solar)					20170423
		24	Mo		16:45		17:59	100% but not 3% (7.0% minimum at end of solar)					20170424
2017	May	1	Mo		00:04			SoC<75%					20170501
		2	Tu		12:14					20170502
		3	We		00:18					20170503
		4	Th		17:06		18:31	SoC>75% …; SoC<75%					20170504
		5	Fr		11:39			SoC>75%					20170505
		6	Sa		05:45		08:59	SoC<75% …; SoC>75%					20170506
2017	Jun	27	Tu					[L1-3] Email to Mark "Re: DC UPS quote examples (RW, RN)": / I talked with Mark and Keith while they were at RW to meet AmerenUE	EML					20170627
2017	Jul	10	Mo					[L1/3] Email to Mark "Re: DC UPS quote examples (RW)": / I quoted $500 for a DC UPS at RW, and was looking at a 180 Watt power supply.					20170710
		12	We					[L1/3] We met at McDonald's in Richmond (I had to buy Skype Credit $10 to facilitate communications, and 20 miles @ $0.54) / Mark Webb of Turbonet advanced me $400.00 for "Rayville Battery Back-up DR" (this was to develop WISPower #1 for them) / Emails with Mark and Keith "RE: DC UPS stuff (WISPOWER)"; Started design and procurement of parts	TW1 WP1 EML					20170712
2017	Nov	3	Fr	~	16:15			Batteries swapped					B4	B5	B6	B7					20171103
		28	Tu	~	15:30					B8	B9	B10	B11					20171128
2017	Dec	22	Fr	~	14:15					B4	B5	B6	B7					20171222
		28					“7 Day Average Load Watts” (AED L1W8M1O2 5/2/18-5/3/18)	AED					24.1					20171228
		29	Fr	~	14:00			Batteries swapped					B8	B9	B10	B11					20171229
2018	Jan	15	Mo	~	12:00			Batteries swapped; WebRelay R_2 (R2) Removed	AED					B4	B5	B6	B7					-			20180115
2018	Feb	23	Fr					Email to Mark & Keith "AC at RW?": Potential crisis this weekend as batteries are very low / Pleaded for a change, as I was getting very weary of swapping out batteries	EML TSP					20180223
				Email to Mark & Keith "Re: AC at RW?": 'P.S. - it looks like Rayville will be down starting in about 30 minutes (9:30pm). Hopefully the sun comes up first thing in the morning.'					20180223
		24	Sa		08:27			Email from Mark "Re: AC at RW?": He asked me to go swap the batteries (Rayville was down)					20180224
				~	09:30			Batteries swapped					B8	B9	B10	B11					20180224
2018	Mar	29	Th	~	13:50					B4	B5	B6	B7					20180329
2018	Apr	23	Mo	~	05:30			Noticed that portal data stops on 4/20/18 ~22:30 CST (~23:30 CDT) / Tried some remote troubleshooting but decided it would be best to bring W8 to L0 and fix it here …	AED	Errors Exporting					20180423
		24	Tu	~	09:05			Onsite; Photos of current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery) / Removed W8	AED IMG	No Wattmon					None					20180424
				“7 Day Average Load Watts” (AED L1W8M1O2 5/2/18-5/3/18)	AED					26.0					20180424
		26	Th				06:22	SoC corrected for 2 days logging gap …; Onsite @ RW: Wattmon_8 and T_2 up and running		Active					W8			O2		20180426
2018	May	28					“7 Day Average Load Watts” (AED L1W8M1O2 6/4/18)					28.2					20180528
2018	Jun	4					Onsite (outside fence) to shoot photos needed to plan AC installation; Email from Mark Webb with AUE specs	IMG EML					20180604
		5	Tu					Email to Mark Webb "Rayville Water Tower - Initial Estimate - Request for Advance" (AC Installation and W100) / Email from mo@occinc.com (Missouri One Call, locating, link to request status)	EML					20180605
		6	We					Met with Mark Webb at USB in Richmond and rec'd $400.00 check for "Rayville electrical hook -up (half)"	TW2-3					20180606
		8	Fr					Onsite to meet with Christ Adams (USIC), Doug Alberti (AUE) and Stan Barr (PWSD) to locate and discuss AC installation for TurboNet	IMG					20180608
		20	We					Changes to my.wattmon.com: Latitude and Longitude corrected (they were reversed)					20180620
		27					“7 Day Average Load Watts” (AED L1W8M1O2 7/1/18)	AED					28.3					20180627
2018	Jul	3					20180703 PWSD Proposal.pdf sent to Stan Barr (and Mark and Keith)	EML DBT TW2-3					20180703
		20	Fr					Onsite with Stan Barr of PWSD to install AC drop from their equipment; Removed P_3; Removed Genasun_5			200		280					-			-					20180720
		24	Tu					Email to Mark with 20180724 Invoice - Rayville Water Tower.pdf ($498.50 due when installed, ETA 7/27/18) / Also see 20180724 Invoice - Rayville Water Tower - Detailed Labor.pdf	EML DBT TW2-3					20180724
		28					“7 Day Average Load Watts” (AED L1W8M1O2 8/12/18)	AED					28.1					20180728
		31	Tu					Met Mark @ Richmond WalMart and rec'd $498.50 check (final payment, AC and W100 @ RW)	TW2-3					20180731
2018	Aug	2	Th	~	04:30			Since I pulled the 3rd panel and Genasun on 7/20/18 the battery has been dropping, now ~60% WSoc / WSoC has dropped from ~90% on 7/20 to ~60% today (losing 2.3% per day average); Unless solar improves batteries will be exhausted in about 3 weeks (working on W100_2 but it's not ready yet)					20180802
		8	We					Analysis: w/o 3rd panel we lose 1% WSoC on a good sunny day (currently 42%, low of 11.3v). But charge efficiency is very high, so we could be breaking even or even a little better. In any case, a few cloudy days and we can drop a lot. (Working on finishing W100_2 for RW before the batteries die.)					20180808
				11:06		11:19	SMS from Mark Webb "Did you get there Rayville tower totally switched over to electric let me know man thanks" …; SMS reply to Mark "I was working on this when you texted me. Final installation should be done by Friday. I'll be contacting Stan Barr to let me in."; His response "Ok. Let me know when it's done. Thanks"	SMS					20180808
		10	Fr		08:19			Stan Barr called: he will call again Mo8/13 ~08:00 and if nothing is in the way he can come up to Rayville right after that					20180810
		13	Mo	~	09:00		13:30	Stan Barr called, he can be there at 09:15; Loaded Subaru and left for tower; Onsite 09:15; AC OK; Photos (before) / Removed solar panels, Genasuns, (2) T-105s in main equipment box and C252_1 / Installed W100_2 (with C252_2) and 27TMX (Netonix running); Set up for onsite Tshooting of Wattmon_8 corruption issues; SD Card Copy (not checked, decided to Tshoot at shop); Removed Wattmon_8; Removed (2) T-105s, battery box and battery bus bar; More photos (after); Returned to Shop ~12:30 / Subaru unloaded (but lots of stuff to sort through and put away); T450s problems (no drives, keyboard, mouse)	IMG		-	-	-	105.00		-	-		-	-		-	-		B1	-	-	-			-	M2			WP3	20180813
	Nov	29					Photos of Porsche with Water Tower in the background					20181129
2019	Jan	19	Sa					Email to phone "MMS graphic to send to Mark & Keith" showing screenshot of SpeedTest and extremely poor download and upload speeds (0.79/0.56 Mbps down/up)	EML SMS SSC					20190119
		31					From shop porch: Snow, cold, water tower, Triton, Julia's Throne	IMG					20190131
2019	Feb	14	Th					Emails from/to Mark Webb "Re: Reason Swafford photos, Jan 22nd visit to tower" where he asks me "Have you talked to the guy at the water Dept lately? …"; Mentioned that I haven't reinstalled the monitoring system at RW and that they s/b using Netonix to send email below 13.0v	EML					20190214
				Stan Barr conversation (relayed to Mark Webb): No date yet on painting tower, but probably "mid year"; PWSD people will meet ~3/12/19 to talk about needs; See white sheet notes	TW2-3					20190214
				15:33		16:27	Email to Mark Webb "Speedtest, this morning and yesterday morning" showing 0.75 Mbps average download for 2 tests …; Email to Mark Webb (same subject) with screenshot showing 5.51/3.27 Mbps down/up (much better)	EML SSC					20190214
		15	Fr		06:25			Email to Mark Webb "Speedtest this morning" with screenshot showing 16ms, 12.44/4.49 Mbps down/up and I say "This is the best I've seen in a week, whatever was causing the problems has disappeared."					20190215
2019	Apr	3	We					Stan Barr conversation: Everything has to come off, they're going to cut the center section out, center top will be cut off, pully system mounted there; Probably September; PWSD is thinking of getting a 100-125' tower, inside the fence, self-supporting; I suggested NE corner (if only 100' tall). Mark Webb conversation: He suggested we should bid on the tower installation; Discussed the offer I made (see email), ~$100 per month internet, I'd like to work it off each month. Another Stan Barr conversation: I mentioned we would like to bid on the tower installation; he said he'd check water tower height and get back to me by the end of the week. See printout of detailed call record.	EML TW2-3					20190403
		4	Th					Stan reports that water tower overflow is 110 feet + 2 feet for hatch (we need 115' foot tower?); See printout of detailed call record	SMS					20190404
		17	We					Email to Mark and Keith "Multiple Short Internet Outages": Just FYI, 4 different 1-2 minute outages detailed	EML					20190417
		19	Fr		20:34		20:47	No internet …; Internet Restored (outage 13 minutes)					20190419
		20	Sa					Email to Mark and Keith "FYI - You knew about the outage last night, right?"	EML					20190420
		28	Su		15:58			No internet …					20190428
		29	Mo					Stan Barr conversation: They aren't going to build a tower; Painting/restoration of Rayville Water Tower begins ~5/15; TurboNet is inquiring about using the Elkhorn tower (Overflow 1205', Railing 1165' MSL, close to Elkhorn school, 12719 Short Road, E.S. MO); Rayville tower is 1100' MSL. 2nd call from Stan: Do TurboNet/Mark/Keith know that PWSD in Richmond is also down?. 3rd call from Stan: I told him that PWSD Richmond TurboNet w/b fixed in about 2-4 hrs; arrangements to meet at RW for maintenance of the power system. See printout of detailed call record.	TW2-3					20190429
				11:00		12:05	Prepared to go onsite for Maintenance					20190429
				12:05		12:50	Travel & onsite: Battery watered; Checked AC outlet & installed cover plate / Removed the last of the Wattmon stuff; Cleaned W100 fan/filter (compressor); Ant trap installed					-		-		20190429
				12:50		14:05	Follow up: Rayville still down but Mark says they see my unit; Rebooted CradlePoint; Restarted Ubiquiti; No service; CradlePoint Static --> DHCP; 13:32 we are up but without incoming services that need fixed IP. Includes communications with Mark. See white sheet for details on today's maintenance.	TW2-3 WS					20190429
				17:15		17:40	Phone call to Mark Webb: I'm hoping to put up a 75-100' tower (PWSD is removing our stuff ~5/15); I finished maintenance on his equipment, good for the next 6 months; I agreed to $110/month for my internet ($105 + $5 for static IP) starting 5/1; Discussed Elkhorn and the fact that he may not be able to provide me service here from that tower; He'll pay my invoices, I'll pay his invoices; See back of bank check note					20190429
		30	Tu		11:33			Email from Mark originally from Keith "Jeff Klute Static IP address" which I could use on current subnet: 207.229.103.54, 255.255.255.252, 207.229.103.53, 1.1.1.1, 8.8.8.8 (not used)	EML CPSN TW2-3					20190430
2019	May	1	We		02:42		03:33	No internet …; SMS to Mark and Keith	SMS					20190501
				08:23		08:29	Called Mark, no answer …; Internet restored (outage 5 hrs 47 min)					20190501
				08:30		08:33	No internet …; Internet Restored (outage 3 mins 9 s)					20190501
				09:17			Email from Worldwide Technologies with PDF Invoice $110 for May	EML TW2-3					20190501
				12:29		12:56	No internet; Mark advises me to switch back to my fixed IP (unit has been replaced) … / CradlePoint set for previous fixed IP; Internet Restored (outage 26 mins 18 s)	CPSN					20190501
		2	Th		01:16		01:18	No internet …; Internet Restored (outage 1 min 19 s)					20190502
				07:41			Called WT 660-259-4705, office hours are 9-5 M-F, LMVM (questions) …					20190502
				09:10		09:37	Call from Mark Webb: Full agreement has been arrived at / "10Mg plan" is 10 Mbps up and down CIR (Committed Information Rate) / Previous Invoices are "Paid in Full for Service Rendered" / Internet invoices start 5/1/19, I will mail a check today for $110; BTW Art Morrill is moving to Idaho	TW2-3 DBT					20190502
				10:41			Speed Meter w/o CrashPlan or OneDrive: 3.35 Mbps down, 2.80 Mbps up					20190502
				13:30		13:31	No internet …; Internet Restored (outage 52 s)					20190502
				14:25		15:23	Speed Meter w/o CrashPlan or OneDrive: 3.47 Mbps down, 3.49 Mbps up …; SMS from Mark, "Yes. Just updated the firmware on your unit. It's set to 11 mg up and down. Watch it tonight and let me Know tomorrow how it's doing? OK"	SMS					20190502
				15:19		15:29	No internet …; Internet Restored (outage 2 min 7 s)					20190502
				18:47		18:53	Speed Meter w/o CrashPlan or OneDrive: 4.62 Mbps down, 4.61 Mbps up; Email to Mark …; Email from Mark "Ok. Keep watching and let me know in the morning."	EML					20190502
				18:54		18:55	SMS from Mark: "Make sure your other stuff isn't running when you do the test. Also what speed test site are you using?" …; SMS to Mark"I told you in my last messagae that that is exactly what I have been doing. Background traffic is less than 1 kilobit per second."	SMS					20190502
				18:59		19:03	SMS from Mark: "Plug directly into my power supply and go to speedtest.googlefiber.net and tell me what it is." …; SMS to Mark "First of all, I don't use a website to check my speeds. I have software which I paid a lot of money for that tells me exactly what it is, locally. NetWorx, industry-standard."					20190502
				19:04		19:04	SMS from Mark: "Just humor me. Send me a pic of what you get" …; SMS to Mark "Yes, will do"					20190502
				19:18		19:25	Email to Mark Subject "Screenshot from speedtest.googlefiber.net" Body "Mark, Various results, but this is the best." (Screenshot attached, 3.61 Mbps down, 0.87 Mbps up) …; SMS to Mark "Screenshot sent to your email. Please check it in the morning and I will be in touch with you tomorrow, thank you. 3.61 Mbps down, 0.87 Mbps up. I think you should agree that my networx reading is more accurate. Obviously, because we are at PEAK internet times, I do not have a committed information rate or CIR."	EML SMS					20190502
				19:44			Email to Mark Subject "Re: Screenshot from speedtest.googlefiber.net" Body "Follow up: This is Screenshot from NetWorx (this is NOT free software). Much better way to test, industry-standard. Ignore the other tests, they weren't when all background traffic was stopped. 4-5 Mbps up and down."	EML SSC					20190502
				05:14		05:22	(3) Speed Meter tests w/o CrashPlan or OneDrive (down/up, Mbps): 3.99/4.98, 4.65/5.09, 4.84/6.20 (average 4.49/5.42)					20190502
		3	Fr		09:43			Email to Mark "Re: 10 Mbps CIR?" (I asked him to set 22 Mbps throttle so we can see what happens)	EML					20190503
				11:32			Speed Meter with CrashPlan/OneDrive (hourly schedule): 13.3/1.15					20190503
				12:32			Speed Meter with CrashPlan upload doing about 2-5 Mbps (hourly schedule): 20.4/5.44					20190503
				14:47			SMS from Mark "Changed you to wide open" (no CIR, just whatever is available)	SMS					20190503
		4	Sa					Invoice sent to Mark via email & USPS "Revised Invoices as per our agreement", $160 and $120 but "Paid in Full by Service Rendered (Internet before 5/1/19)"; Income for $120 added to revenue for WP3	DBT TW2-3					20190504
				$110 paid for May internet invoice 77260	TW2-3					20190504
		7	Tu		00:38		00:48	No internet …; Internet Restored (outage 9 min 34 s) - Thunderstorms					20190507
				10:47		10:51	Noticed (2) PWSD trucks down at the tower; Call to Stan Barr (who is at the tower talking about what needs to be done); They haven't heard from the contractor; Yesterday Mark mounted antenna at Elkhorn but it isn't fully programmed yet; Don't have a definite date yet (on when the radio stuff must be removed), but he'll let me know					20190507
				22:30		22:31	No internet …; Internet Restored (outage 1 min 9 s) - Thunderstorms					20190507
		8	We		01:40		01:42	No internet …; Internet Restored (outage 2 min 7 s) - Thunderstorms					20190508
		9	Th		21:49		21:50	No internet …; Internet Restored (outage 55 s)					20190509
		10	Fr		05:47		05:47	No internet …; Internet Restored (outage 46 s)					20190510
				13:05		13:05	No internet …; Internet Restored (outage 48 s)					20190510
		12	Su		22:43		22:43	No internet …; Internet Restored (outage 9 s)					20190512
				Relaxed NetWorx Connection Monitor Settings: Timeout 10-->20 secs (3 retries) as I don't really want to know about outages of less than 1 minute (T400s/T450s)					20190512
		13	Mo		22:50		22:51	No internet …; Internet Restored (outage 1 min 17 s)					20190513
		14	Tu		05:25		05:27	No internet …; Internet Restored (outage 1 min 18 s) - Thunderstorms					20190514
				12:52		12:53	No internet …; Internet Restored (outage 1 min 36 s) - Thunderstorms					20190514
				14:10		14:12	No internet …; Internet Restored (outage 1 min 32 s) - Thunderstorms					20190514
				14:14		14:15	No internet …; Internet Restored (outage 47 s) - Thunderstorms					20190514
				14:58		14:59	No internet …; Internet Restored (outage 49 s) - Thunderstorms					20190514
				15:08		15:10	No internet …; Internet Restored (outage 1 min 39 s) - Thunderstorms					20190514
				15:18		15:19	No internet …; Internet Restored (outage 1 min 3 s) - Thunderstorms					20190514
		15	We		08:38		09:28	Power outage including Rayville, Wood Heights …; Power restored after 50 minutes / Load during this time was about 28 Watts/~2.3 Amps; Therefore B1 discharged to ~98 %SoC	A1					20190515
		18	Sa		08:09		09:31	No internet; Switched to hotspot 08:47 …; Switched off hotspot 09:31 / Internet Restored (outage 38 mins to 1 hr 22 mins, not sure, was on hotspot) - Thunderstorms					20190518
		20	Mo		11:23		11:27	No internet …; Internet Restored (outage 3 min 59 s) - Thunderstorms					20190520
				16:24		16:25	No internet …; Internet Restored (outage 1 min 26 s) - Thunderstorms					20190520
		21	Tu		01:26		01:27	No internet …; Internet Restored (outage 59 s) - Thunderstorms					20190521
				14:38		14:40	No internet …; Internet Restored (outage 1 min 19 s) - Thunderstorms					20190521
				14:43		14:49	No internet …; Internet Restored (outage 6 min 32 s) - Thunderstorms					20190521
				14:53		14:54	No internet …; Internet Restored (outage 1 min 47 s) - Thunderstorms					20190521
		24	Fr		21:25		21:26	No internet …; Internet Restored (outage 1 min 27 s) - Thunderstorms					20190524
		25	Sa		23:41		23:42	No internet …; Internet Restored (outage 1 min 29 s) - Thunderstorms					20190525
2019	Jun	4	Tu		14:21	~	15:05	Phone call from Keith Jones (concerning W100 for Odessa): RW will be down next week, and now PWSD is saying that we can put the service back on the tower about a month later when they are done; This was news to me, because Stan Barr had said PWSD does not want any radio stuff put back on the tower after it is refurbished / The sandblasting company is working on the tower now, and they often block the signal when they are on top, causing outages	WP4					20190604
				17:10		17:27	No internet …; Internet Restored (outage 16 min 40 s) - Workers on tower					20190604
				17:45		17:49	No internet …; Internet Restored (outage 4 min 8 s) - Workers on tower					20190604
		5	We		07:26		07:38	No internet …; Internet Restored (outage 12 min 3 s) - Workers on tower					20190605
				09:12		09:44	No internet …; Internet Restored (outage 31 min 23 s) - Workers on tower					20190605
				13:42		13:43	No internet …; Internet Restored (outage 50 s) - Workers on tower					20190605
				16:46		16:47	No internet …; Internet Restored (outage 1 min 47 s) - Workers on tower					20190605
				16:48		17:03	No internet …; Internet Restored (outage 15 min 28 s) - Workers on tower					20190605
		9	Su		05:11		05:12	No internet …; Internet Restored (outage 1 min)					20190609
				06:10		06:11	No internet …; Internet Restored (outage 58 s)					20190609
		10	Mo					The workers are on the tower again today; I checked the Speed Meter which is now mysteriously working again, and discovered that the internet for the past few days sucks, below 1 Mbps down, 1.5 Mbps up / Emails to Mark and Keith, with Screenshot of Speed Meter results for the past day or so	EML SSC					20190610
				09:48		09:51	Call Stan Barr (c): Mark & Keith probably know better than Stan as to when we lose service; It is correct that we can put the stuff back … maybe, he’ll check, confirm and get back to me today, but that’s what he thought; “It could be 90-120 days” before they finish! (Keith talked about it being 30 days)					20190610
				~	10:15			I walked down and talked with the man on the ground at the tower: He said he'd let the tower guys know not to sit in front of the antenna for long periods of time; He also said that "the end" could be this week, or several weeks, depending on the weather; I managed a few quick photos before the battery died on the Samsung phone / Email to Mark	IMG EML					20190610
				12:59			Missed call and voicemail from Stan Barr: TurboNet will be able to put their antenna back up on top / But he also said this would be "at least 90 days"					20190610
				21:26		21:29	No internet …; Internet Restored (outage 3 min 10 s)					20190610
		11	Tu		08:50		09:50	Called Mark (c): Relayed info from Stan Barr; Complained again about <1Mbps service; Was told not to bother to pay $110 for June until after we see when RW goes down and if they can possibly give me a temporary link / Will meet @ USB in Richmond for check for W100 in Odessa					20190611
				~	11:00			Met Mark @ Richmond USB: Rec'd check for Odessa W100; Mark and Keith will be in Rayville tomorrow (We6/12) to finish work on Van Till connection to Elkhorn and will see then if they can get me a temporary connection from the Van Till Farms (but I think there's too much in the way, including Tom's old church building)	TW2-3 WP4					20190611
				14:26		14:44	No internet …; Internet Restored (outage 17 min 54 s) - Workers on tower					20190611
				14:55		14:57	No internet …; Internet Restored (outage 1 min 12 s) - Workers on tower					20190611
				15:42		15:43	No internet …; Internet Restored (outage 1 min 18 s) - Workers on tower					20190611
				16:27		17:36	No internet …; Internet Restored (outage 1 hr 9 min) - Workers on tower					20190611
		12	We		06:16		06:22	No internet …; Internet Restored (outage 6 min 29 s) - Possibly due to thunderstorms					20190612
				12:27		12:32	I drove past Elkhorn Water Tower and shot photos; TurboNet recently installed service from there, and the Van Till Farm is or will be serviced from Elkhorn; I don't think I can see Elkhorn, but maybe we'll be able to "piggyback" on the Van Till feed temporarily	IMG					20190612
				13:19		13:20	I called Mark: Their trip to Rayville, Van Till and my place postponed until tomorrow (Thursday)					20190612
				15:00		15:01	No internet …; Internet Restored (outage 1 min 22 s) - Thunderstorms					20190612
		13	Th	~	07:15	~	07:45	I tried to get a photo of the water tower but the phone battery is so poor now I couldn't even get one / Talked with the foreman, the shroud won't go up until next week, it is raised and lowered each workday (so I should be able to get a good photo, standing in front of "the guys" house, with their flag in the foreground, showing the water tower's "crown")					20190613
				09:30		09:30	No internet …; Internet Restored (outage 36s) - Workers on tower					20190613
				10:52		10:52	No internet …; Internet Restored (outage 31s) - Workers on tower					20190613
				11:52		12:00	No internet …; Internet Restored (outage 7 min 49s) - NO workers on tower					20190613
				12:41		12:42	No internet …; Internet Restored (outage 1 min 5s)					20190613
		14	Fr	~	23:30	~	00:53	Very poor internet, pings are 450-650ms; NetWorx Speed Meter on T450s has stopped working; Unable to get a test with Speedtest.exe or .net; CradlePoint wouldn't connect to hot spot; Rebooted CradlePoint, still wouldn't connect; Manually disabled Ethernet in CradlePoint; 00:12 Established internet for about 40 mins until 00:53 when I Enabled Ethernet on CradlePoint and turned off WiFi Hotspot	CPSN					20190614
		15	Sa	~	00:55	~	00:57	NetWorx Speed Meter still not working …; Speedtest.exe 30ms, 3.2/0.23 Mbps down/up (useable); Very poor internet was probably caused by thunderstorms in the area					20190615
		16	Su	~	06:30	~	15:15	SpeedTest.exe: 268-382ms, 0.2-2.7 Mbps down, 0.2-2.3 Mbps up; Browsing is unuseable …; 655ms, 1.33 Mbps down, 0.80 Mbps up; Browsing is unuseable					20190616
		17	Mo	~	01:40			SpeedTest.exe: 21 ms, 3.9/1.9 Mbps down/up					20190617
		18	Tu		12:11	~	14:45	Missed call from Stan Barr …; I called him back: He asked about our battery backup, because he needs to disconnect the AC to his box when he removes it; He'll reconnect the AC after ~15-30 mins so that we have power; He highly recommends that we remove our box as (1) it will be in their way and (2) there will be a tremendous amount of dust; He's not sure if we can leave the posts in place; We could use duct tape and seal the box; They are still waiting for DigRite to locate so that they can place the anchors for the shroud, but it's looking like this week we'll lose the internet					20190618
		19	We		23:05			SpeedTest.exe: 178ms, 1.5/0.3 Mbps down/up; Browsing is poor					20190619
		21	Fr		08:07		08:08	No internet …; Internet Restored (outage 1 min 37s) - Thunderstorms					20190621
				~	13:37	~	13:55	Keith called: (Odessa will be installed Tuesday or Wednesday); RW internet sucks: resonances in cables, very low speeds, nothing to be done about it; He provided 200 Mbps to Van Till, but there is no way to get a connection from there to here; Helium balloon, omni antenna, dirigible?					20190621
				22:03		22:11	No internet …; Internet Restored (outage 7 min 59s) - Thunderstorms					20190621
		22	Sa		21:56		21:57	No internet …; Internet Restored (outage 1 min 23s) - Thunderstorms					20190622
		23	Su		04:38		04:39	No internet …; Internet Restored (outage 1 min 17s) - Thunderstorms					20190623
				04:44		04:45	No internet …; Internet Restored (outage 52 s) - Thunderstorms					20190623
		24	Mo		06:13		06:15	No internet …; Internet Restored (outage 2 min 17 s)					20190624
				06:16		06:26	No internet …; Internet Restored (outage 9 min 19 s)					20190624
				06:55		06:58	No internet …; Internet Restored (outage 2 min 51 s)					20190624
		25	Tu	~	09:50			I walked down and talked with the man on the ground at the tower: He said they had contacted whoever about taking down TurboNet stuff tomorrow, as they are getting ready to lift the curtain and cover the top; I also met Stan Barr who confirmed this; Mark Webb called to say he hadn't yet heard from PWSD, but I told him what I knew, and not to plan anything until he hears from them					20190625
		26	We	~	00:52			SpeedTest.exe: 31ms, 3.8/0.4 Mbps down/up; Browing is poor, probably due to upload speed being so low					20190626
				~	18:15	~	18:30	Discussion with guys working on the tower (as they drove past at the end of their day): They have been trying to contact Keith Jones for 2 days; I gave them TurboNet office and Mark Webb cellphone numbers / I called and left a voice mail for Mark explaining all this, that they "need the stuff off the tower now."					20190626
		27	Th		08:11	~	09:45	Call from Mark Webb: He asked that I come over and help him remove the battery and box, and store it at my place; I volunteered to keep it float charged (but it doesn't really need to be if we're down for less than 6 months); I should charge him for this time, and settle on the internet; Stopped my work with W100 Testing, got dressed, loaded tools and went in the Subaru ...; Returned and moved box and battery to W storage, and the poles to the old house driveway; Chargeable time at least one hour; Onsite I agreed with Mark that if he considered the $110 invoice as paid in full (worth about $60 to me, because it hasn't been 10 Mbps CIR) than I won't bill him for my time; Updated status on L1, B1 and WP3; WP3 hours increased by this time; WP3 income increased by $60	TW2-3 WP3 IMG					-	-			-					-					-	20190627
				08:32			TurboNet offline until tower is repainted		Down					20190627
2019	Jul	1					Sandblasting curtain raised, as seen from shop porch	IMG					20190701
		2					20190702
		10					Various views of the Rayville Water Tower and sandblasting curtain					20190710
2019	Aug	7	We	~	08:15	~	14:55	Called Keith, NA; SMSs …; Call from Keith: He's in California setting up wireless for a wine train; He'll be back from CA and FL in 1-2 weeks; B54 and W100_2 won't be installed at Lexington until he is back and there is time to do it; I mentioned that RW tower may be finished in about 2 weeks and he said "I don't care"	SMS WP5 B54 WP3					20190807
2019	Sep	3	Tu	~	08:30	~	11:13	It looks like sandblasting/painting job will be finished this week; Called Stan Barr (PWSD), he or John will be talking to Mark Webb, should be able to put TurboNet stuff back up later this week; Called Keith Jones, LMVM; Called Mark Webb, LMVM …; Mark called, he's going to visit the water board tonight (they want him to possibly take equipment from Elkhorn), depending on how it comes out with the board he's planning on We-Th this week, he said he'd call me after he meets with PWSD					20190903
		4	We		11:39			Call from Mark; Poles are on the driveway; He'll be @ RW w/Keith this PM / Elkhorn stays but PWSD wants $300/mo + $50 to open					20190904
				~	15:00	~	15:30	Onsite with Mark and Keith; They picked up the poles from my driveway; Stan Barr also there (he's retiring in the next year or so); Keith to be here ~10:30 tomorrow; There will be new equipment for shop					20190904
		5	Th	~	10:15		10:45	From/To Keith (he's on his way, I suggested he stop at the shop to load up the box and the battery); New label applied to equipment box …; Keith and Brandon left for RW with equipment box, battery and my post driver	SMS					B54					WP3	20190905
				~	16:23			Keith reports that Netonix is hooked up and running (w/o AC)					20190905
		6	Fr		13:13		14:20	Call to Keith who is onsite; Mark is on the tower; Please come and help with AC; Prep. and onsite; AC connection finalized; Zip ties; WP3 is in Float; Mark and I agree to call it even for this service call and this month's internet charge (24/30*$110=$88 added to revenue for WP3); Returned to shop; Onsite again, silicone in conduit					20190906
				14:33		14:57	TurboNet up …; NetWorx Speed Meter 22ms, 19.2/18.7 Mbps; To Keith	CPSN SMS	Active				105.00	C/20			-					20190906
		7	Sa					NetWorx Speed Meter at times when CrashPlan is NOT utilizing any bandwidth: 02:31 12.3/6.75; 03:31 0.66/1.25; 04:30 0.81/10.2 Mbps Down/Up (we do not have 10 Mbps CIR)					20190907
		8	Su		05:13		08:27	No internet …; To Keith & Mark "Rayville down since 05:13	SMS					20190908
				10:27			From Keith "Power issue whole tower is down backup link is offline as well"					20190908
		9	Mo	~	10:30			Mark Webb knocks on the door and asks me for a fuse (internet outage this weekend was caused by the Netonix shorting down during a thunderstorm); I tell him there is one silver taped to the cable next to the fuse holder; I also gave him (2) from stock [Note added after talking with Brandon: Keith replaced the DC Netonix with an AC Netonix, because they don't have another DC unit in stock; Battery is probably being charged by WP3]					20190909
				~	11:00	~	11:25	Brandon Webb changes out the transceiver on the roof: The Ubiquiti NanoStation is replaced with a LiteBeam AC with directional antenna; Note that the old Red Elm @ 204/206 W 3rd is in the path between the tower and the AC unit (but it is probably not affecting performance except to a small degree); New POE injector; Brandon set bandwidth throttling at 11.5 Mbps; When we couldn't get a connection with fixed IP he switched the LiteBeam to bridge mode; Internet Restored (total time down 1 day 6 hours); Good connection with fixed IP / 11:19 19/10.7/10.3, 11:23 26/10.6/9.39 (ms/Mbps down/up)					20190909
				14:41	~	14:45	Call to Keith NA; Call to Mark NA; To Keith "So from what I learned from Mark and Brandon, when the DC Netonix went down it shorted out the power supply, but the fuse I designed did what it was supposed to do and kept there from being a fire. And that now, the water tower is running on an AC Netonix. Correct?"	SMS					20190909
				14:51	~	14:56	Call from Mark, who confirmed the facts stated above (but that they used some cheap switch, not an AC Netonix)					20190909
		16	Mo	~	04:00	~	05:16	Noticed Speed Meter results starting 9/15 13:13 are all <=1 Mbps download; Speedtest.exe ~2.5 Mbps (2 tests); (R) T450s; Speed Meter 701 kbps down (SSC); Speed Meter (2) tests w/FireFox closed and CrashPlan paused (855/791 Kbps down, 8.31/6.62 Mbps up, SSC) ...; To Mark & Keith	SSC EML					20190916
		17	Tu		03:55		03:59	Downloads continue 0.5 to 1.0 Mbps (SSC) …; To Mark & Keith "Re: Sudden drop in speeds"					20190917
				09:05		09:10	Call to Keith Jones, NA; Calls to Mark Webb, could not connect					20190917
				10:05		10:12	From/To Keith "Made some changes please test. Let me know."; Paused CrashPlan, Speed Meter, SSC ... / "No improvement, see attached."	SSC EML					20190917
		18	We		07:12		07:17	Speed Meter recorded a sudden increase in download speeds starting around midnight (SSC) / To Keith/Mark "Sudden increase in speeds"					20190918
				16:38		16:39	Calls to Keith and Mark (NA)					20190918
		22	Su		05:45		05:58	Speed Meter shows sudden decrease in download speeds starting at about 6pm on Th9/19, continuing at <= 1 Mbps …; To Keith/Mark "Again: Sudden decrease in speeds"	SSC EML					20190922
		23	Mo		10:00		10:10	Call from Mark & Keith: Test directly on their PoE splitter, especially 1.1.1.1 ping times, using T450s laptop (DHCP and static 207.229.103.164)					20190923
				10:29		10:35	T450s direct on TurboNet (PoE adapter), NetWorx Speed Meter results: / DHCP, 1 Gbps link speed, 10.10.11.210 67/22.3 Mbps down/up … / Static IP 207.229.103.164, 255.255.255.248, 207.229.103.161, 8.8.8.8, 8.8.4.4, 50.9/21.6 down/up					20190923
				10:38			Restored cabling, T450s DHCP on my network 30.5/6.53 down/up					20190923
				~	10:42	~	10:45	Call to Mark & Keith: I've got a problem with my equipment, I'll Tshoot, he'll leave the interface wide open for now (no bandwidth throttling)					20190923
				11:10		11:17	NetWorx Speed Meter, CrashPlan paused, 36.1/15.3 down/up; Unplugged and replugged Dlink switch … / 957 kbps down, 10.1 Mbps up					20190923
				11:20		11:23	Removed Dlink, 1.17/11.8 Mbps down/up; Rebooted CradlePoint …; 37.0/20.1 Mbps down/up					20190923
		24	Tu		16:39			NetWorx Speed Meter T450s Hourly: Download speeds dropped again <=1.4 Mbps					20190924
		25	We	~	04:00	~	04:20	Rebooted CradlePoint; NetWorx 27.4/15.7 Mbps down/up … / Disabled "WiFi: AndroidHotspot3365" in Internet / Connection Manager; Also disabled WiPipe Central Services	Z1					20190925
		27	Fr		02:29		05:10	NetWorx Speed Meter tests (02:29 and 03:29), speeds have dropped again; Rebooted CP_1 (04:05); System Settings / Administration > System Logging > Logging Level: Info->Debug; Clear Log; Speeds have not substantially improved (04:12); Rebooted CP_1, but speeds have not improved; Powered down and restarted entire network, but speeds have not improved, in fact, they are worse; T450s rebooted; NetWorx Speed Meter stopped working; Speedtest.exe 6.6/9.4 Mbps down/up; NetWorx Speed Meter on T400s 976 Kbps down; T450s direct to TurboNet PoE injector, speedtest.exe 3/6 Mbps down/up; To Keith and Mark					20190927
				~	12:00			Mark and Brandon stopped by to test: Their laptop direct to PoE injector at first showed reasonably good speeds (32/12 Mbps down/up); T450s direct to PoE injector poor speeds, multiple speedtest.exe, 2-6 Mbps; Then Brandon's laptop again and poor speeds (2-6 Mbps, some long pings); They went on the roof and aimed the antenna up a bit; No improvement; But these tests confirm it isn't in my network or the CradlePoint; Problem is most likely either cabling issues (run to the roof) or the tree in the way really does matter; TODO "Drop the tree or move the antenna to the S end of the shop roof (requires new cable)"					20190927
2019	Oct	24	Th	~	09:50	~	13:50	Very poor internet speeds for 5 days (Kbps); Rebooted CP_1 immediate improvement (Mbps) …; Tested again, poor speeds (Kbps)					20191024
		30	We					Very poor speeds lately; Rebooting CP_1 sometimes helps slightly, but poorest on windy days					20191030
2019	Nov	2					Again, slight improvement with CP_1 reboot					20191102
		7	Th				06:58	I discovered part of the problem with poor speeds (since September): Ubiquiti Tough Switch stopped working and internet lost entirely until I restarted it (see notes on white sheet stored with Ubiquiti); Removed Ubiquiti entirely (I don't need it or something like it until and if I get all 5 security cameras installed) ...; Tested internet speeds with SpeedTest.exe and immediately saw 16ms pings and 48/59 Mbps down/up (wow!); The tree might still be an issue, but for now all looks good	Z1 WS					20191107
				07:22		07:37	Speedtest.exe T450s: 14ms, 9.1/7.3 Mbps down/up …; 284ms, 4.6/5.6; There's still something else going on, it could be CP_1 or the tree and the windy day; Rebooted CP_1 …					20191107
				07:44		07:55	Speedtest.exe 60ms 2.8/3.9 Mbps …; T450s NetWorx is working again (Ubiquiti was the problem), 36ms 40.1/41.6 Mbps down/up					20191107
				08:21			T400s NetWorx is working again (yes, bad Ubiquiti!, but had to reboot T400s 1st), 38ms 29.9/17.8 Mbps down/up					20191107
2019	Dec	4	We	~	18:00			Cut down the tree, video; Notes on NetWorx Speed Meter results for 11/7 to date: results vary widely, but most of the Average download speeds are less than 1 Mbps; Ocassional (but rare) very good speeds down/up >30/20 Mbps; During the past few days it's been 228-814 kbps down and 1-13 Mbps up	IMG					20191204
		5	Th		03:47	~	06:50	TurboNet down; ~04:10 rebooted network (still down, switched to hotspot) … / Hotspot off & TurboNet OK (it came back up sometime in the past 2-1/2 hours)					20191205
				06:54		06:56	NetWorx Speed Meter T450s 9.4/21.3 Mbps down/up … / T400s 10.0/10.1 Mbps down/up (I'm now getting what I pay for)					20191205
		8	Su		01:18		01:38	TurboNet down for 20 Mins (good weather)					20191208
2020	Jan	7	Tu		14:17	~	15:00	NetWorx Speed Meter T450s <1Mbps down for days (since 1/5/20 16:11) / Restarted Network stuff (power off/on) and 24-50 Mbps down, 13-21 Mbps up … / Brandon on roof and re-aimed antenna, 30-48 Mbps down, 13-19 Mbps up					20200107
2020	Feb	4	Tu	~	11:30		14:23	NetWorx Speed Meter T450s <=1Mbps since yesterday 08:50; Cold restart of Cradlepoint (no improvement) / Cold restart of all network equipment (no improvement); MMS to Mark & Keith … / No response from Mark or Keith but speeds are good again	SMS					20200204
		25	Tu		02:06		05:32	TurboNet down for 3 Hrs 25 Mins					20200225
2020	Mar	12	Th		00:16		06:48	TurboNet down for 6 Hrs 31 Mins					20200312
		17	Tu		01:33		02:18	TurboNet down for 44 Mins 43 Secs					20200317
		18	We		01:19		01:32	TurboNet down for 12 Mins 42 Secs					20200318
2020	Apr	6	Mo		08:11		08:28	TurboNet down for 17 Mins					20200406
2020	May	8	Fr					While onsite at LWT Keith reported that he was onsite at RW "a few weeks ago"	B54					20200508
		19	Tu		15:12		15:30	TurboNet down for 17 Mins					20200519
2020	Jun	4	Th		09:33		11:22	TurboNet down for 1 Hr 49 Mins; SMS to/from Mark and Keith; Mark says “transformer blew and RHS has no power” and “… We’ll do that [RHST] with one [W100] you’re building”	SMS L12					20200604
		9	Tu		09:36			TurboNet down for 26 Hrs 58 Mins; When I called Mark on the morning of We6/10 he said “Fiber damaged, should be fixed in a few hours” (~Noon)					20200609
		10	We				12:35					20200610
		16			11:14		13:17	TurboNet down for 2 Hrs 2 Mins; I didn’t notice this one, saw it Th7/2 in the Connection Monitor logs					20200616
		25	Th					From Keith: New fixed IP	EML TW6-10 Z1					20200625
		27	Sa		10:02			To Keith: “I’ll update … in the next few days.”					20200627
2020	Jul	1	We		15:38		18:27	Internet down …; To Keith and Mark; From Mark	SMS Z1					20200701
		2	Th		00:55	~	02:15	Tshooting CP_1 configuration; DHCP works, static IPs don’t work; EML to Keith and Mark; TODO	SSC EML TW6-10 Z1					20200702
				08:13	~	18:00	Internet down …; I noticed that it was down; Set static IP and internet is up	Z1					20200702
		16	Th	~	04:00	~	07:11	Internet working but very slow: I don’t know when this started, but I noticed it 1st thing in the morning @ ~04:00; Rebooted CP_1 (no improvement); Unplugged/plugged TurboNet device (no improvement); Had to use iPhone hotspot (and I burned almost 200MB of data allowance); CP_1 not able to send all alerts, test emails OK (ethernet and iPhone connections), rebooting CP_1 may have helped (but both ethernet and iPhone connections do have problems with lost packets, etc.); 06:34 & 06:40 SMSs to Keith & Mark; 06:36 Speedtest fails (can’t connect); 07:11 Speedtests 19ms 31/14 Mbps down/up and 30 ms 35/24 Mbps down/up; Total “outage” at least 3.25 Hrs	SMS					20200716
		22	We	~	04:00	~	04:45	Internet working but slow: I noticed it 1st thing in the morning @ ~04:00; NetWorx Speed Meter results mostly under 1Mbps up/down since yesterday afternoon, last test 04:20 800/749 Kbps down/up; Rebooted CP_1 (no improvement, 04:39 610/601 Kbps); Unplugged/plugged TurboNet device (slight improvement, 04:44 1.85/3.66 Mbps down/up)					20200722
2020	Aug	10	Mo	~	12:24	~	13:31	TurboNet down for 1 Hr 7 Mins; There were thunderstorms in the area; I switched to iPhone hotspot; Restoration time by "connected" email from CP	EML					20200810
		12	We	~	00:42	~	01:15	TurboNet down for 33 Mins; I was asleep so I didn't notice it until looking at NetWorx Connection Monitor log					20200812
				~	21:30	~	21:45	Internet working but slow: I noticed it 1st thing upon resuming work @ ~21:30; Long pings 70-200ms; Browsing impossible; NetWorx Speed Meter test fails; GS having connection issues resolving to mediator ...; Then suddenly OK, browsing OK, Speed Meter OK (33/6 Mbps down/up)					20200812
2020	Sep	14	Mo	~	04:28	~	04:52	TurboNet down for 24 Mins; I didn't notice it until looking at NetWorx Connection Monitor log on Fr9/18					20200914
		27	Su	~	12:19	~	12:36	TurboNet down for 17 Mins; Thunderstorms in the area					20200927
2020	Oct	1	Th					Many (~15x) short (2-12 mins) disconnections last night from ~22:00 to 04:00 for a total of about 1 hour Offline					20201001
		8	Th	~	12:13	~	15:02	Phone call from Mark Webb: He wants a favor; Calls to Mark; They were planning on going to RW earlier and so they had PWSD unlock the gate and the ladder; Please go lock it and text when done; Spoke briefly of fall maintenance (which I haven't had time or inclination to start on, but Mark appears to be open); I told him I would go do it, but then after developments in my day and consideration I sent an SMS "Mark, I'm sorry, but something has come up and I won't be able to lock up at Tower today. I'll go there first thing in the morning if it's still not done, maybe seven or 8 AM."; I didn't hear any more about it after that	SMS					20201008
		9	Fr	~	01:15	~	01:42	TurboNet down for 27 Mins; I didn't notice it until looking at NetWorx Connection Monitor log on We10/21					20201009
		21	We	~	00:24	~	00:38	TurboNet down for 14 Mins					20201021
2020	Nov	19		~	15:03	~	15:42	TurboNet down for 39 Mins; This event noticed in T450s Connection Monitor 11/26/20; T400s CM didn't show it, but that may be because I started to shut down T400s when I'm not planning on using it for long periods of time (more than 5 hours)					20201119
2021	Jan	6	We					TurboNet down for 10 mins, 15 mins and 13 mins; And there are many other 1-2 min outages which I do not record here (I only record them if 10' or longer)					20210106
		7	Th					SMSs to/from Mark and Keith concerning frequent drops in the past week and Keith said it was due to interference from military flying and "I think I might have got it fixed" [Note added 2/1/21: It was fixed, there were no more drops after that until 1/31/20 when there was a ~1 min drop]	SMS					20210107
	Mar	8	Mo	~	12:15			IP and credentials for Netonix rec'd from Keith; 10.1.20.41, admin, admin; Warning voltage 12->13; SMTP configured and tested; Float is 14.2v as per Netonix (probably erroneously high, not calibrated yet); Load watts 24.8-33.0 (28.9 mean, not calibrated yet)	EML TM21S DBT					20210308
		10	We	~	14:30	~	16:25	Onsite for contracted maintenance: 14.2v Float and 28.9w Load; See B54 for details	TM21S SMS EML SSC					B54					WP3	20210310
		11	Th	~	08:45	~	09:00	Onsite to reapply AC power and shoot a photo showing the watering system in use; See B54 for details	TM21S SMS SSC IMG					20210311
				11:19			Screenshot of Netonix Input Voltage graph showing Bulk/Absorption transition; See B54 for details	TM21S SSC					20210311
				13:36			Screenshot of Netonix Input Voltage graph showing transition from Absorption to Float; See B54 for details					20210311
	Jun	11					37 min power outage; Low voltage warning; Screenshots, 13.3v Float and 14.4v Absorption; Email to Mark and Keith with photo of tree near the tower that was exploded and destroyed by lightning	EML SSC IMG					20210611
	Aug	4	We	~	16:46			TurboNet down; 16:56 SMS to K&M; 17:13 call to Keith (he did not make any changes to my account, even though lately I dropped the fixed IP and went back to basic service @ $55/month starting August); 17:42-17:43 SMS from/to Mark "Tower down", "Which one?", "Rich. City" (RCWT), "ETA on restoration?", "Chill out", "Power issues"; See RCWT ...	L3 SMS					20210804
		5	Th			~	08:30	TurboNet internet was restored while I was at RCWT; Total outage ~13.75 Hours; But upon returning to the shop at about 09:15 I had no internet on the LAN because the CradlePoint needed to be replaced; This took two days, but I had internet restored on the LAN by Thursday evening; See CP_1 and CP_2	Z1 Z2 CPSN					20210805
		24	Tu	~	20:12	~	21:18	TurboNet down for 1 hr 6 mins; 21:12 SMS to Keith and Mark; No response; 21:49 SMS to Keith and Mark to let them know it was back up at 21:18	SMS					20210824
	Sep	8	We	~	00:45	~	00:58	TurboNet down for ~13 mins					20210908
		13	Mo	~	18:08	~	18:24	TurboNet down for ~16 mins					20210913
	Oct	15	Fr	~	12:00	~	12:47	TurboNet down for ~47 mins; 12:17 SMSs to Keith & Mark; 12:32 Keith "Power outage Richmond"; 12:33 Mark "They think it'll be up in about an hour."; More SMSs; 13:01 SMS to Keith and Mark "Rayville up 12:47"; 13:07 SMSs to Keith and Mark "So, which site in the link from your backbone to me was not battery backed?"; 13:08 Mark "Richmond city feeds to Reaville that was the first battery back up you put in"; 13:09 to Mark "But that back up system was working"; 13:17 SSC RW (could not log in to RCWT); 13:19 Called Brian Long (no power loss @ RHS); 13:22-13:25 Call to Mark; 14:12 Mark "They thought it was down for about an hour"; 14:14-14:19 Call to Mark (evidently not all of their equipment is being run from PoE from the DC Netonix on the W50)	SMS SSC TM21F L3					20211015
		22	Fr	~	16:13	~	17:11	TurboNet down for ~58 mins; 16:55 SMSs to Keith & Mark; 16:56 Call from Mark "probably RCWT, he called the water department to see if power down, otherwise need to reset Netonix, he'll let me know (hinted he might have me go, he's on the way to the airport)"; 17:03 SMS from Mark "power outage"; 17:13 SMS from Mark "Let me know what works in your schedule to go to Richmond city and see why the battery back up isn't keeping everything alive thanks"; 17:28 SMSs to Mark & Keith "Up @ 17:11"; 17:37 SMS from Mark "Ok good"	SMS TM21F L3					20211022
		24	Su	~	16:44	~	17:40	TurboNet down for ~56 mins; Because it was Sunday, I did not contact Mark and Keith, besides, it was probably caused by a power failure at RCWT	TM21F L3					20211024
	Nov	23	Tu	~	00:45	~	01:50	TurboNet down for 1 hr 5 mins					20211123
		24	We	~	00:32	~	00:45	TurboNet down for 13 mins; I continue to not bother to record any outages less than 10 mins, but there have been a lot of them lately; I spoke with Keith yesterday, RCWT is an an area of Richmond that has had a lot of power problems; The battery backup system at RCWT does not include all of the equipment at the site, and we still haven't had time to go see what can be done about it					20211124
	Dec	15	We	~	18:44			TurboNet down ...; See RCWT Emergency for more details	TM21F EML L3					20211215
		16	Th	~	15:20	~	18:10	Onsite at RCWT; Internet restored for brief periods while testing and swapping out batteries & power supplies ... / Internet fully restored @ 18:10; Total outage ~23 Hours	TM21F EML L3					20211216
				Procedure/practice change: I've been recording only the internet outages that go longer than 10 mins, but will start to record them all; The vast majority of these incidents are caused by RCWT or RHST outages/disruptions, and I need to watch more carefully; Entries can be made "after the fact" from printouts of Networx CM SSC, CP or Netonix emails; All we need here is outage length (mins, hours) (bold if >2m) and references					20211216
		18	Sa	~	09:57	~	10:00	~2m; CradlePoint	TM21F EML					20211218
		23	Th	~	10:27	~	10:30	~2m; Netonix; CradlePoint; Logged into Netonix, cleared log, no power losses in past 24 hours, Float 13.7-13.8v					B54					WP3	20211223
		27	Mo	~	06:55			Logged into Netonix: Load ~56w; Float 13.78v (OK for <20⁰C)	TM21F SSC					20211227
		31	Fr					[L1-3 L6-7 L10-16] 20211231.3 Invoice & Report - Fall 2021 Maintenance.pdf / RW Not Maintained as Hoped (last visit 3/10/21)	TM21F DBT					20211231
2022	Jan	4	Tu					[L1-3 L6-7 L10-16] 20220104.0 Email to Mark, Keith & Brad 'Invoice and Report - Fall 2021 Maintenance'.pdf					20220104
		5	We	~	11:14	~	11:16	~2m; NetWorx; Netonix; CradlePoint / Logged into Netonix, no power losses in past 24 hours, Load ~56w, Float 14.0v	TM22 SSC EML					B54					WP3	20220105
				~	13:39	~	13:41	~2m; NetWorx; CradlePoint					20220105
		12	We	~	12:00	~	12:02	~2m; NetWorx; Netonix; CradlePoint					20220112
		15	Sa	~	08:22	~	08:24	~2m; CradlePoint	TM22 EML					20220115
		19	We	~	01:46	~	01:48	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220119
		20	Th	~	01:10	~	01:12					20220120
				~	01:37	~	01:39	~2m; NetWorx	TM22 SSC					20220120
				~	03:12	~	03:14	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220120
				~	03:37	~	03:39	~2m; NetWorx	TM22 SSC					20220120
		28	Fr	~	17:06	~	17:08	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220128
		31	Mo	~	02:19	~	02:21					20220131
				~	02:29	~	02:36	~7m; NetWorx	TM22 SSC					20220131
2022	Feb	7	Mo	~	15:30	~	15:33	~3m; NetWorx; CradlePoint	TM22 SSC EML					20220207
		9	We	~	12:53	~	13:26	~1h48m; NetWorx T400s; Most likely spurious (not a real outage) as it was not detected by T450s or CradlePoint	TM22 SSC					20220209
				~	15:15	~	15:16	~2m; NetWorx T400s; Most likely spurious (not a real outage) as it was not detected by T450s or CradlePoint					20220209
		14	Mo	~	19:41	~	19:43	~2m; CradlePoint	TM22 EML					20220214
		15	Tu	~	00:49	~	00:51					20220215
		18	Fr	~	12:28	~	12:30	~2m; NetWorx; Netonix; CradlePoint	TM22 SSC EML					20220218
				~	12:33	~	12:35	~2m; NetWorx; Netonix					20220218
		26	Sa	~	13:27	~	13:29	~2m; NetWorx; CradlePoint					20220226
				~	15:27	~	15:29					20220226
		27	Su	~	13:22	~	13:34	~13m; NetWorx; CradlePoint					20220227
				~	15:57	~	16:01	~4m; NetWorx; CradlePoint					20220227
		28	Mo	~	11:33	~	11:34	~2m; NetWorx; CradlePoint					20220228
				~	11:41	~	11:51	~10m; NetWorx	TM22 SSC					20220228
				~	12:17	~	12:23	~6m; NetWorx					20220228
				~	12:40	~	13:07	~27m; NetWorx; CradlePoint	TM22 SSC EML					20220228
				~	13:33	~	13:55	~22m; NetWorx; CradlePoint					20220228
				~	13:59	~	14:31	~31m; NetWorx	TM22 SSC					20220228
				~	14:42	~	14:50	~8m; NetWorx; CradlePoint	TM22 SSC EML					20220228
				~	15:02	~	15:51	~49m; NetWorx; CradlePoint					20220228
				~	16:28	~	16:30	~2m; NetWorx; Mo2/28 Totals (9) outages ~157m (2.6h)	TM22 SSC					20220228
2022	Mar	1	Tu	~	15:30	~	15:39	~10m; NetWorx; CradlePoint	TM22 SSC EML					20220301
				~	15:49	~	15:50	~2m; NetWorx	TM22 SSC					20220301
				~	15:54	~	15:55					20220301
				~	15:59	~	16:07	~6m; NetWorx					20220301
				~	16:12	~	16:32	~11m; NetWorx; CradlePoint	TM22 SSC EML					20220301
				~	16:43	~	17:05	~23m; NetWorx	TM22 SSC					20220301
				~	16:58	~	17:01	Phone call from Mark: He asked me to go check the lock on the gate; He revealed that Keith has been working on the omni, and had changed the end on the cable at the bottom of the tower / This explains the increased frequency and duration of outages since Su2/27	TM22					20220301
				~	17:08	~	17:25	~18m; NetWorx	TM22 SSC					20220301
				~	17:30	~	17:50	Onsite: Electrolyte checked and filled / Found that at some point in the past they had caulked some of the vent holes / Pulled cardboard/caulk from 1-1/2" hole in front left and wrote with felt tip "<-- Vent Hole" "Do Not Block" / Battery 14.03vF at 75⁰F (slightly high for that temperature, Genasun has not reset lately) / Load ~1.3aE (18w) (down significantly from 56w observation We1/5); No cleaning was performed	TM22					B54					WP3	20220301
				~	17:33	~	17:39	~6m; NetWorx; CradlePoint; Tu3/1 Totals (8) outages ~78m (1.3h)	TM22 SSC EML					20220301
				~	18:12	~	18:13	Logged into Netonix: Screenshots show Battery 14.05v and Load ~18w (good agreement with onsite measurements); Netonix Input Voltage calibration is good	TM22 SSC					20220301
		2	We	~	11:01	~	11:14	~13m; NetWorx; Netonix; CradlePoint; This outage happened while "the guys" (Keith?) were onsite / 20220302 Report & Invoice - Rayville Emergency and Maintenance.doc [emailed to Mark and Keith Tu5/24]	TM22 SSC EML DBT					20220302
		13	Su	~	00:55	~	00:57	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220313
		28	Mo	~	10:59	~	11:05	~6m; NetWorx; CradlePoint					20220328
				~	13:05	~	13:10	~5m; NetWorx; CradlePoint					20220328
2022	Apr	6	We	~	02:18	~	02:24	~6m; NetWorx; CradlePoint					20220406
		16	Sa	~	08:41	~	08:44	~3m; NetWorx; CradlePoint					20220416
		21	Th	~	13:34	~	13:37					20220421
				~	13:40	~	13:43	~3m; NetWorx	TM22 SSC					20220421
		24	Su	~	09:49	~	19:20	No charging: Netonix notification EML 09:52; Logged into Netonix, SSCs; Load ~18w (battery should last ~48 hrs) ... / Charging resumed (not sure yet why)	TM22 EML SSC					B54					WP3	20220424
		25	Mo	~	00:00			No charging again: Netonix notification EML 00:06; SSCs, 08:00 shows the entire event so far					20220425
		26	Tu	~	07:00			Logged into Netonix: No charge in past 24h, now ~31h on battery ... / Mark confirmed I should go onsite, he will call PWSD for access	TM22 SSC					20220426
				~	13:40	~	13:45	Onsite, but gate is still locked; SMSs to/from Mark	TM22 SMS					20220426
				~	14:40	~	15:35	Onsite #2: No AC Power; Battery ~19degC; Wasp spray / Power restored by wiggling plug in PWSD's exterior outlet; Charging, Netonix notification EML at threshold 13.0v as V came up; PWSD's exterior plug is NOT waterproof, rear hole plug is missing, top conduit entrance is not waterproof; Called Mark, recommended removing plug and using wire nuts, he'll set up a time to meet onsite with PWSD, probably next week; Replaced zip tie on W100 output; Load ~18w	TM22 EML SMS SSC					B54					WP3	20220426
		27	We	~	07:00	~	12:40	Logged into Netonix: SSC shows battery reached Float yesterday ~21:40 (unfortunately there was a Netonix "fart" to ~90v right before I made the SSC, so the vertical scale makes it difficult to see what happened during recovery) ... / Netonix rebooted (high on memory usage) / 20220427 Report & Invoice - Rayville Power Failure Emergency.doc [emailed to Mark & Keith Th6/23]	TM22 SSC DBT					20220427
2022	May	16	Mo	~	10:00	~	16:46	Very poor internet; Intermittent performance; ~750ms pings; Browsing impossible ...; Contacted Keith and Mark / Keith rebooted something that fixed it / Unuseable performance ~6 hrs but connection lost for only 2m during reboot; NetWorx; CradlePoint	TM22 SSC EML					20220516
		24	Tu					20220302 Report & Invoice - Rayville Emergency and Maintenance.pdf / 20220524 Email to Mark & Keith 'Report & Invoice - Rayville Water Tower'.pdf	TM22 DBT EML SMS					20220524
2022	Jun	20	Mo	~	00:06	~	00:08	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220620
				~	02:43	~	02:46	~3m; NetWorx; CradlePoint					20220620
		23	Th	~	09:16			Netonix rebooted: High Memory Usage 123.3/128 MB	TM22					20220623
				20220427 Report & Invoice - Rayville Power Failure Emergency.pdf / 20220623 Email to Mark & Keith 'Report & Invoice - Rayville Power Failure'.pdf	TM22 DBT EML					20220623
		27	Mo	~	04:47	~	04:49	~2m; NetWorx T450s only (no CP notification)	TM22					20220627
		28	Tu	~	04:19	~	04:21					20220628
				~	08:02			SMS to Mark concerning scheduling for onsite visits to TLNB/WWT/RCWT: / Shared CO trip "gone" days and "Rayville will have to be done after I return" (fix to bad exterior outlet)	TM22 SMS					20220628
				~	09:34	~	09:46	~11m; NetWorx; CradlePoint	TM22 SSC EML					20220628
				~	17:50	~	18:14	~24m; NetWorx; CradlePoint; Caused by my onsite work at RCWT					20220628
2022	Jul	1	Fr	~	07:51	~	07:54	~3m; CradlePoint	TM22 EML					20220701
		4	Mo	~	13:36	~	13:40	~4m; NetWorx; CradlePoint	TM22 SSC EML					20220704
		11	Mo	~	02:34	~	02:37	~3m; CradlePoint	TM22 EML					20220711
				~	21:40	~	21:45	~5m; NetWorx; CradlePoint	TM22 SSC EML					20220711
				~	22:13	~	22:18	~5m; NetWorx	TM22 SSC					20220711
		12	Tu	~	04:41	~	10:39	~5h 58m; NetWorx; CradlePoint	TM22 SSC EML					20220712
				~	15:47	~	15:52	~5m; NetWorx; CradlePoint					20220712
				~	21:54	~	22:09	~15m; NetWorx; CradlePoint					20220712
		13	We	~	12:14	~	12:18	~4m; NetWorx; CradlePoint					20220713
				~	15:52	~	15:55	~3m; NetWorx; CradlePoint					20220713
				~	22:07	~	22:12	~5m; NetWorx; CradlePoint					20220713
				~	22:39	~	22:42	~3m; NetWorx	TM22 SSC					20220713
		14	Th	~	21:21	~	21:27	~6m; NetWorx; CradlePoint	TM22 SSC EML					20220714
		15	Fr	~	19:48	~	19:57	~9m; NetWorx	TM22 SSC					20220715
		16	Sa	~	22:47	~	22:53	~6m; NetWorx; CradlePoint	TM22 SSC EML					20220716
		17	Su	~	10:26	~	14:53	~4h 26m; NetWorx; CradlePoint					20220717
				~	15:41	~	15:43	Call from Mark (while I was travelling in CO): Rayville was down; Keith onsite and "reset everything" / [Notes added We7/20: There were no power failures at shop during entire trip to CO 7/3-18 / There were no Netonix notifications that AC power had been lost at RW]	TM22					20220717
		18	Mo	~	08:44	~	08:51	~7m; CradlePoint	TM22 EML					20220718
				~	11:56			Screenshot of Netonix (no reboots for >6 days); Float 13.3vN; Load 23wN	TM22 SSC					20220718
				~	18:06	~	18:21	~15m; NetWorx; CradlePoint	TM22 SSC EML					20220718
		20	We	~	20:31	~	20:42	~11m; NetWorx; CradlePoint					20220720
		21	Th	~	09:25	~	09:28	~3m; NetWorx; CradlePoint					20220721
				~	11:05	~	11:35	With Keith at shop to discuss Power Cable Assembly for CFS / We also discussed his recent onsite visit to RW (Su7/17): / According to Keith the RW equipment did lose AC power as he said he saw the W100 flash red (idling on battery) / But we received no Netonix notification, so I would assume the loss was only temporary while Keith was there fiddling with stuff not knowing what he was trying to do; Keith didn't know about the bad outlet issue (either Mark hadn't told him or he had forgotten); We still need to visit RW with PWSD present in order to hardwire the defective "outdoor" outlet	T48-4 L18					20220721
		24	Su	~	18:59	~	19:09	~11m; NetWorx; CradlePoint	TM22 SSC EML					20220724
				~	21:15	~	21:20	~5m; NetWorx; CradlePoint					20220724
		25	Mo	~	11:58	~	12:02	~4m; NetWorx; CradlePoint					20220725
		26	Tu	~	18:19	~	18:22	~3m; NetWorx; CradlePoint					20220726
				~	21:38	~	21:42	~4m; NetWorx; CradlePoint					20220726
				~	22:19	~	22:34	~15m; NetWorx	TM22 SSC					20220726
		28	Th	~	02:14	~	02:18	~4m; NetWorx; CradlePoint	TM22 SSC EML					20220728
				~	20:12	~	20:24	~12m; CradlePoint	TM22 EML					20220728
				~	22:39	~	22:46	~7m; CradlePoint					20220728
		29	Fr	~	21:40	~	21:46	~6m; NetWorx; CradlePoint	TM22 SSC EML					20220729
				~	22:20	~	22:25	~5m; NetWorx	TM22 SSC					20220729
		30	Sa	~	22:39	~	23:44	~6m; NetWorx; CradlePoint	TM22 SSC EML					20220730
		31	Su	~	13:43	~	13:47	~4m; NetWorx; CradlePoint					20220731
				~	19:22	~	19:24	~3m; NetWorx; CradlePoint					20220731
2022	Aug	1	Mo	~	17:11	~	17:17	~6m; NetWorx; CradlePoint					20220801
				~	19:59	~	20:09	~11m; NetWorx; CradlePoint					20220801
		2	Tu	~	23:12	~	23:24	~12m; CradlePoint	TM22 EML					20220802
		3	We	~	06:40	~	06:43	~3m; NetWorx; CradlePoint	TM22 SSC EML					20220803
				~	10:11	~	10:14					20220803
				~	15:33	~	15:40	~6m; NetWorx; CradlePoint					20220803
				~	20:21	~	20:31	~10m; NetWorx; CradlePoint					20220803
		4	Th	~	01:37	~	01:49	~13m; NetWorx; CradlePoint					20220804
				~	12:13	~	12:18	~5m; NetWorx; CradlePoint					20220804
				~	15:11	~	15:16					20220804
				~	15:39	~	15:54	~14m; NetWorx	TM22 SSC					20220804
				~	16:44	~	16:57	~13m; NetWorx; CradlePoint	TM22 SSC EML					20220804
				~	20:12	~	20:17	~5m; NetWorx; CradlePoint					20220804
				~	21:29	~	21:33	~4m; NetWorx; CradlePoint					20220804
				~	21:54	~	21:59	~5m; NetWorx	TM22 SSC					20220804
		5	Fr	~	04:19	~	04:29	~10m; NetWorx; CradlePoint	TM22 SSC EML					20220805
				~	10:29	~	10:31	~3m; NetWorx; CradlePoint					20220805
				~	12:04	~	12:14	~10m; NetWorx; CradlePoint					20220805
2022	Sep	1	Th	~	11:19	~	11:21	~2m; NetWorx; Short, not seen T450s, no CradlePoint notification EML	TM22 SSC					20220901
		2	Fr	~	01:00	~	01:03	~4m; NetWorx; CradlePoint	TM22 SSC EML					20220902
				~	01:20	~	01:46	~25m; NetWorx	TM22 SSC					20220902
				~	01:50	~	01:57	~6m; NetWorx					20220902
		4	Su	~	13:45	~	15:41	~1h 56m; NetWorx; CradlePoint	TM22 SSC EML					20220904
		6	Tu	~	03:32	~	03:38	~5m; NetWorx; CradlePoint					20220906
		7	We	~	16:44	~	16:46	~3m; NetWorx; CradlePoint					20220907
		8	Th	~	10:34	~	10:43	~9m; NetWorx; CradlePoint; Outage caused by Brandon and Dakota upgrade of rooftop Ubiquiti to Mimosa	TM22 SSC EML L					20220908
				[L1/3/10/14-18] Brandon and Dakota at Shop: General discussion / TurboNet Orders Pending List (see TM22 and L17 links to sites on list) / I tried to get them interested in power systems maintenance	TM22 L17					20220908
		12	Mo	~	01:05	~	01:07	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220912
				~	03:17	~	03:18	~2m; NetWorx T450s (not detected T400s); CradlePoint					20220912
				~	04:29	~	04:30	~2m; NetWorx; CradlePoint					20220912
				~	05:04	~	05:10	~5m; NetWorx	TM22 SSC					20220912
				~	05:47	~	05:50	~2m; CradlePoint; Short, not seen by NetWorx on T400s and T450s	TM22 EML					20220912
				~	06:17	~	06:18	~2m; NetWorx	TM22 SSC					20220912
				~	06:23	~	06:24	~2m; NetWorx T400s (not detected on T450s)					20220912
				~	06:53	~	06:56	~3m; NetWorx; CradlePoint	TM22 SSC EML					20220912
				~	07:41	~	07:43	~2m; NetWorx	TM22 SSC					20220912
		13	Tu	~	00:10	~	00:12	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	00:46	~	00:48	~3m; NetWorx	TM22 SSC					20220913
				~	02:16	~	02:20	~2m; CradlePoint; Short, not seen by NetWorx on T400s and T450s	TM22 EML					20220913
				~	02:58	~	03:00	~2m; NetWorx	TM22 SSC					20220913
				~	03:34	~	03:37	~3m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	04:10	~	04:12	~2m; NetWorx	TM22 SSC					20220913
				~	04:46	~	04:48	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	05:22	~	05:24	~2m; NetWorx	TM22 SSC					20220913
				~	05:58	~	05:59	~2m; NetWorx T400s (not detected on T450s)					20220913
				~	06:34	~	06:35	~2m; NetWorx T400s (not detected on T450s); CradlePoint	TM22 SSC EML					20220913
				~	07:16	~	07:19	~3m; NetWorx	TM22 SSC					20220913
				~	09:05	~	09:07	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	09:39	~	09:42	~3m; NetWorx T400s (not detected on T450s)	TM22 SSC					20220913
				~	09:49	~	09:50	~2m; NetWorx T450s (not detected on T400s)					20220913
				~	10:33	~	10:35	~3m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	20:47	~	20:50	~2m; CradlePoint; Short, not seen by NetWorx on T400s and T450s	TM22 EML					20220913
				~	22:40	~	22:42	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220913
				~	23:34	~	23:35	~2m; NetWorx	TM22 SSC					20220913
		14	We	~	00:10	~	00:12	~2m; NetWorx; CradlePoint	TM22 SSC EML					20220914
				~	16:18			Speedtest.net T450s: 50ms, 12.1 Mbps down, 78.0 Mbps up / Shown to Geri Kincanon and his son Drake (potential TurboNet customers, Rayville)	DNT					20220914
		15	Th					RW mentioned in Report (discussed AC power problems with Keith Th7/21): / 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 DBT EML L18					20220915
		17	Sa	~	09:07	~	09:11	~4m; NetWorx; CradlePoint	TM22 SSC EML					20220917
		23	Fr	~	13:37	~	13:40	~3m; NetWorx; CradlePoint					20220923
		24	Sa	~	04:29	~	05:31	~2m; CradlePoint; Short, not seen by NetWorx on T400s and T450s	TM22 EML					20220924
				~	05:09	~	05:11	~2m; NetWorx	TM22 SSC					20220924
		25	Su	~	03:58	~	04:00	~2m; CradlePoint (T400s/T450s OFF)	TM22 EML					20220925
				~	05:04	~	05:06					20220925
				~	06:52	~	06:55	~3m; CradlePoint (T400s/T450s OFF)					20220925
		26	Mo	~	07:50	~	07:53	~2m; CradlePoint (T400s/T450s OFF)					20220926
2022	Oct	4	Tu	~	20:34	~	20:36	~2m; NetWorx (T450s, T400s did not detect); CradlePoint	TM22 SSC EML					20221004
		8	Sa	~	04:09	~	04:12	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221008
				~	06:50	~	06:52	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221008
				~	07:45	~	07:47	~3m; NetWorx	TM22 SSC					20221008
				~	08:33	~	08:35	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221008
		10	Mo	~	01:33	~	01:36	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221010
				~	02:39	~	02:42					20221010
				~	03:51	~	03:54					20221010
				~	05:03	~	05:06					20221010
				~	06:33	~	06:36					20221010
				~	07:39	~	07:42	~3m; CradlePoint (T400s/T450s OFF); There may have been more RW outages as CP only sends 1 email per hour					20221010
				~	10:15	~	10:17	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221010
		14	Fr	~	06:59	~	07:00					20221014
		24	Mo	~	10:54	~	11:05	~12m; NetWorx; CradlePoint					20221024
		26	We	~	00:52	~	00:55	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221026
				~	02:17	~	02:20					20221026
				~	05:23	~	05:26					20221026
				~	08:53	~	08:55	~2m; CradlePoint (T400s/T450s OFF); There may have been more RW outages as CP only sends 1 email per hour					20221026
		28	Fr	~	18:52	~	18:55	~3m; CradlePoint (not detected by NetWorx, T400s/T450s ON)					20221028
		31	Mo	~	01:22	~	01:24	~3m; NetWorx; CradlePoint	TM22 SSC EML					20221031
				~	02:34	~	02:35	~2m; NetWorx; CradlePoint					20221031
				~	03:45	~	03:47					20221031
				~	04:16	~	04:18	~2m; NetWorx	TM22 SSC					20221031
2022	Nov	1	Tu	~	01:40	~	01:43	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221101
				~	04:16	~	04:19					20221101
				~	05:27	~	05:30					20221101
				~	06:51	~	06:53	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221101
				~	08:39	~	08:41					20221101
				~	16:25	~	17:53	~1h 28m; NetWorx; CradlePoint (2x)					20221101
				~	22:01	~	22:04	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221101
		10	Th	~	20:40	~	20:40	~1m; CradlePoint (T400s/T450s OFF)					20221110
		14	Mo	~	10:48	~	10:51	~3m; NetWorx (T400s, T450s saw ~4m; CradlePoint	TM22 SSC EML					20221114
		20	Su	~	10:18	~	10:34	~17m; NetWorx; CradlePoint					20221120
		23	We	~	10:13	~	11:09	~56m; NetWorx; CradlePoint					20221123
				~	10:53	~	11:13	SMSs to Mark and Keith "Rayville down ..."; SMSs from Keith "I would not worry about it ..."	TM22					20221123
				~	11:13	~	11:19	Logged into Netonix: Float 13.8v (past 24 hours) (OK, <15⁰C); Rebooted Netonix (high memory usage)					20221123
				~	11:19	~	11:59	~41m; NetWorx	TM22 SSC					20221123
				~	12:01	~	12:29	~28m; NetWorx					20221123
				~	12:35	~	12:39	~4m; NetWorx					20221123
				~	12:41	~	13:08	~27m; NetWorx					20221123
				~	13:10	~	14:49	~1h 39m; NetWorx					20221123
				~	20:16	~	20:23	~6m; NetWorx					20221123
				~	20:44	~	20:49	~5m; NetWorx					20221123
		28	Mo	~	03:34	~	03:39	~5m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221128
				~	05:09	~	05:12	~3m; CradlePoint (T400s/T450s ON but no CM)					20221128
				~	07:20	~	07:21	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221128
				~	08:08	~	08:10	~2m; NetWorx	TM22 SSC					20221128
		29	Tu	~	03:15	~	03:18	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221129
		30	We	~	13:40	~	13:42	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221130
2022	Dec	1	Th	~	06:09	~	06:11					20221201
		2	Fr	~	23:42	~	23:45	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221202
		3	Sa	~	03:03	~	03:06					20221203
				~	14:35	~	14:37	~2m; NetWorx; CradlePoint	TM22 SSC EML					20221203
		4	Su	~	06:00	~	06:02					20221204
		11	Su	~	02:47	~	02:50	~3m; CradlePoint (T400s/T450s OFF)	TM22 EML					20221211
		13	Tu	~	03:56	~	03:59					20221213
				~	13:02	~	13:18	~16m; NetWorx; CradlePoint	TM22 SSC EML					20221213
		28	We		12:00		14:00	Onsite at CFS, Discussions with Keith: He said the RCWT equipment is all running on backup (last time I was at RCWT on Tu6/28 there was equipment still running on AC) / We also discussed why the internet drops out at RW: Whiteman Air Force Base is 50 miles from Rayville "as the crow flies"; RW omni uses frequencies that the Air Force uses, and must drop to another channel when there is interference; Channel negotiation requires 2-3 minutes to complete, and after the interference is gone the omni will go back to the better channel which produces another 2-3m outage; This "theory" does not explain the longer outages, perhaps those are still being caused by power failures at RCWT (not all backed despite what Keith says) or LHS (no backup at tower)	T48-4 L18					20221228
2023	Jan	10	Tu	~	09:32	~	09:33	~2m; NetWorx; CradlePoint	TM23 SSC EML					20230110
				~	10:03	~	10:05	~3m; NetWorx	TM23 SSC					20230110
				~	10:14	~	10:16	~2m; NetWorx; Not seen by T450s					20230110
		29	Su	~	09:01	~	09:06	~4m; NetWorx; CradlePoint	TM23 SSC EML					20230129
	Feb	3	Fr	~	14:29	~	14:32	~3m; NetWorx; CradlePoint					20230203
		4	Sa	~	13:13	~	13:19	~6m; NetWorx; CradlePoint					20230204
		5	Su	~	03:40	~	03:42	~2m; CradlePoint (T400s/T450s OFF)	TM23 EML					20230205
		6	Mo	~	04:20	~	04:22					20230206
		8	We	~	06:33	~	06:36	~3m; CradlePoint (T400s/T450s OFF)					20230208
				~	07:35	~	07:38					20230208
		9	Th	~	05:27	~	05:30					20230209
		10	Fr	~	02:35	~	02:37	~2m; CradlePoint (T400s/T450s OFF)					20230210
		11	Sa	~	04:40	~	04:58	~18m; CradlePoint (T400s/T450s OFF)					20230211
				~	11:10	~	11:28	~18m; NetWorx; CradlePoint	TM23 SSC EML					20230211
		13	Mo	~	06:43	~	06:45	~2m; CradlePoint (T400s/T450s OFF)	TM23 EML					20230213
				~	07:57	~	08:03	~6m; NetWorx; CradlePoint	TM23 SSC EML					20230213
				~	08:08	~	08:12	~4m; NetWorx	TM23 SSC					20230213
				~	08:47	~	08:54	~7m; NetWorx					20230213
				~	08:59	~	09:06	~7m; NetWorx; CradlePoint	TM23 SSC EML					20230213
				~	09:12	~	09:17	~5m; NetWorx	TM23 SSC					20230213
				~	09:52	~	09:54	~2m; NetWorx T450s only (not detected on T400s)					20230213
				~	10:23	~	10:26	~3m; CradlePoint (not detected by CM)	TM23 EML					20230213
		15	We	~	03:11	~	03:13	~2m; CradlePoint (T400s/T450s OFF)					20230215
		16	Th	~	04:30	~	04:33	~3m; CradlePoint (T400s/T450s OFF)					20230216
		20	Mo	~	04:00	~	04:02	~2m; CradlePoint (T400s/T450s OFF)					20230220
		21	Tu	~	02:57	~	03:12	~15m; CradlePoint (T400s/T450s OFF)					20230221
				~	22:22	~	22:37					20230221
		24	Fr	~	00:54	~	00:57	~3m; CradlePoint (T400s/T450s OFF)					20230224
				~	10:27	~	10:33	~6m; NetWorx; CradlePoint	TM23 SSC EML					20230224
				~	10:59	~	11:10	~11m; NetWorx	TM23 SSC					20230224
		27	Mo	~	20:27	~	20:33	~6m; CradlePoint (T400s/T450s OFF)	TM23 EML					20230227
				~	22:09	~	22:32	~23m; CradlePoint (T400s/T450s OFF)					20230227
		28	Tu	~	04:40	~	04:42	~2m; CradlePoint (T400s/T450s OFF)					20230228
				~	23:45	~	23:48	~3m; CradlePoint (T400s/T450s OFF)					20230228
	Mar	1	We	~	01:02	~	01:44	~42m; CradlePoint (T400s/T450s OFF)					20230301
				~	02:10	~	02:20	~20m; CradlePoint (T400s/T450s OFF)					20230301
		2	Th	~	04:29	~	04:52	~23m; CradlePoint (T400s/T450s OFF)					20230302

## L2
Locations: L2	A					RN: Rayville North (Swafford) Tower					Panel 1	Panel 2	Controller	Battery 1	Battery 2	Converter	Load Device	Wattmon	Module	WebRelay

Date/Time CST/CDT					Description	Other Sources	Status	Solar Panel Total Watts	Tilt Angle	Charge Controller Maximum Watts	Battery AH	Battery C-Rating	Charge Efficiency	Peukert Constant	7 Day Average Load Watts
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	200	54	140	215	C/20	-	-	11.00	P4	P5	C5	Swafford	Swafford	-	Netonix 8-port DC	-	-	-
2015	Sep	16					L1-2	SMS EML					20150916
		19	Sa					Approximate Date of completion of initial installation; Photos of tower	AED IMG	Active	200	45	140	235.45	C/40	90%	1.07	14.8	P4	P5	C5	B6	B7	V8	Ubiquiti TS-5-POE	W3	M6		20150919
				L1-2	EML CPSN					20150919
		26					L1-2	AED					95%					20150926
2015	Oct	15					L1-2					20151015
		17		~	10:00			Logging stopped …					20151017
		19					Manually reset onsite (logging starts)					20151019
		21			13:52			Corrected Battery SoC to 100%					20151021
		24					L1-2					20151024
		25					20151025
2015	Nov	13					Inaccessible, Putty used to reboot; The entire down time was less than 30 minutes, because I was watching it at the time					20151113
				Inaccessible, Putty used to reboot [AGAIN]; The entire down time was less than 1 min., because I was watching it at the time					20151113
		14					L1-2					90%					20151114
		15					20151115
		16		~	07:00	~	08:30	I noticed "Inaccessible" and TelNet (Putty) won't connect; Portal working (no logging gap there) …; Akash managed to Telnet and reboot					20151116
				Inaccessible (again), TelNet (Putty) rebooted; Communication errors for 120s (I was watching)					20151116
		17		~	05:50		12:50	Logging gap …; Manually reset onsite					20151117
		22					Multiple (3-4) short connection errors since 11/18/15, TelNet (Putty) reboot OK					20151122
		23					Connection Error, lasted for about 7 minutes; TelNet (Putty) rebooted					20151123
		24		~	14:45	~	14:55	Logging stopped (but it reset itself)					20151124
				~	16:00			Inaccessible, rebooted with TelNet (Putty)					20151124
		27		~	03:50	~	12:05	8.25 hours of no logging ...; Butch & I at the "cow pasture" to manually reset; Corrected the battery SoC to compensate					20151127
2015	Dec	10					Inaccessible, TelNet (Putty) reboot OK					20151210
		11					Inaccessible, TelNet (Putty) reboot OK; Local logging (SD card) stopped from ~13:30 to ~13:42 (12mins); Battery SoC adjusted to compensate					20151211
		14					Inaccessible, TelNet (Putty) reboot OK; ~10 minute logging gap, insignificant (load only), no SOC correction made					20151214
		19					Inaccessible, TelNet reboot OK					20151219
		20					Inaccessible, but after a while it restored itself w/o reboot; It doesn’t look like any logging was lost					20151220
		25					Inaccessible, TelNet reboot OK; Two small logging gaps on SD Card; No Battery SoC correction needed					20151225
		31		~	00:50	~	12:04	Battery SoC mysteriously set to 100% …; Battery SoC corrected to compensate					20151231
				Later, http inaccessible, TelNet reboot OK					20151231
2016	Jan	1					Won’t reboot from http, TelNet reboot OK; Battery SoC adjusted due to logging gaps on 12/31/15					20160101
		3					Inaccessible, TelNet reboot OK					20160103
				L1-2					85%					20160103
				Will not reboot by http interface, TelNet reboot OK					20160103
		4					Inaccessible, TelNet reboot OK					20160104
		10					20160110
		11					20160111
		12		~	08:35		11:01	Logging gap; Inaccessible, TelNet reboot NOT OK …; Manual reset @ tower by Bryce and I					20160112
				13:10	Battery SoC correction to compensate					20160112
				Inaccessible, TelNet reboot OK					20160112
		18					Akash disabled SNTP and rotated the logs	AED EML					20160118
		20					Inaccessible, TelNet reboot NOT OK, but it fixed itself	AED					20160120
		23					20160123
		27					Inaccessible, TelNet reboot OK					20160127
		31					SNTP enabled: It started blowing up the System Log, every 5-15 seconds; Called Akash: he’ll have to take a look at it next week; Disabled	AED EML					20160131
2016	Feb	18			19:02	~	13:30	Logging gap; Inaccessible, TelNet won't connect …; Swapped T-105s; Cover screws redrilled and tapped (4) …	AED					B2	B3					20160218
		19	Fr				14:30	Entered correction to battery SoC					20160219
		23					L1-2	EML					20160223
		24					EML CPSN					20160224
		25					Inaccessible, TelNet reboot OK	AED					20160225
		26			13:17			Adjusted Battery SoC 97.6% --> 100% (Genasun in float @ 23W)					20160226
2016	Mar	2			21:49			Logging gap starts; Inaccessible, TelNet reboot NOT OK (Spider Bite, can't get to tower to reset now) …					20160302
		16					R_1 installed at RN; Corrected battery SoC 97% to 100% (logging stopped for 13+ days) / Set [UTC-5] Eastern Standard Time (because of DST change); Photos	AED IMG					15.7					R1	20160316
		20					L1-2	AED					235.00					20160320
		21					Battery SoC corrected from 97% to 100% (Genasun float @ 28W)					20160321
		24					Logging gap (caused by OS update corruption of cache); Akash fixed it right before midnight …					20160324
		25		~	04:50			Battery SoC corrected from 91% to 94%					20160325
		28		~	23:40	~	07:56	Battery SoC --> 0% …; Battery SoC corrected to 94%					20160328
		29		~	09:50			Battery SoC 94.3% --> 0% …; Corrected to 94.96%					20160329
2016	Apr	6		~	21:55	~	09:16	Battery SoC 98.79% --> 0% …; Battery SoC corrected to 93.6%					20160406
		9					L1-2					20160409
		17		~	19:30		03:36	Battery SoC 99.83% --> 0% …; Battery SoC corrected to 95.7%					20160417
		18		~	16:05		03:55	Battery SoC 93.20% --> 0% …; Battery SoC corrected to 88.5%					20160418
		23			16:40			Battery SoC corrected from 98.9% to 100%					20160423
		25		~	20:20		03:30	Battery SoC 99.61% --> 0% …; Battery SoC corrected to 95.7%					20160425
		30					Possible Genasun Failure: But it resolved itself on the next day (inconclusive)					20160430
2016	May	14		~	18:30		11:15	Battery SoC 100% --> 0% …; Battery SoC corrected to 98.3%					20160514
		17		~	18:05		10:20	Battery SoC 97.4% --> 0% …; Battery SoC corrected to 95.3%					20160517
		20		~	07:55	~	13:55	Battery SoC 94.7% --> 0% …; Battery SoC corrected to 99.1%					20160520
2016	Jun	2		~	17:02	~	17:04	Battery SoC 100% --> 0% ...; Battery SoC corrected to 100%					20160602
		10		~	17:50		18:09	Battery SoC 100% --> 0% ...; Battery SoC corrected to 100%					20160610
		22					Glitches & errors continue (WebRelay used 3-5 times in the past week)					20160622
				~	05:10		06:10	Battery SoC 95.97% --> 0% ...; Battery SoC corrected to 95.7%					20160622
		23		~	15:50	~	23:40	Battery SoC 100% --> 0% ...; Battery SoC corrected to 98.3%					20160623
2016	Jul	5					Details on Re-Analysis of 7 Day Average Total Load Watts: I adjusted the historical data due to now known calibration errors					20160705
				L1-2					20160705
		9		~	16:10		04:39	Battery SoC 99.8% --> 0% …; Battery SoC corrected to 226 AH (96.2%) [yesterday's value at this time]					20160709
		16	Sa		08:08		09:22	Onsite Shutdown for replacement of Wattmon & C252: SD Card copy; Site specific information copied to SD Card #7 / Removed Wattmon_3 and C252_3; Replaced with Wattmon_7 and C252_4	AED					W7	M7		20160716
				09:22		09:46	Initial onsite test using laptop (all looks good)					20160716
				09:46		09:52	Onsite shutdown to copy SD Card …; In service [but not logging to portal yet] …					20160716
				Ant trap installed; Many photos (batteries, inside cabinet, panels, site, Genasun, Converter)	AED IMG					20160716
				12:39	~	22:10	Notified Akash of MAC address change needed on portal …; Akash changed it (email from Akash 22:14)	EML					20160716
				13:59			Battery SoC corrected to 100% (due to logging gaps today for swap, currently in float, 1W net charge, 13.25v, 235AH)	AED					20160716
		19	Tu		08:15			L1-2					246.00		80%	1.15					20160719
				08:57			Corrected Current Battery AH to reflect change in capacity 246/235*210.91687=220.790 (set 221)					20160719
				~	13:53		14:00	RN switches to float when 94.8% SoC, 13.5v and net charge drops (after a few minutes) to 4W/246AH=1.6% ratio … / Corrected Current Battery AH to 246 AH (100%)					20160719
		20	We	~	08:15			L1-2					20160720
				09:43					225.00	C/20					20160720
				~	14:00		14:05	RN switches to float when 99.61% SoC, 13.5v and net charge drops to 3W/225 AH=1.3% ratio … / Corrected Current Battery AH from 224.16249 to 225 AH (100%)					20160720
		21	Th	~	08:30			L1-2					20160721
				~	11:00					20160721
				12:30			L1-2	AED					1.13					20160721
				~	13:23			Wattmon hits "100%" about 1.5 hours into the Genasun's absorption cycle; This I consider "spot-on" for the algorithm, and so no Battery SoC correction is needed and the Battery Parameters configuration looks very good					20160721
		22	Fr	~	11:15	~	13:42	Observations: Absorption period 14.3v …; Float 13.4v when SoC 99.81% and net charge 0W climbing slowly / Wattmon will most likely hit 100% after a few hours, but it is SLIGHTLY LATE					20160722
				~	14:30			L1-2	AED					1.11					20160722
				15:19			L1-2					20160722
		23	Sa		11:36	~	13:55	Observations: Absorption period 14.3v (97.4% SoC, trigger seen was 0.1 or 0.2 above (14.4-14.5v) … / Float 13.5v (not as hot today) net charge 0W climbing slowly					20160723
				14:15	~	18:45	Observations: Float @ net charge 2W and 99.62% …; Highest point reached 99.91%; Obviously LATE					20160723
		24	Su	~	11:45	~	14:00	Observations: Absorption period 14.3v …; Float 13.5v (99.77%)					20160724
				16:36			Wattmon hits "100%" (net charge 2W); LATE					20160724
				17:39			Increased Charge Efficiency 80 --> 85%					85%					20160724
		25	Mo	~	12:50	~	15:15	Observations: Absorption period 14.4-14.5v (cooler today, but heating up) …; Float 13.5v (99.93%)					20160725
				15:56			Wattmon hits "100%" (net charge 2.5W, ratio 1.1%): Slightly late but OK					20160725
		26	Tu		13:54			Wattmon hits "100%" about 3 mins before Genasun switches to float; "Spot-on"					20160726
		27	We	~	11:25	~	13:50	Observations: Absorption period (14.5v); Wattmon hits "100%" @ 13:18 or about 80% through Absorption period; "Spot-on"					20160727
		28	Th		13:24			Wattmon hits "100%" about 3/4 into the Genasun Absorption period (but no email has been rec'd yet as of 14:25, I don't know why); "Spot-on"					20160728
				15:35			Increased Peukert Constant 1.11-->1.17; Decreased Charge Efficiency 85-->80%					80%	1.17					20160728
		29	Fr		12:42			Wattmon hits "100% about 1/2 way into the Genasun Absorption period; Slightly Early					20160729
		30	Sa		04:20			Decreased Charge Efficiency 80-->75%					75%					20160730
				"100%" @ ~ end of Genasun Absorption; "Spot-on"					20160730
		31	Su	~	18:15	~	19:35	Float …; "100%"; 1 Hr 20 Mins Late					20160731
2016	Aug	1	Mo	~	16:35	~	19:00	Float …; "99.8%" maximum for the day; More than 2 Hrs 25 Mins Late					20160801
		2	Tu	~	14:50	~	15:05	Float …; "100%"; 15 Mins Late					20160802
				16:47			Increased Charge Efficiency 75-->80%					80%					20160802
				Subsequent color coding: 100% but not 3%; Neither 3% or 100% OR 100% and 3%; 3% but not 100% (should/did correct SoC at least +x%)					20160802
		3	We		15:31	~	16:33	"100%" while in Float; 5.2% Ratio (spot on by 5% rule, because within mins it was 5%, but EARLY by newer better 3% Ratio Rule) … / 3% Ratio, "100%" is EARLY by ~1Hr; I need to drop C.E., but I would very much like to see what happens tomorrow if Genasun goes to Absorption in order to decide how much (-->75%? -->77%?)					20160803
		4	Th		15:52	~	17:30	"100%" while in Float …; 3% Ratio; 1Hr 38Mins Early					20160804
		5	Fr		04:41			Decreased Charge Efficiency 80-->77%					77%					20160805
				Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate	AED					16.1					20160805
		6	Sa	~	11:35		13:37	Absorption …; "100%" 2 Hrs into absorption; "Spot-on"					20160806
		8	Mo	~	17:00		17:24	Absorption Period ended …; "100%" (24 mins late by 3% rule)					20160808
		9	Tu		13:12	~	14:10	"100%" …; Absorption Period ended (58 mins early by 3% rule)					20160809
		10	We	~	17:45		17:55	Float day (no absorption) ~3% Ratio …; "100%" (10 mins late)					20160810
		11	Th		17:32	~	18:30	Float day (no absorption) "100%" …; ~3% Ratio (58 mins early)					20160811
		12	Fr	~	04:50			Decreased Charge Efficiency 77-->76%					76%					20160812
		13	Sa		14:26	~	16:15	"100%" (Absorption ended before that at ~14:00) …; ~3% Ratio (1 Hr 49 Mins early, but I'm not going to judge if it isn't a float day)					20160813
		14	Su	~	16:20		17:28	Float day (no absorption) ~3% Ratio …; "100%" (1 Hr 8 Mins late)					20160814
		15	Mo	>	15:30	<	17:00	Watered batteries; Lowered panels (I managed to hit 54.0 +- 0.1 degrees); Cleaned solar panels				54					20160815
				15:07	~	16:55	"100%"; No obvious regulation (poor solar day); 14.7v peaks (2 short ones) …; 15.1v peak (short); EARLY					20160815
		16	Tu		14:05	~	14:25	100% ...; Absorption ends and <3% Ratio (20 mins early)					20160816
		17	We		13:48	~	14:15	100% ...; Absorption ends and <3% Ratio (27 mins early)					20160817
		18	Th		13:47	~	14:30	100% ...; Absorption ends and <3% Ratio (43 mins early)					20160818
		19	Fr		14:33	~	14:40	100% ...; Absorption ends and <3% Ratio (7 mins early)					20160819
		20	Sa	~	15:50		17:39	(Absorption ~12:45 to ~15:05) ~3% Ratio …; 100% (1 hr 49 mins late)					20160820
		21	Su	~	14:25		14:47	Absorption ends and <3% Ratio …; 100% (22 mins late)					20160821
		22	Mo	~	14:15		14:40	Absorption ends and <3% Ratio …; 100% (25 mins late)					20160822
		25	Th	~	13:50	~	18:30	Absorption ends and <3% Ratio …; 99.93% at end of solar (more than 4 hrs 40 mins late, should correct SoC at least +0.7%)					20160825
		26	Fr	~	15:00		16:31	Absorption ends and <3% Ratio …; 100% (1 hr 31 mins late)					20160826
		27	Sa		14:09	~	14:20	100% ...; Absorption ends and <3% Ratio (11 mins early)					20160827
		28	Su		13:43	~	14:25	100% ...; Absorption ends and <3% Ratio (42 mins early)					20160828
		29	Mo		14:05	~	14:25	100% ...; Absorption ends and <3% Ratio (20 mins early)					20160829
		30	Tu		14:20	~	14:40	100% ...; Absorption ends and <3% Ratio (20 mins early)					20160830
		31	We		17:38	~	18:05	100% ...; Absorption ends and <3% Ratio (27 mins early)					20160831
2016	Sep	1	Th	~	14:05		14:15	Absorption ends and =~3% Ratio …; 100% (10 mins late)					20160901
		2	Fr					L1-2	AED					16.2					20160902
				~	14:40		15:47	(Absorption ~11:40 to ~14:10) ~3% Ratio …; 100% (1 hr 7 mins late)					20160902
		3	Sa	~	14:20		16:26	(Absorption ~11:30 to ~14:00) ~3% Ratio …; 100% (2 hr 6 mins late)					20160903
		4	Su	~	14:25		15:48	Absorption ends and <3% Ratio …; 100% (1 hr 23 mins late)					20160904
		5	Mo		13:54	~	14:15	100% ...; Absorption ends and <3% Ratio (21 mins early)					20160905
		6	Tu		13:35	~	14:20	100% ...; Absorption ends and <3% Ratio (45 mins early)					20160906
		7	We		15:21	~	16:05	100% ...; Absorption ends and <3% Ratio (44 mins early)					20160907
		9	Th		17:15	~	17:30	(Absorption ~12:50 to ~14:55) 3% Ratio (6.75W Net, I watched it live, 99.8%) … / 99.83% maximum SoC (but if we had sun it would have been ~45 mins late, should correct SoC at least +0.2%)					20160909
		10	Sa	~	14:45		15:37	(Absorption ~11:30 to ~13:50) 3% Ratio (6.75W Net) …; 100% (52 mins late)					20160910
		11	Su	~	14:45		17:03	(Absorption ~11:40 to ~14:00) 3% Ratio (6.75W Net) …; 100% (2 hrs 18 mins late)					20160911
		12	Mo	~	14:10		15:22	Absorption ends and <3% Ratio …; 100% (1 hr 12 mins late)					20160912
		15	Th	~	18:15			No absorption, floated down to ~3% ratio @ 99.5% SoC (lost solar at that time, so it didn't make it to 100%) / (slightly late, should correct SoC at least +0.5%)					20160915
		17	Sa	~	18:15			Absorption day, then floated down to ~3% ratio @ 99.7% SoC (lost solar at that time, so it didn't make it to 100%) / (slightly late, should correct SoC at least +0.3%)					20160917
		18	Su	~	18:15			No absorption, floated down to ~3% ratio @ 99.6% SoC (lost solar at that time, so it didn't make it to 100%) / (slightly late, should correct SoC at least +0.4%)					20160918
		19	Mo		14:47	~	15:00	Absorption, then float to 100% …; 3% ratio (13 mins early)					20160919
		20	Tu		13:40	~	14:30	100% during absorption (until ~14:15) …; 3% ratio (50 mins early)					20160920
		21	We	~	17:55			Float day: 13.5v, 3% ratio …; 99.8% at end of solar (slightly late, should correct SoC at least +0.3%)					20160921
		22	Th		13:45	~	15:10	Absorption (14.5v) and 100% …; 3% ratio (1 hr 25 mins early); Decreased charge efficiency 76-->75%					75%					20160922
		23	Fr		13:43	~	14:10	100% during absorption …; Absorption ends and 3% ratio (27 mins early)					20160923
		24	Sa		13:57	~	14:10	100% during absorption …; Absorption ends and 3% ratio (13 mins early)					20160924
		26	Mo	~	15:10	~	17:25	Absorption ended …; 3% ratio; 99.6% at end of solar (about 2 hrs 30 mins late, should correct SoC at least +0.5%)					20160926
		27	Tu	~	17:10	~	18:00	Float day: 13.8v, 3% ratio …; 99.3% at end of solar (about 3 hrs late, should correct SoC at least 0.8%)					20160927
		28	We	~	15:00	~	18:15	Absorption 14.7v and then float 13.9v and 3% ratio …; 99.5% at end of solar (~ 7 hrs late, should correct SoC at least +1.0%)					20160928
		29	Th	~	15:00	~	18:00	Absorption 14.8v and then float 13.9v and 3% ratio …; 99.6% at end of solar (~ 5.5 hrs late, should correct SoC at least +0.9%)					20160929
		30	Fr	~	09:30			Increased charge efficiency 75-->76%; SoC corrected +0.9% (210.005325-->212AH, to compensate some for 4 days of not hitting 100%)					76%					20160930
				13:45	~	14:45	Absorption; 100% …; 3% ratio (1 hr early)					20160930
2016	Oct	1	Sa					L1-2; RN using 22.65 W solar in float as 3% ratio	AED					15.9					20161001
				L1-2					20161001
		7	Fr	~	17:30	~	18:10	Absorption and 3% ratio …; 98.6%SoC max at end of solar (~4 Hrs 40 mins late, should correct SoC at least +1.5%)					20161007
		8	Sa	~	17:10			3% ratio but did not make 100%, should correct SoC at least +1.6%					20161008
		9	Su		12:48		14:21	Increased charge efficiency 76-->78% ...; Corrected SoC +1.6%					78%					20161009
				~	14:55		16:38	3% … 100%					20161009
		10	Mo					3% but not 100% (99.9% maximum at end of solar), should correct SoC at least +0.1%					20161010
		11	Tu		14:39	~	14:50	100% … 3%					20161011
		18	Tu					Onsite to reset Ubiquiti and water the batteries. Node inaccessible.					20161018
		23	Su					3% but not 100% (99.9% maximum at end of solar), should correct SoC at least +0.1%					20161023
		24	Mo	~	15:55		16:00	3% … 100%					20161024
		25	Tu	~	08:25			Increased charge efficiency 78-->79%					79%					20161025
				100% … 3%					20161025
		27	Th					20161027
		28	Fr					20161028
		29	Sa					20161029
2016	Nov	1	Tu					20161101
		3	Th					L1-2; RN using 22.4 W solar in float as 3% ratio	AED					15.7					20161103
				100% but not 3% (3.4% minimum at end of solar)					20161103
		4	Fr	~	03:10			Decreased charge efficiency 79-->78%					78%					20161104
				100% but not 3% (3.8% minimum at end of solar)					20161104
		5	Sa					3% but not 100% (99.96% maximum at end of solar), should correct SoC at least +0.04%					20161105
		6	Su					100% … 3%					20161106
		8	Tu					3% but not 100% (99.25% maximum at end of solar), should correct SoC at least +0.75%					20161108
		9	We					3% but not 100% (99.48% maximum at end of solar), should correct SoC at least +0.52%					20161109
		10	Th					3% but not 100% (99.36% maximum at end of solar), should correct SoC at least +0.64%					20161110
		11	Fr					3% but not 100% (99.48% maximum at end of solar), should correct SoC at least +0.52%					20161111
		12	Sa					3% but not 100% (99.12% maximum at end of solar), should correct SoC at least +0.88%					20161112
		13	Su	~	10:35			Increased charge efficiency 78-->79%; Corrected SoC +1.15%					79%					20161113
				3% but not 100% (99.87% maximum at end of solar), should correct SoC at least +0.13%					20161113
		14	Mo					3% … 100%					20161114
		15	Tu					100% … 3%					20161115
		16	We					20161116
		17	Th					20161117
		20	Su					3% but not 100% (97.30% maximum at end of solar), should correct SoC at least +2.70%					20161120
		21	Mo	~	11:20			Increased charge efficiency 79-->80%; Corrected SoC +2.65%					80%					20161121
				~	11:30			L1-2					20161121
		24	Th		07:35		11:54	SoC<75% …; SoC>75%					20161124
		27	Su	~	07:50	~	15:05	Logging gap; Not sure why; This was the day we lost the power at RW, but this should not have affected RN, and the time of start of the gap was almost 3 hours before the Netonix at RW started cycling					20161127
2016	Dec	4	Su		08:25		13:02	SoC<75% …; SoC>75%					20161204
		5	Mo		02:21		10:13					20161205
		6	Tu		14:57	~	16:00	Soc 82.61-->0% (need SoC correction of at least +82.61%, but too busy to deal with it)… / 3% near end of solar (and it would not have made 100% w/o the glitch) …					20161206
		14	We	~	08:10			Corrected SoC to 82.2%; NOTE: I tried to calculate a correction based on the energy graphs, AH 185.9 before drop to zero - 97.0 * 225/260 (for Peukert Constant) lost while at zero + 25.2 current tally = 127.2 rounded up to 128 AH or 57%, but I know this isn't right by looking at yesterday's energy graph; Yesterday we reached a 9.2% ratio at the end of solar; This is typical of about 85-95% charge / So I decided that my calculations are significantly in error, and set 185 AH (82.2%) (loss through the night of about 8%)					20161214
		15	Th		06:49		12:23	SoC<75% …; SoC>75%					20161215
				18:25			SoC<75%					20161215
		17	Sa	~	23:30			SoC<50%					20161217
		18	Su	~	12:50					20161218
		19	Mo					L1-2; RN using 22.5 W solar in float as 3% ratio	AED					15.7					20161219
		24	Sa		10:33			SoC<50%					20161224
		26	Mo		13:47			SoC>50%					20161226
		31	Sa	~	16:30			3% ratio at end of solar day when Soc 64.27%, should correct SoC at least +35.73%, and should increase Charge Efficiency					20161231
2017	Jan	1	Su		05:42	~	14:55	Corrected SoC +35.73% from 57.61% to 93.33% (connection difficulties) …; Onsite: redid connections, etc.; Restored some of the missing logs / Increased charge efficiency 80->82%; SD Card copies; Cleaned solar panels; Watered batteries / [Note added 3/29/18: THIS WAS THE LAST TIME I WAS ONSITE, Swaffords would not renew maintenance contract]	AED					82%					20170101
		2	Mo					L1-2; RN using 22.6 W solar in float as 3% ratio					15.9					20170102
		6	Fr		03:15		10:52	SoC<75% …; SoC>75%					20170106
		7	Sa		07:12		09:15					20170107
				09:44	~	10:58	SoC 75.86% -> 0% …; Corrected SoC to 77.78% (175AH, solar positive since it dropped, 1.65% at ~10:50)					20170107
		8	Su		05:23		13:57	SoC<75% …; SoC>75%					20170108
		9	Mo		00:25		13:38					20170109
				20:27			SoC<75%					20170109
		10	Tu		14:02		17:25	SoC>75% …; SoC<75%					20170110
		15	Su		07:26			SoC<50%					20170115
		17	Tu		21:38			SoC<25%					20170117
		18	We		15:19					20170118
		19	Th		00:35					20170119
		23	Mo		05:50		09:15	SoC=0%, 11.3v, should increase Charge Efficiency, but due to other errors, I'll hold off doing that …; SoC>0%					20170123
				09:56		09:59	SoC=0% …; SoC>0%					20170123
				Email to Swaffords "Solar Power System Quote": Quote, Basic Maintenance.pdf / Attachment Photo, Inside of Equipment Box.pdf; Attachment Battery Status, January 2017.pdf	EML DBS IMG TSP					20170123
		24	Tu					Emails to Mark "Fw: Solar Power System Quote" (from yesterday), I was surprised that Jackie called it an invoice / Requested Mark to help them understand	EML DBS TSP					20170124
		25	We					Email to Jackie Swafford "Re: Solar Power System Quote"	EML TSP					20170125
		26	Th		11:27		15:58	SoC=0%, 11.5v (with a little solar help), should increase Charge Efficiency …; SoC>0%					20170126
				16:20			SoC=0%, 11.5v, should increase Charge Efficiency					20170126
		27	Fr		08:36		09:04	Increased Charge Efficiency 82->85% (holding on at SoC=0% and 11.1v) …; SoC>0%					85%					20170127
				16:15		19:12	SoC>25% (superb solar day, 1.00 KwH) …; SoC<25%					20170127
		28	Sa		11:38			SoC>25%					20170128
		30	Mo		14:38			SoC>50% (no email, but the System Log shows it)					20170130
		31	Tu		07:21			SoC<50%					20170131
				08:53		08:58	Soc dropped from 49.67% to 0% (this was caused by me testing a reboot with the WebRelay) … / Corrected SoC to 49.78% (112AH) (this was an almost perfect correction due to net increase of 0.126% during 5 minute period)					20170131
				09:09			SoC>50%					20170131
				L1-2	EML CPSN					20170131
2017	Feb	1	We		06:06		11:52	SoC<50% …; SoC>50%					20170201
				23:15			SoC<50%					20170201
		2	Th		10:57			SoC>50%					20170202
		7	Tu		22:40			SoC<50%					20170207
		9	Th		13:53			SoC>50%					20170209
		10	Fr		02:42		10:31	SoC<50% …; SoC>50%					20170210
		12	Su		17:10			28.3 W solar in float at end of solar day (5.5% ratio); 64.8% SoC; My "gut" says we need to increase Charge Efficiency again.					20170212
		13	Mo	~	02:40			Increased Charge Efficiency 85->90%					90%					20170213
		17	Fr		12:56		22:36	SoC>75% …; SoC<75%					20170217
		18	Sa		10:49			SoC>75%					20170218
		19	Su		06:32		09:18	SoC<75% …; SoC>75%					20170219
		21	Tu		05:33		09:39					20170221
		26	Su	~	17:00	~	17:30	3% ratio (92.8% SoC) …; End of solar day about 30 mins later (92.97% SoC)					20170226
2017	Mar	3	Fr	~	14:30	~	17:30	3% ratio (98.3% SoC) …; End of solar day about 3 hours later (99.11% SoC)					20170303
		4	Sa		12:53	~	16:30	100% … 3%					20170304
		7	Tu		15:08			SoC dropped 99.87 -> 0% and solar charge dropped from 37.8 to 0 watts	AED					20170307
		8	We	~	04:45			Corrected SoC 0% -> 95.1%					20170308
				Details on current Analysis of "7 Day Average Load Watts" including figures on Average Load A and C-Rate / Using 22.5 W solar in float as 3% ratio; Approximately the same as 1/2/17 data					15.8					20170308
				L1-2	EML CPSN					20170308
				11:30		17:39	100% but not 3% (4.4% minimum at end of solar)					20170308
		9	Th		12:13		17:29	100% ... 3% before end of solar					20170309
		10	Fr		12:34		17:01					20170310
		17	Fr		12:59		18:01	100% … 3% before end of solar [CDT]					20170317
		18	Sa		12:50		18:27	100% … and almost 3% before end of solar (3.1%)					20170318
		19	Su		13:08		18:23	100% … 3% exactly at end of solar					20170319
		20	Mo		12:16		18:29	100% … and almost 3% before end of solar (3.2%)					20170320
		21	Tu		13:50		18:47	100% … 3% about 2 hrs before end of solar					20170321
		22	We		13:19		18:33	100% … 3% about 3.5 hrs before end of solar					20170322
		23	Th		12:51		18:54	100% … 3% about 4 hrs before end of solar					20170323
		28	Tu		22:22			SoC<75%					20170328
2017	Apr	5	We		03:30		14:44	SoC<50% …; SoC>50%					20170405
		6	Th		17:36		23:16	SoC>75% …; SoC<75%					20170406
				Superb solar day, 0.98 KwH, +20.1% SoC gain					20170406
		7	Fr		11:35			SoC>75%					20170407
		8	Sa		12:55		18:46	100% but not 3% (8.7% minimum at end of solar)					20170408
		9	Su		13:54		18:23	100% but not 3% (5.0% minimum at end of solar)					20170409
		10	Mo		05:14			Decreased Charge Efficiency 90-->85%					85%					20170410
				14:37		18:52	100% but not 3% (3.8% minimum at end of solar)					20170410
		11	Tu		13:13		18:51	100% but not 3% (6.1% minimum at end of solar)					20170411
		12	We		13:09		17:25	100% but not 3% (5.2% minimum at end of solar)					20170412
		13	Th		12:40		18:41	100% but not 3% (3.4% minimum at end of solar)					20170413
		14	Fr		14:22		18:59	100% … 3%					20170414
		15	Sa		12:20		18:46					20170415
		16	Su		12:42		17:51					20170416
		17	Mo		12:50		19:06					20170417
		18	Tu		12:53		19:01					20170418
		19	We		12:22		18:47					20170419
		20	Th		12:40		19:02					20170420
		21	Fr		13:55		17:07					20170421
		22	Sa		13:05		19:23					20170422
		23	Su		12:45		18:49	100% but not 3% (3.3% minimum at end of solar)					20170423
		24	Mo		12:48		18:46	100% … 3%					20170424
		25	Tu		13:04	~	16:55					20170425
		27	Th		15:05		18:21					20170427
2017	May	5	Fr		14:24		18:54	100% but not 3% (5.0% minimum at end of solar)					20170505
		6	Sa		12:24		18:45	100% … 3%					20170506
		7	Su		12:42		18:52	100% but not 3% (3.6% minimum at end of solar)					20170507
		8	Mo		12:13		18:50	100% … 3%					20170508
		9	Tu	~	12:30		18:50					20170509
		10	We		13:58		18:58					20170510
		12	Fr		12:53		18:47	100% … 3% (barely)					20170512
		13	Sa		12:15		18:44					20170513
		14	Su		12:27		18:46	100% … 3% (I will discontinue recording these events until noted)					20170514
		22	Mo		15:25		15:55	100% but not 3% (unable to see regulation in float by end of solar)					20170522
2017	Jun	5	Mo		13:13		19:00	100% but not 3% (3.8% minimum at end of solar)					20170605
		27	Tu					L1-3	EML					20170627
2017	Jul	7					Portal data stopped	AED	Unknown					20170707
2019	Jan	18	Fr	~	10:40			Mark Webb & Keith Jones onsite: No power, batteries are dry; It has been operating, Mark said something about the switch throwing errors on their network in the past few weeks; Note that RN has been running for 2 yrs 17 days w/o any maintenance / See white paper notes file 'TurboNet - Solar Power Systems'	SMS TSP	Dead Batteries					20190118
		21	Mo		08:21		08:39	Reason Swafford called: "I solved the problem."; He bought two "equivalent" batteries, not Trojan, but flooded, paid $130 each but had to turn in the two Trojans as cores; They don't yet have internet, he says Mark said the Tough Switch needs to be replaced; I explained again the need for (4) batteries instead of (2), and discussed the monitoring system, which, if they aren't interested in using they should disconnect / See white paper notes file 'TurboNet - Solar Power Systems'	TSP	Unknown				?	?					Swafford	Swafford					20190121
				10:14			Mark called, I have somehow upset the Swaffords (probably Jackie, who never understood anything I said), they will lose the contract unless Mark satisfies them; Quoted $160 for 2 hrs to go replace Ubiquiti switch with the spare I have					20190121
		22	Tu					Onsite; Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)	TSP IMG	Active				215.00	C/20	-	-					-	-	-	20190122
		29	Tu					Spoke with Mark, he's good w/$160 for Ubiquiti replacement visit, he'll be asking Swafford to reimburse him	TSP					20190129
				Keith onsite, he's replaced everything, now suspect convertor; They want me to go back, another $160 quote					20190129
				13:15		14:30	Prepped and left to meet Reason @ 13:30; Replaced converter, but old one was 24.6v and new one 24.5v / Watered Swafford's batteries, they were down ~1/8" …; Returned to shop	TSP IMG					V1					20190129
				14:30		15:00	V1 Converter bench tested and proved to be defective (1A load causes it to shut off); See white paper notes file 'TurboNet - Solar Power Systems'	TSP					20190129
		31	Th					Keith reports that Swafford's internet is running (he had to play with the ports, but now OK) / Discussion with Mark; Email to Mark and Keith with Invoice for $445.45; Email sent to Mark and Keith with Invoice for $420 (modified to discount converter); Also emailed Invoice to Swaffords; Corrected TurboNet mailing address and resent invoice to Mark	TSP EML DBT DBS					20190131
	Feb	4	Mo					Rec'd $420.00 check from TurboNet "Swafford Solar tower -fix"	TSP					20190204
		13					20190129;0213 Scan, Business Card 'Show-Me Ziplines, L.L.C.' 1 (Front).jpg / 20190129;0213 Scan, Business Card 'Show-Me Ziplines, L.L.C.' 2 (Back).jpg	TSP SSC DBS					20190213
		14	Th					Emails to Swaffords, Mark and Keith "Reason Swafford photos, Jan 22nd visit …" with 20190122 photos	EML IMG TSP					20190214
2020	Jul	3	Fr		13:13		13:30	Missed call and from Mark “Can you see the watt man at the zipline tower? That tower went down about 5 minutes ago. Let me know. …” … / LMVM; To Mark “The Swafford’s did not want to pay for maintenance and remote monitoring. The Wattmon equipment was removed a long time ago. The only way to find out what’s going on is to go up there. Let me know if they want me to go.”	SMS					20200703
				~	14:25	~	14:50	Called Mark: 3x could not connect; LMVM “I’m back, status on Swaffords?”; Mark called “do you have stuff to put an end on a cable in case there’s water in it?”, “Yes”, Keith interrupted and he said he’d call right back … I waited by the phone for 10 mins					20200703
				~	15:20	~	15:25	Called Keith, NA; Called Mark, Keith got in and reset it, now OK (also confirmed Mo7/6 09:30 Odessa N and next week “New Tower” [OT])					20200703
		27	Mo	~	11:29	~	12:15	Calls to/from Mark and Keith: Discussed Swafford site (Ubiquiti keeps needing a reset, suggested MicroTek w/quality 12-24vdc converter $150+)	WP10					20200727
	Aug	3	Mo	~	17:13	~	17:29	Call from Mark: Amongst other projects discussed Swafford's; Send him quotes/estimates Tu8/4 AM	WP10					20200803
		4	Tu	~	06:20	~	08:30	Phone calls/SMSs to Keith and Mark: In call to Mark to discuss New Building Electrical I hit on the idea that the best thing to do for Swafford would be to install a DC Netonix; All I will have to do is provide load cables to put it directly on the battery, and go onsite with Keith to be sure it is all OK (including a quick check on the solar power system); It will monitor the battery voltage, so Keith will have some idea of the health of the solar system (remotely); Dumped recommendation to install MicroTek 24vdc with better 12-24vdc converter	SMS WP10					20200804
				~	09:00	~	10:00					20200804
		10	Mo	~	10:28	~	10:31	Call from Mark: Swafford tomorrow after lunch; Meet at zipline office 13:00	WP10					20200810
				~	20:20	~	20:25	SMS from Mark: Keith may arrive in Rayville earlier, 11:00-12:00					20200810
		11	Tu	~	12:05	~	13:45	Onsite with Keith; Custom load cables with fuse installed on battery and Netonix; Added 5/8" water to Swafford's battery (was only ~1/8" above plates); Solar system OK, weak sunlight 14.0v Micronta (trying for Absorption, Genasun solid green); Installed ant trap / Netonix reports 11.0 watts (was 15.8w Wattmon March 2017); Keith did not set up Netonix notification (I recommended 11.5v, he said he'd do it later, but I doubt that he will); Photos TurboNet Onsite @ Swafford Tower; Keith Jones	TSP WP10 SMS IMG V1					11.0	P4	P5	C5			-	Netonix 8-port DC				20200811
		12	We					20200812 Invoice - Swafford.doc sent by email to Mark and Keith (the email contains a pitch for solar at low powered sites)	TSP WP10					20200812
2021	Mar	9	Tu					IP and credentials for Netonix rec'd from Keith; 192.168.1.34, admin, admin / NTP is enabled but not working, zone -> Mexico; SMTP configured but not working (times out); Warning voltage 11 (not changed)	EML TM21S DBT					20210309
		10	We	~	10:31	~	10:36	Keith logged in to the Netonix and worked on fixing the NTP/SMTP problem as evidenced by two test email notifications / 192.168.1.34 is no longer valid; Keith confirmed that he changed it, did not give me the new address, and said it might be a couple of days before he gets back to working on this as "I have towers down"	EML SMS					20210310
	Apr	17	Sa					Keith sent new IP; 10.10.11.247, admin, admin; NTP is working (clock is correct); Test email OK / Threshold warning voltage 11 (not changed); MAC ec:13:b2:e2:54:b8	SMS					20210417
	Jun	21	Mo	~	12:45	~	13:10	Onsite for the Backup Power Supply Maintenance Program; Reason Swafford said it had been 3-4 months since he'd been up there; I could not completely remove the wasps (no spray), there's a nest hanging from the Genasun; Electrolyte ~ 1/8" above plates; Added ~1" water to all cells; MAC ec:13:b2:e2:54:b8; Ticks and chiggers abound; Netonix graphs looked at since 4/17 show that solar system is doing fine; 12.4 watts	DBT TM21S					20210621
		23	We					Email report to Mark and Keith for 6/21 visit	EML TM21S					20210623
	Dec	31	Fr					L1-3 L6-7 L10-16; RN Not Maintained as Hoped (last visit 6/21/21)	TM21F DBT					20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104

## L3
Locations: L3	A					RCWT: Richmond City Water Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Battery
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	WP7	B9/10
2017	Mar	29	We					Email to Mark Webb "DC UPS quote examples (RW, RN)", after "3 days of internet research and engineering design" [but we were talking about installing WP1 at RW]	EML WP1	Research			20170329
	Jun	27	Tu					L1-3	EML				20170627
	Jul	10	Mo					L1/3					20170710
		12	We					TW1 WRD EML	On Order	WP1		20170712
		18	Tu					Battery Received; "Let There Be WISPOWER" (prayer and inspiration)	TW1 WRD			B26	20170718
	Aug	3	Th					Emails with Mark "Re: WISPOWER"; Photos of bench testing setup (incomplete); Phone call discussion with Mark; $980 invoice sent via email "Re: Invoice" (20170803 Invoice.pdf)	EML IMG DBT TW1				20170803
		4	Fr					Phone call to Mark; He mailed $300.00 check for "Disaster recovery Box"	TW1 WRD				20170804
		7	Mo					Test setup; Discharge Test Conclusions; Received $300.00 check (now $700 total rec'd for WISPer #1)	IMG WRD TW1				20170807
		14	Mo					Rec'd M3 screws and Allen insert bits from BoltDepot.com; Rec'd Red/Black Zip Cord from BulkWire.com; Rec'd Enclosure, Schottky Diodes and NTC Thermistors from Mouser	TW1 BDC	Assembly			20170814
		18	Fr					Adjusted PS1 with 3w resistor load to simulate fully charged battery, tested Temperature Compensation; Discharge Test with 75-100w resistive load (~7.5 hrs); Recovery Test with 65-90w resistive load (HOT!!!)	TW1 WRD	Testing			20170818
		31	Th					I drove to Lexington to show Mark and Keith the prototype and to discuss things; Email to Mark and Keith "WISPOWER Basic Features and Benefits" with WISPOWER Features & Benefits.pdf	EML DBT	Ready to Install			20170831
	Sep	5					Photos: WISPer #1 Ready to Install at RCWT	IMG				20170905
		6					WISPer #1 and battery installed at RCWT, components are Mean Well SCP_PS1 (BC4) and SCP_PS2 (BC5) Dual Supply Design with Schottky Diode, Battery 20170718; Photo of water tower / Final payment of $280 rec'd from TurboNet, total rec'd $980; 1 Year Warranty (we didn't discuss it but I'll honor it); Keith email "FW: test email from Rich-City-DC" (he got the Netonix SMTP working) / I emailed him back and said "From the chart I gave you, you should have about 14 hours of battery backup for your load of 65 watts"	IMG WRD TW1 EML	Active			20170906
2019	Mar	27	We		12:15			SMS from Mark Webb: '… come check out battery back up @ RCWT … DC switch blew up like the beginning of winter … we're going to put in another but "it's not getting enough power to do it" so give me a holler thanks' / [see white sheet notes]	SMS TW1 WS				20190327
	Apr	1	Mo		09:46		09:56	Spoke with Mark concerning RCWT, Swafford's and RW; RCWT 'Hooked up new DC unit last week, and not enough power'; Scheduled onsite Tu AM					20190401
		2	Tu		07:53		08:02	MMS & SMSs from Keith Jones: Screenshot showing 33.2 watts on AC Netonix @ RCWT; 'Seems to be between 34-45 watts'	SMS				20190402
				09:05		10:35	Onsite at RCWT: 48°F, battery 14.1vdc, load 15.2vdc (DC Netonix is running but no loads on it, Schottky is blocking, Tcomp on battery charger is AOK, s/b 14.15vdc battery) / Removed AC, battery 13.9vdc, load 13.6vdc (AOK); AC on, battery 13.8vdc, load 15.2vdc (AOK); Power supplies are both cold; No visible signs of heat damage; Everything is working as it should / Waited ~20 mins for Keith to show up; 'Show and Tell', discussion [Service Call to be billed as 'No Fault Found' and 'Defective DC Netonix']					20190402
		3	We	~	05:00	~	05:30	Email to Mark and Keith "Invoice for Service Call @ RCWT + Offer": $160.00 (4/2/19, added to income for WP1); I offer to work for him on his network or infrastructure in any capacity	EML DBT TW1				20190403
				Email response from Mark "We'll have to figure something out.": He complains about not having charged me for internet "for ever"	EML				20190403
	May	4	Sa					Revised invoice sent to Mark Webb via email & USPS (typo fixed, "Paid in Full by Service Rendered")	EML DBT TW1				20190504
2020	May	8	Fr					While onsite in Lexington Mark and Keith mentioned that they needed to visit RCWT sometime in the next week; I asked to be notified as I'd like to inspect the power supply/battery (it was last checked 4/2/19)					20200508
2021	Mar	9	Tu	~	10:30			IP and credentials for Netonix rec'd from Keith; 10.1.20.156, admin, admin; NTP and SMTP configured and tested; Warning voltage 11->13; Float is 14.9v as per Netonix (probably erroneously high, not calibrated yet)	EML TM21S DBT				20210309
		12	Fr	~	10:25	~	11:55	Onsite for the Backup Power Supply Maintenance Program; 52°F; Battery 13.9v Fluke (T compensated power supply, slightly low for ambient conditions, s/b 13.7+0.4=14.1v as per Genasun spec. for SLA); Load 14.975v Fluke, Netonix 15.0; Netonix Input Power Supply calibration OK (not changed); Load 40 watts; Discharge 10 mins; Warning notification sent in < 1min (13.0 threshold) / Therefore set 12.0v threshold for warning @ 4-5min; 11:35 SSC shows discharge test; REMINDER Netonix does not see the battery voltage when there is AC power and during a discharge there is a relatively large difference between what the Netonix sees and the actual battery voltage because of the light guage wire and the diode used in this #1 prototype (~0.6v drop battery to load)	DBT TM21S SMS SSC		WP1	B26	20210312
		13	Sa					Email Report to Mark and Keith; Run-time Estimate ">24 Hrs @ 40 watts"; Battery Service Life "... probably useable for another 2-4 years due the low temperature controlled environment (45-65°F year round)"	EML TM21S				20210313
	Aug	4	We	~	16:46			Internet down @ shop (see RW for details); I found out at 17:42-17:43 that it is RCWT power issues; 19:21-19:22 SMS to/from M&K "1 mile from tower, any news?", "60 people down"; 20:41 SMS to/from Mark "Need me?", "Be there @ 07:45"; There have been no notifications sent from RCWT lately; I did get a partial network connection via CC/iPhone, but could not login to RCWT at 10.1.20.156 / [Note added 12/20/21 August 4th is when the W50 most likely blew its fuse, either from the water on the Netonix (load short, most likely cause) or when recovering the SLA after the power was restored (not likely)]	L1 SMS				20210804
		5	Th	~	07:45	~	08:55	Onsite at RCWT: Green lights, both power supplies (WP1, W50, prototype); Battery 70°F 13.02v Micronta (not fully charged, s/b ~13.6v M at 70°F); Load 15.2v M; Mark was onsite last night and found the power supply unplugged, so power was restored @ ~18:15 We8/4; As per everybody there (Mark, Keith and the workers painting the tower) the power was off 1-8 hours; Netonix was destroyed by water (that's what brought down the internet, not lack of battery), Keith replaced it; Load 37-39 watts; Removed possibly water damaged TrippLite UPS 750VA (450W) (I can keep it), they are powering one device with an adapter direct from AC, Keith says "not important, only a few customers" and so I didn't push to have the PoE for that placed on the Netonix and the battery backup, although it might well handle it fine; [Note added 12/20/21 I missed the fact that the W50 had blown a fuse; At the time I didn't have the Extech so there was no way to see the battery charge current; The battery V was low, but that was because it was an OCV (not connected/charging)]	SMS TM21F			B26	20210805
		8	Su					Email to Mark & Keith with invoice for $240-55=$185 net due	EML TM21F				20210808
	Oct	15	Fr	~	12:00	~	12:47	Internet down @ shop (see RW for details); Caused by power loss @ RCWT; 14:14-14:19 Call to Mark (evidently not all of their equipment is being run from PoE from the DC Netonix on the W50)	SMS SSC TM21F L1			B26	20211015
		22	Fr	~	16:13	~	17:11	Internet down @ shop (see RW for details); Caused by power loss @ RCWT	SMS TM21F L1				20211022
		24	Su	~	16:44	~	17:40	Internet down @ shop (see RW); Most likely caused by power loss @ RCWT (but not sure, I didn't contact Mark & Keith)	TM21F L1				20211024
	Dec	15	We	~	18:44			Internet down @ shop (see RW); Caused by power loss @ RCWT	TM21F L1				20211215
		16	Th	~	11:19	~	12:47	SMSs to Keith & Mark "... Is there anything you can tell me?"; SMS from Mark (confirmed it was RCWT power loss) ... / SMS to Keith and Mark "I need to go to rich city: this long power outage will kill that SLA battery dead as a door nail and possibly forever."	TM21F SMS				20211216
				~	12:54	~	13:15	Calls to Mark, Keith and office NA; Call to Brian Long (currently no power issues at RHS); Call to Mark NA; Call to Keith (3m) "Can't go onsite" "Power may not be restored until tomorrow", I asked him to notify me when site is accessible and to ask Mark if he wants me to go check the battery, also told Keith that the Netonix may not run even if power is restored, and Keith confirmed that the 27TMX for RHST is still in the Lexington office	TM21F L5				20211216
				~	14:05	~	14:20	Missed call & SMS from Mark "Call me back I was on the phone thanks"; Call to Mark (1m) he'll call the water company and ask to let me in; Call from Mark (2m) "They'll unlock it" and he wants me onsite if possible	TM21F SMS				20211216
				~	15:20	~	16:15	Onsite: SMS to Mark "No problems getting in"; Power and Netonix are OFF; SLA 12.71vM OCV; SMS from Mark "Let me know as soon as you know if I need to bring over the other battery" / 15:36 W50 powered by Trace, 12.71vM no charging, Netonix is up (~2.65aE @ 15.05vM = ~40w); 15:49 Their other stuff powered by Trace (~0.43aE @ ~120vac = ~52w); Call from Mark (1m, not sure yet, I'll call you) / 16:07 Call to Mark (4m), I told him site is all powered on SAP, the battery is "shot" and the W50 won't handle everything at site (if Keith puts the other stuff on the Netonix ~90w), we agreed to meet at RHS for him to give me the 27TMX and for me to get the W100 from RHST; 16:12 Removed SAP and my equipment (site down); Departed leaving all doors and gate open / 16:18 SMS from Mark "I would like to meet you in the parking lot and give you this battery so I don't have to drive out in the grass"	TM21F SMS L12		WP1	B26	20211216
				~	17:20	~	19:15	Onsite: AC power is ON (site is up); SLA 12.71vM not charging (once again, I did not find out until returning the W50 to the shop that this was due to a blown fuse); 17:33 Removed SLA and W50 (Netonix down) / B58 27TMX (from Mark @ RHS parking lot) electrolyte levels checked and AOK, 12.64vM OCV 12-16⁰C (~92% SoC by OCV); 18:09 Finished installing W100 and 27TMX (site up) / 18:12 W100 plugged into AC (Bulk, Absorption ...); 18:33 SMS to Mark & Keith "RCWT equipment has been powered up since 18:09. AC power was restored at about 5 PM. Load (Netonix) about 40 W. 27TMX and W100 from RHS. If another power failure estimated run time is 24 hours (but you've still got equipment not running on the battery back up)." / 18:34 SMS from Mark (also to Keith) "Can you put ALL the equip on the battery backup?"; 18:57 Absorption 0-4aE 14.81-14.91vM / 19:12 SMS to Mark (and Keith) "No, not without Keith to configure the Netonix"; 19:14 SMS to Mark and Keith "Leaving RCWT (all locked up)."; 19:15 SMS from Mark (also to Keith) 'two thumbs up'	TM21F SMS L1		WP7	B58	20211216
				Attempted login to Netonix but could not connect	TM21F				20211216
		22	We					Political Thoughts for Invoicing (over an hour thinking on the porch); I will reverse/eliminate all charges for RCWT 8/5/21 to date	TM21F WP1				20211222
		28	Tu					20211228 Credit - Richmond City.pdf; 8/5/21 invoice for onsite @ RCWT reversed ($240); No Charge for onsite visit 12/16/21 and subsequent followup; [Emailed 1/3/22]; Restitution and apologies / Recounting of the Events; Recommendations for Further Discussion (W50/SLA should go to WWT, T-105s from WWT should go to RCWT, RHST needs Wiegmann, Schauer and T-105s)	TM21F DBT WP1 B26 L6 L12				20211228
		31	Fr					L1-3 L6-7 L10-16; (RCWT was not scheduled to be maintained, not mentioned)	TM21F DBT				20211231
2022	Jan	3	Mo					20220103 Email to Mark, Keith & Brad 'Account Credit - Richmond City Water Tower'.pdf	TM21F DBT EML WP1				20220103
		4	Tu					L1-3 L6-7 L10-16	TM21F DBT				20220104
	Jun	10	Fr					Call from Mark & Keith: New site LSWT; Discussed RCWT, 27TMX to be replaced with T-105s from WWT (site power is still expected to be >75w); 27TMX will go to LSWT	T48-3 SMS L17				20220610
		28	Tu	~	17:20	~	19:20	Onsite at RCWT to swap batteries: 27TMX (high on top of electrical box) ~26⁰C (~79⁰F); Ambient ~27⁰C (81⁰F); W100_6 fan is running / 14.00vM (13.93vF equivalent, Float V is too high for current battery T, compensation has not reset lately); Float charge ~0.050aE erratic; Netonix load ~2.98aE (~42w) / Cleaned T-105s from WWT and on chair with cardboard to level; Lead posts and ring connectors filed with emery board (corrosion, WWT is a humid site and the cross connect uses old ring connectors) / ~17:48 27TMX removed, W100 unplugged (internet down); ~18:10 T-105s attached (internet up, T400s/T450s NetWorx CM detected this outage, CP notification EML) / W100_6 filter/fan cleaned (compressor), screws tightened; W100 AC connected, initial charge >11aE (Bulk); T-105s electrolyte ~3/16" below factory, ~1/2" above plates, generous fill to meniscus 1/2 up slot / ~19:00 ambient & battery ~29⁰C (~84⁰F), ~14.31vM (~14.24vF equivalent, good Absorption V for current battery T), charge current ~1.5aE erratic; Netonix load ~2.95aE (~42w) / Photos; SMS to Mark & Keith "... gate is locked .. All done"; SMS from Mark "Ok. Thank you"	TM22		WP7	B58	20220628
				TM22 EML IMG SMS			B9/10	20220628
				~	20:40	~	20:45	Back at the shop I tried to login to RCWT to get graphs, but could not	TM22				20220628
		29	We					Battery maintenance, B58 (27TMX): Significant electrolyte loss in transport (probably from tilting to get it down off the shelf at RCWT) / TFTP "proper installations at all sites", "enclosures and proper access", "Look at how much RCWT has cost TurboNet and me!" / Electrolyte generous fill; Equalization caused significant electrolyte loss (see B58)	TM22 B58				20220629
	Sep	7	We					[L3/6/17] 20220630 Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps.pdf / 20220907 Email to Mark & Keith 'Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps'.pdf	TM22 DBT EML L17				20220907
		8	Th					L1/3/10/14-18	TM22 L17				20220908
	Oct	28	Fr					[L3/6/17] 20221011 Report, Photos & Invoice - Wiegmann and Power Cable Assemblies for LSWT.pdf: Emailed to Keith and Mark; RCWT mentioned in report (prerequisite for LSWT)	T48-3 DBT EML L17				20221028
	Dec	22	Th					[L3/6/16-18] 20221021 Report, Photos & Invoice - LSWT Installation.pdf: Emailed to Keith and Mark; RCWT mentioned in report (prerequisite for LSWT)	T48-3 DBT EML L17				20221222
		28	We		12:00		14:00	Onsite at CFS, Discussions with Keith: He said the RCWT equipment is all running on backup (last time I was there on Tu6/28 there was equipment still running on AC); We also discussed why the internet drops out at RW	T48-4 L18				20221228

## L4
Locations: L4	A					TL: TurboNet Lexington office, 924 Main ST

Date/Time CST/CDT					Description	Other Sources	Status	UPS	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Moved	-	-
2017	Aug	31					Meeting with Mark and Keith at TurboNet Lexington office (see yellow sheet notes): They wanted an installed quote on a UPS system for the fiber setup in the basement there, and at first we were talking about installing one of the JC TrippLite 3kVA units with 12 new batteries; I shot photos of the equipment and looked at maximum power ratings (4A and 2A, or 720w) and we talked about it being more like 350w	TA1 IMG	Research			20170831
	Sep	1					I sent Mark and Keith a quote for the Tripp-Lite with 12 new batteries (20170901 Fiber UPS Quote.pdf, $845 installed with adapter cord); This didn't go anywhere for quite a while, and in the meanwhile I got to thinking that it would be wiser to install a smaller inverter in order to maximize battery runtime, and the Tripp-Lite requires a 30A supply circuit which they don't have	EML DBT TA1	Quote			20170901
	Oct	24					I sent Mark and Keith another quote for $850: "UPS for fiber setup in Lexington - Longer runtime option" (20171024 Fiber UPS Quote 2.pdf); This quote for Liebert PS700MT-120 and (2) 100AH SLA batteries / "Bench testing suggests that with a 100 Watt load the system should run for 8 to 16 hours."			A2		20171024
	Nov	2					Rec'd advance Payment of $425 less $12.63 Paypal fee (net $412.37)	EML TA1	On Order			20171102
		6					Batteries ordered from BatterySharks.com (as needed for TurboNet fiber setup in Lexington office, 2x100AH)				B27_28	20171106
		8					Batteries received and installed in test setup (UPS modified for external battery bank); Testing notes (white sheet) / 20171109 Fiber UPS Final Invoice.pdf (sent via email, "The system is ready to go …")	TA1 DBT EML WS	Ready to Install			20171108
		9					UPS and batteries installed on fiber setup in TurboNet Lexington office basement (final payment of $437.63 rec'd from TurboNet, total rec'd $850); 1 Year Warranty (we didn't discuss it, but I'll honor it)	TA1	Active			20171109
2018	Feb	26					Onsite at TL; See WWT for details	L6				20180226
	May	8					I was in Lexington (to install WISPer #2 W100 at WWT): Fiber setup is running somewhere between 113-225 watts (2 bars out of 4 is 450/2 = ~225 watts); I told Keith it would probably only go about 8 hours at that load					20180508
2019	Jul	9					Stopped in Lexington briefly to meet Keith Jones and follow him to Odessa South Water Tower to install W100_3 (WP4)	IMG				20190709
2020	May	8	Fr					Onsite briefly (photos at LWT TurboNet Onsite @ Lexington Water Tower; Mark Webb; Keith Jones)	B27_28 IMG				20200508
	Jul	6	Mo					Onsite; Photos at TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb	WP9 IMG				20200706
		31	Fr					In discussion with Keith at new TurboNet Building/Office in Lexington he revealed that they are trying to move out by the end of August, but if they need to leave equipment at the old office longer than that they will do so	L16	Moving			20200731
	Aug	11	Tu	~	12:05	~	13:45	While with Keith onsite at Swafford tower [RN] he related that he had just gotten the fiber setup with UPS moved to the New Building / (A2/B27_28 L4->L16)	WP10 L16 A2 B27_28	Moved	-	-	20200811

## L5
Locations: L5	A					RHS: Richmond High School, 451 E South St, Richmond, MO 64085

Date/Time CST/CDT					Description	Other Sources	Status	UPS	Batteries		UPS	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	A26	B62-B67	-	A27	B62-B67	-
2016	Mar	18					[L5/12] During March there was a major internet outage caused by loss of power at RHS; Mark Webb begins talking about power backup solutions / See Email "Text for SMS to Mark Webb" which is only part of the SMS/phone conversation concerning these issues, spanning several days	EML SMS	Inquiries					20160318
2017	Nov	9					White sheet notes "Richmond High School" (while in Lexington installing UPS for fiber setup): "Not sure of energy budget - maybe 300 watts"; "William wants 1 hour (TurboNet to piggyback)" / "Will have energy budget estimate, and meet We11/15/17 ~3pm"; Tools list to bring	TA2 WS	Quote					20171109
		16	Th					Onsite with Mark Webb and Keith Jones (TurboNet); Discussed needs with RHS data center manager; Email to Mark and Keith "Re: UPSs for RHS" with 20171116 RHS UPS Quote.pdf ($1700 installed)	EML DBT TA2					20171116
		27					Met Mark at WalMart and Received $1000 advance from TurboNet; Questions about power cord length answered (RHS is installing 30 Amp circuits)	TA2	On Order					20171127
	Dec	7					24 batteries ordered from BatterySharks.com ($390.68): I chose to buy the slightly more expensive 9 AH batteries (more dense)	EML TA2			B29_34	B35_40		B41_46	B47_52	20171207
		12					Batteries received; Confirmed appointment for 12/20/17 to install at RHS (Mark will check with them to be sure 30 Amp circuits are installed)	TA2					20171212
				In garage, exact date unknown: 24 batteries 20171212_1, 20171212_2, 20171212_3, 20171212_4 (B29-52) installed in JC#20 (TL3_2, A26) and JC#21 (TL3_3, A27)			A26			A27			20171212
		20	We		15:00			UPSs (and installed batteries) delivered to Richmond High School (installed, final payment rec'd from TurboNet, total $1700); 1 Year Warranty	TA2	Active					20171220
2018	Jan	10	We					Email to Mark "Re: UPSs for RHS": 'I trust that all is well at the Richmond High School …'; I mention that I have more of these units in stock, and Mark said he's working on another business that wants one	EML TA2					20180110
		12	Fr					Email to Mark "Re: UPSs": 'I've also got (7) of the 6KvA units …'	EML					20180112
2020	May	8	Fr					While onsite in Lexington I asked Mark and Keith to contact them and ask if I could stop by for a quick inspection (it's been 3-1/2 years)					20200508
	Nov	19	Th	~	15:26	~	15:45	Missed call and SMSs from Mark Webb: Major power outage in Richmond; High School wants new or bigger batteries; Contact Mark tomorrow ~9am	SMS					20201119
		20	Fr	~	04:15	~	05:10	TODO and .ods; Email to Mark; SMS to confirm and ask for phone call / Further SMSs ... Meet Tu11/24 10:00 RHS	EML SMS TA2					20201120
				~	07:30	~	08:15					20201120
				~	09:45	~	10:00					20201120
		21	Sa	~	07:25	~	09:30	SMSs to/from Mark asking about RHS purchasing rules and how we'll estimate/quote the job; TODO; Additional thoughts concerning TurboNet Ukraine; LMVM BFMS John (or Kevin)	SMS					20201121
		23	Mo	~	05:45	~	10:30	Researched HUP Solar Batteries (eliminated, smallest is ~845AH ~$2600x6); Researched Indoor Battery Enclosures (custom built from wood); Researched unattended/attended boost charging methods / TODO; Called BFMS, (1) LMVM John and (2) LM w/Chad; Consideration of impact of slightly higher float voltage designed for SLA on this project (water more often, possibly trim charger voltage down somehow, boost charging probably not needed very often); Re-considered Questions to ask onsite and the possibility that they'll want a more standard solution using SLA batteries / TODO outline of "Questions and General Proposal" to be completed tomorrow morning	TA2					20201123
				12:49		12:59	John @ BFMS called and confirmed pricing on (6) 27TMX: $157.25 x 6; Call when order from RHS is confirmed					20201123
		24	Tu	~	04:30	~	06:05	Completed 20201124 RHS Questions and Solutions.pdf / Email and SMS to Mark	DBT EML SMS TA2					20201124
				~	06:50	~	08:25					20201124
				~	09:20	~	11:30	Mark called, Brian has been sent home for two weeks because of Covid; I suggested I go onsite to look at things anyway, and Mark suggested we have a conference call with Brian at home; Prep. to go onsite; Mark called again, put Brian on the line, I asked the initial questions; Travel and onsite; Inspection, see notes on printout of 20201124 RHS Questions and Solutions.pdf [Mileage 22 @ $0.575]	TA2 IMG					20201124
				~	12:37	~	12:42	Call to Mark: "It's another Swafford"; Overheating destroyed the batteries, I'll send a full report in the morning					20201124
		25	We	~	02:45	~	06:05	Tools put away; TODO; .ods; Photos ORC / 20201124.1 RHS Inspection Report.pdf sent to Mark via email; SMS from Mark "I sent it to Brian"	TA2 DBT EML SMS					20201125
				~	07:00	~	11:15					20201125
		30	Mo	~	10:55	~	11:00	Call to Mark: He'll call Brian to see if 11:30 works					20201130
				~	14:45	~	15:00	Text to Mark: "I haven't heard ..."; Brian wants to phone conference Thursday 11:30 'cause "he wants to go to the school and measure"; I said "Maybe we should meet him at the school?"; Mark said "Let's talk then we could always meet him. Or go there if you want at 1130"; I said "It's really up to Brian, what he wants to do"; ... Meet onsite with Brian Th11/3 11:30 (Mark will not be there)	SMS					20201130
	Dec	3	Th	~	09:15	~	10:20	Prep. to go onsite; Reviewed and printed paperwork to refresh my mind; Call to Mark	TA2					20201203
				~	11:15	~	14:00	Travel and onsite; Brian wants the 27TMX solution but we need a 2x3 battery box; Photos of space (13" from floor to door of some connection box they will move forward) / Measured UPS battery float voltages (Fluke, lower 83.3v, upper 83.1) / Brian 816-400-6175 (c), blong@RichmondSpartans.org; Travel to Lexington and discussed RHS quote which should come in at $3,750 with $400 for Mark and Keith; [Mileage 33 @ $0.575]	TA2 IMG					20201203
		9	We	~	07:20	~	09:55	Tools put away; TODO and .ods; Brian Information put in iCloud Contacts / 20201209 RHS UPS Battery Upgrade Quote.pdf; Emailed to Mark & Keith with SMS notification	DBT EML SMS TA2					20201209
				~	10:35	~	12:00					20201209
				~	11:53			From Mark "Looks good ..." and he commented on the maintenance	SMS					20201209
				~	12:54			To Mark "Any maintenance contract is a separate deal that will be negotiated later."					20201209
				~	13:25	~	14:00	Emailed quote to Brian with SMS notification	EML SMS TA2					20201209
		11	Fr	~	12:42	~	12:52	Call from Mark: "It's a done deal."; RHS will pay the entire $3,750 to TurboNet (1-2 weeks); Mark will cut me a check today for $3,350 and meet me in Richmond (2 hours?) / Start work immediately (order batteries, draft the plans)	B62-B67					20201211
				~	13:20	~	13:50	Calls to BFMS (no answers, LMVM); Found the graph paper; Prayer; John @ BFMS called, he checked, all (6) 27TMX are Nov 2020 man'f code / Text to Mark "I'll be in Richmond..."; Meet @ USB @ 15:25; Travel to USB, met Mark & Rec'd $3,350 and deposited / [Mileage 9 @ $0.575]	SMS TA2					20201211
				~	14:08	~	14:18					20201211
				~	14:25	~	14:35					20201211
				~	14:40	~	15:30					20201211
		15	Tu	~	03:30	~	04:35	TODO and .ods; USB SPF; Photos 12/3/20 C, printed; Travel to BFMS and NVD @ Meritex Caves / [Mileage 110@$0.575]	TA2					20201215
				~	08:30	~	13:00					20201215
		16	We	~	06:00	~	06:25	USB/SPF, TODO and .ods					20201216
		17	Th	~	02:20	~	05:20	.ods; Batteries unloaded from Subaru to cart; Cleaned; Labelled; Electrolyte levels checked; OCVs measured; Initial charges started on BK; Conceptual plans for the battery box ...	TA2					20201217
				~	07:20	~	07:25	Battery 1/6 to Float					20201217
				~	09:00	~	09:10	Battery 2/6 to Bulk					20201217
				~	09:50	~	11:30	Battery 2/6 to Absorption; Called Brian to discuss conceptual plans for battery box / He'll start work on the box Mo12/21 and I can meet him at RHS with plans and materials then (he'll call when leaving home, ~9am); ... Conceptual plans for the battery box completed	TA2					20201217
				~	15:20	~	15:30	Battery 3/6 to Bulk					20201217
				~	18:25	~	18:35	Battery 3/6 to Float					20201217
		18	Fr	~	07:55	~	08:25	.ods; Battery 4/6 to Bulk					20201218
				~	09:55	~	10:00	Battery 4/6 transition to Absorption					20201218
				~	10:15	~	11:10	Constructed 12 gauge parallel wiring setup so that all (6) batteries can float together on BK	TA2					20201218
				~	12:40	~	12:45	Battery 4/6 transition to Float					20201218
				~	14:15	~	14:25	Battery 5/6 to Bulk					20201218
				~	15:55	~	16:00	Battery 5/6 to Absorption					20201218
				~	18:28	~	18:33	Battery 5/6 to Float					20201218
				~	19:25	~	19:35	Battery 6/6 to Bulk					20201218
				~	21:15	~	21:20	Battery 6/6 to Absorption					20201218
				~	23:50	~	23:55	Battery 6/6 to Float					20201218
		19	Sa	~	03:10	~	04:40	All (6) to Float on BK	S2					20201219
				~	05:20	~	06:40	Photo of parallel charge setup on gray rolling cart / Detailed dimensional drawings completed; TODO	IMG TA2					20201219
				~	09:30	~	14:00					20201219
		20	Su	~	03:45	~	07:15	Equalization; Research on boost charger needed for Equalization; Mouser order started (but will wait until later as there are other things I need); TODO					20201220
		21	Mo	~	09:00	~	10:00	See white sheet "RHS Mo 12/21/20 ~ 1 hr": SMSs and phone call to Mark Webb; Target for installation moved to Mo1/4 to Mo1/11; Promised to get the box plans to Brian no later than We12/23	TA2 SMS WS					20201221
		23	We	~	07:35	~	11:35	.ods; Battery box specifications finalized; 20201223.0 RHS Battery Box Specifications.pdf; Email to Brian, Mark and Keith; SMS to Brian and Mark	TA2 EML SMS					20201223
		29	Tu	~	04:00	~	07:15	Review of other items needed for Mouser Order / Placed Battery Mart order (Battery Mats); Placed Mouser order	TA2 MOU EML					20201229
				~	08:00	~	08:35					20201229
2021	Jan	4	Mo	~	09:15	~	11:50	Mouser order rec'd 1/1/21; .ods Supplies MW_1 and MW_2; Miscellaneous MV_3 / Removed batteries from BK; Corrected spacing; Fabricated jumpers for 72v setup / MW_1 and MW_2 tested on B62-B67 (97.2v equalization) / Hiccups! Power supplies cannot be used to reach Equalization (need to order supplies that can current limit or with higher power)	MOU S13 S14 Z14 TA2					20210104
				~	13:15	~	13:25					20210104
				~	14:20	~	15:25					20210104
				~	17:15	~	20:15					20210104
		5	Tu	~	03:45	~	06:30	Experiment using BK+S13 to try to reach Equalization: BK and S13 set 48.6v; At 12 mins 92.0v total; At 1.5 hrs 95.9-96.0v total (~197 watts); Research, need to order (2) HRP-150N as they don't used Hiccup overload and they have 250% peak power capacity for 5 secs (with indication that they will cycle until power levels drop within nominal range of 158.4w (316.8w total for 2 PS)	S2 S13 B62-B67					20210105
				~	06:30		07:45	TL3_7 TrippLite 3kva on Bench and cover removed	A31					20210105
				~	16:00	~	16:30	SMSs from/to Brian Long to Mark Webb and me: "Will be at high school today if you want to drop off stuff"; "I can come this afternoon. What time is best?"; Before 230 / [Later when I returned from walking 3 miles in Hardin Conservation area] "Sorry, Brian, I can't make it before 230. Is 10 AM tomorrow morning OK?"; "That will work" / "See you then with the plans and the Ash"; Mouser order placed	SMS EML MOU					20210105
		6	We	~	09:30	~	10:30	Prep. to go onsite and meet Brian with the plans and the Ash; He hasn't even started the box yet, so I have time to finish this project before it needs to be delivered / I asked him to measure to make sure 9 feet is enough battery cable, and he promised to get back to me / But if he doesn't I'll just put the 9 feet I have on the cable, it's only a very small voltage drop at full load of one of the UPSs; [Mileage 10@$0.575]	SMS					20210106
				~	13:25	~	13:35	TODO and .ods					20210106
		8	Fr	~	06:50	~	07:50	Mouser order rec'd yesterday Th1/7; .ods Supplies MW_3 and MW_4	MOU S15 S16					20210108
				~	07:50	~	08:05	Removed batteries from Float on BK+MW_1	B62-B67 S2 S13					20210108
				~	08:05	~	09:00	MW_3 and MW_4 in series tested on B62-B67 (97.2v Equalization): Once again, cannot reach Equalization before one of the power supplies shuts down (power must be removed and reapplied to try again); These power supplies try much harder than the LRS-150F did, but they fight each other for about 3 minutes then quit	S15-S16 B62-B67					20210108
				~	09:00	~	09:45	MW_3 and MW_4 in series/parallel (tied the middle of the string to between the two power supplies): Once again, cannot reach Equalization of 97.2v					20210108
				~	09:45	~	11:10	MW_3 and MW_4 set to 45.0v each (15.0x6=45.0x2=90.0), reached maximum 89.9v before quit; 14.5x6=43.5x2=87.0 is OK, power supplies stop buzzing within a few seconds and it holds; TODO					20210108
				~	11:25	~	11:45	TODO Ideas to perhaps use the BK on one battery to characterize what I'm up against (tabled until later) / Research, Lead-Acid Battery Thevenin Circuit (this is too complex a study to be any good in this need)					20210108
				~	11:45	~	14:00	Temporary wiring of TrippLite to batteries (fabricated Red/Blk #8 with ring connectors and connected to screws inside TrippLite @ rear battery connector)	A31 B62-B67					20210108
				~	14:00	~	15:15	Temporary wiring of TrippLite to AC; Float started at 14:28 (82.95v=6x13.825v) which is 1.95v above Trojan recommendations (81.0v=13.5x6); TrippLite outputs ON (same Float) / MW_3 and MW_4 ON (has no effect on TrippLite); Photos Bench Testing for Turbonet and Richmond High School (RHS) UPS Battery Contract	IMG					20210108
		10	Su	~	11:15	~	12:50	Powered down the TrippLite and removed power (AC and battery); Removed blue glue from a potentiometer near the rear battery connection entrance / Reapplied power and adjusted ... but it doesn't seem to affect the Float voltage at all (left it where it was as close as possible) / Conclusion at this point is that we'll have to live with a Float voltage that is slightly higher (82.95v=6x13.825v) than Trojan specs (81.0v=6x13.5)	A31					20210110
		11	Mo	~	10:30	~	11:15	Test fitted one of the DC cables from a 6kva battery module and it fits the 3kva units; Research on connectors "CO-2 400V 40A", the only way I can see to get more of these is to buy used TrippLite battery modules without batteries (found some on eBay); Nathan might be able to help bring me more salvage units					20210111
				~	11:15		13:00	Experimented with Equalization boost chargers; 2x43.5=87.0=6x14.5v (OK from before); 2x45.0=90.0=6x15.0v (PSs quit, TrippLite Error); 2x44.1=88.2=6x14.7 (PS OK, but Error) / 2x43.8=87.6=6x14.6 (OK, started 2 hour test); Note that there is no way to clear the Error without dropping the loads as the unit must be turned OFF, AC removed/reapplied and then turned ON / CONCLUSIONS (1) 14.6v equivalent is the highest that can be set w/o TrippLite Error and even this may be marginally too high, (2) The power supplies have enough "oomph" to handle 14.7v equivalent so they s/b adequate at 14.6v equivalent	S15-S16 A31 B62-B67					20210111
				~	14:00	~	14:30	TODO					20210111
		12	Tu	~	08:30	~	10:00	Photos from Fr1/8 ORCPD; Checked the electrolyte level on the batteries in the rear room on the network UPS (in order to better gauge water depletion due to slightly higher Float) / See B4-B7 for details and conclusions; Water use depends on temperature as well as Float voltage and 5 months is the maximum we should wait to add water for B4-B7 (which is probably the initial period we need to schedule for RHS); Photos of B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	B4-B7 IMG					20210112
		14	Th	~	14:00	~	15:00	Obtained (2) DC cables from 6kva Tripp Lite battery modules TL6_5_B (A21) and TL6_6_B (A24)	A21 A24					20210114
				~	17:40	~	18:40					20210114
		15	Fr	~	06:50	~	11:30	Researched what is needed to access the Tripp Lite 3kva units via port(s) and ran some tests; See TL3_7 for details and conclusions / Web interface is of particular use in seeing a more exact load %, and it does reveal some things that can't be seen from the front panel (including logs of events)	A31 B62-B67					20210115
				~	11:30	~	14:45	Searched storage for a metal box that can be used for the boost chargers (nothing found); Planned location of boost charger box (front of battery box top right) / TODO Find source for box (min 8x8x2" WxHxD, max 11.5" H); Spliced 2x DC cables to #4 AWG Red/Blk and #10 Grn (photos/videos) ...	IMG					20210115
		16	Sa	~	04:15	~	06:30	Spliced 2x Tripp Lite battery module DC cables to #4 AWG Red/Blk and #10 Grn (photos/videos); Removed temporary battery wiring from TL3_7/B62-B67 and replaced with new assembly / Replaced cover on TL3_7	IMG A31 B62-B67					20210116
				~	08:50	~	12:05					20210116
				~	12:05	~	13:25	Tripp Lite TL3_6 moved from W storage to bench and 2nd battery connection attached; Cheater cord to switchable 120vac (it won't be used for full-power testing); TL3_6 Float is 82.5v, which is good news as it is ~0.5v lower than TL3_7 and this indicates that the usual Float voltages on these 3kva units may be a closer average to Trojan specs than I thought	A30 A31					20210116
				~	13:25	~	16:45	Load testing begins with TL3_7 (see for details): (TL3_6 is OFF no AC); Set up output load of 85% (perfect, probably higher than RHS current loads) / Discharge began at 15:05 and TL3_7 quit (shut off) at 16:33 (total discharge time 1 hr 28 mins); Restored AC, also turned on TL3_6 to speed recovery (no loads)					20210116
				~	18:00	~	19:15		A31 B62-B67 A30 SSC					20210116
		18	Mo	~	05:15	~	09:15	Recovery nearing completion, see B62-B67 for details / With both TL3_7 and TL3_6 charging recovery required ~2 days, and so with only one UPS charging it would be ~4 days / Images and videos from Friday and Saturday ORCPM; .ods listed equipment "IMG"	B62-B67					20210118
				~	11:45	~	12:30					20210118
				~	13:00	~	13:30					20210118
				~	13:30	~	16:45	2nd discharge test, 75% load; See TL3_7 & white sheet for details; TL3_7 quit at 1 Hr 40 Mins; See TL3_6 for details on A30 self destruction when starting recovery; Battery bank OCV stabilized, 73.3v (57% SoC as per Trojan); Recovery started @ 19:05; Conclusions (1) Tripp Lites will not operate below ~10.8v (by design to avoid ruining SLA batteries), (2) To get the most from FLA batteries the inverter needs to keep operating down to ~9.6v, (3) This 2nd test was at the median low as per front panel bargraph (which has a wide error bar), (4) My quote of "> 2 Hrs" was in error (will confess)	A31 B62-B67 A30 SSC TA2 IMG WS					20210118
				~	17:30	~	19:45					20210118
		19	Tu	~	07:00	~	09:10					20210119
				~	09:10	~	10:30	Boost charger box procurement: Order placed for free store pickup at Gladstone Lowe's; Attached Murata DC meter MV_3 to battery bank with clip leads	EML TA2 Z14					20210119
				~	11:00	~	11:05	Lowe's in Gladstone called, they have no stock but there are (32) at the Independence Lowe's					20210119
		20	We	~	13:15	~	14:15	Visited Scott's Bargain Barn to look for a boost charger box, but they didn't have anything suitable (browsed for parts/tools/supplies for shop) / Picked up an 8x8x4" NEMA 1 screw cover junction box at Lowe's in Liberty; [$21.77; 41 miles @ $0.575]	TA2					20210120
				~	16:30	~	18:30					20210120
		21	Th					Recovery from 2nd discharge test completed: 22:08 Boost ON for 4 hours until Fr1/22 02:08 [~15 mins birddogging]	B62-B67					20210121
		27	We	~	11:50	~	13:00	TODO & .ods; Note that the difference between the Murata and Fluke is now about -0.25v (Murata Boost 87.35v, batteries depleted ~64.35) / Videos and photos of butt splicing and bench testing sent to Brian Long, Mark Webb and Keith Jones; "Brian, the final bench testing was completed last week. How's the battery box project?"	Z14 SMS					20210127
				~	13:15	~	14:15	Planned how to assemble the boost box; 8x8x4" is tight, not easy to get it all in, and can't get to the screws for the electrical connection ...					20210127
				~	18:45	~	19:00	SMSs from/to Brian Long: [photo of box shot on 1/22/21] "Box is built. Need to finish. I have been sick. Hoping to be back tomorrow." / "It looks great! You did a super job Brian. Keep me posted, I'll be ready with a day's notice."	SMS IMG					20210127
		28	Th	~	00:00	~	01:30	Decided to place all the components in the boost box mounted to the cover; Will be easier to mark if I buy a protractor ...					20210128
		30	Sa	~	22:45	~	23:10	Photos from 18th and 22nd ORCP					20210130
2021	Feb	2	Tu	~	12:00	~	21:00	[Span of time but many long interruptions, subtract ~ 5 hours] No protractor yet (I ordered one yesterday) but proceeding to mark holes on the cover for the mill by X-Y coordinates (photos)	IMG					20210202
				~	21:00	~	02:00	Drilled holes on the mill; Everything fits					20210202
		3	We	~	12:15	~	12:45	Some cleanup; Photo of box sent to Pasha					20210203
		4	Th	~	14:00	~	14:30	Searched for best way to run wires from boost box into battery box: Will use left side knockout and a romex clamp (with wires in shrink running into battery box)					20210204
		6	Sa	~	04:20	~	09:20	Mounted components and began wiring up the boost box					20210206
				~	10:40	~	11:30	Scott's Bargain Barn fuse holders and 1/4" shrink tubing [26 miles @ $0.575]	TA2					20210206
				~	14:30	~	15:15	Boost box assembled (photos) / Labels applied / Attached to battery bank (photos) / Started 3 hour Boost/Absorption test @ 14:15 (concluded at ~17:15, highest temperature seen on front center of box ~102°F)	IMG B62-B67 S15-S16					20210206
				~	16:40	~	17:45					20210206
				~	17:55	~	18:20					20210206
		7	Su	~	10:55	~	15:45					20210207
		8	Mo	~	14:05	~	14:50	Redo of Battery Bank Voltage label (Boost sees as low as 87.2) / Photos from 2nd, 3rd and 7th ORCP for CC Facebook timeline post ...					20210208
				~	15:45	~	16:00					20210208
				~	18:45	~	20:00					20210208
		9	Tu	~	04:05	~	13:35	Photos from 1/22, 2/2, 2/3 and 2/7/21 prepared [P] for CC Facebook timeline post and distribution; Video of Boost being turned on and off; Facebook post completed	IMG					20210209
		19	Fr	~	15:05			SMS from Brian Long (also to Mark and Keith): / "Putting last coat on the box this afternoon, so will be ready next week. We will want to do the switch after 4, to minimize impact. How long do you think the switch/installation will take?"	SMS					20210219
		20	Sa	~	12:25	~	12:45	.ods; SMSs to Brian, Mark and Keith concerning scheduling for the installation and switchover					20210220
				~	13:12	~	13:27	SMS from Mark (also to Keith): Better to do the switchover early in the morning before 8am / LATER SMS to Brian, Mark and Keith "Early morning works for me, if that's what Brian wants to do, I'm up for it (6am AOK). But first I must set up the battery bank, on a previous day."					20210220
		22	Mo	~	10:50	~	11:20	SMSs from/to Brian Long (with Mark Webb and Keith Jones): 08:39 assembling the bank can be done at any time, the box is done, but must wear a mask; 08:41 Brian doesn't like the switchover at 06:00 (and it puts is in a deadline position because network MUST be up by 07:15); 11:19 to Brian (Mark and Keith) "No problem with the mask, I will comply. I only said I don't do it if I don't have to. And when I delivered the plans there was no need." + "Assemble battery bank We9am? With a 07:15 deadline I vote against the 6am switchover. Suggest switchover Wednesday 4pm."					20210222
				~	11:30	~	11:50	SMS from Brian, Assembly We9am OK; We4pm not OK, must be Thursday or Friday; SMS to Brain (and Mark and Keith) Thursday OK for both? 9am assembly and 4pm switch over; SMS from Brian "Works for me, need to confirm with Mark"; SMS from Mark "Switch over has to be early in the morning ..."; SMS from me "5am then"; From Mark "6am works for Brian. You guys figure out a date and let me know."; From me: "6am does not work for technical reasons. It's a [If the] load balancing takes more than an hour we won't have enough time."; From Brian "I can make 5 work if that is the only time"; From me "I don't care when, but Mark seems to care. We9am assembly, Th5am switchover. OK?"; From Brian "Works for me."; From me "See you!"					20210222
		24	We	~	06:35	~	11:50	Powered down the TrippLite and removed power (AC and battery); Installed 125A fuse with foam support block; Powered up; Examined photos of #20/A26/TL3_2 and #21/A27/TL3_3 and they have web interfaces; Set up access using T450s2 and cradlepoint router; SMS to Brian (+Mark/Keith) "I won't be able to be there at 9, probably 11-12, I'll text you when I know more exactly." / Cut battery mats 6-3/4x12" -1/16"; Battery box labels printed; B62-B67 electrolyte levels are OK; Loaded Subaru; SMS to Brian "12:45 OK?"; SMS from Brian "Needs to be ..."	SMS B62-B67 A31					20210224
				~	12:15	~	17:00	Travel and onsite: Boost charger mounted to their battery box, which looks great; Batteries installed; Cables hooked up and attached to UPSs / Top UPS #21 (A27, TL3_3) 82.8-82.9v, bottom #20 (A26, TL3_2) 83.1v (MuRata+~0.25=Fluke), will put all loads on top UPS / Tested webcards on RHS TrippLites, top #21 (TL3_3) 41% load, bottom #20 (TL3_2) could not access (needs reboot?); Removed batteries from TL3_2 and TL3_3 (to shop); Photos; [Mileage 20@$0.575]	TA2 IMG S15-S16 Z14 B29_34 B35_40 B41_46 B47_52		A26	B62-B67	-	A27	B62-B67	-	20210224
		25	Th	~	04:30	~	07:15	Onsite again to switch loads over to top UPS; Boost voltage is set too high, the bottom UPS went into OVP bypass beep and error; Adjusted boost down using Fluke, was 43.75v each supply, now 43.25 each supply (14.425 equivalent), 86.3v on Murata (battery bank sticker is wrong); Brian moved all the loads from bottom UPS (TL3_2) to top UPS (TL3_3) without bringing anything down because they have dual power supplies; T450s2 reports 70% total load on top UPS (2nd discharge test @ shop was @ 75% 1hr40mins, so estimated run-time 1hr50mins, front panel bargraph 3rd of 4 LEDs blinking) / Explained reasons why my quote of ">2 Hrs" was in error (TrippLites only discharge to 10.8v, etc.); Bottom UPS unplugged and mentioned to Brian that he can plug it in to speed recovery / "Pulled the plug" for 5 mins (AOK, 12v equivalent); Applied (2) labels for front of UPSs TL3_3 and TL3_2 "2/24/21 Batteries Removed ..."; Photos; [Mileage 20@$0.575]	TA2 IMG S15-S16					20210225
				~	08:00	~	08:30	TODO and .ods / Emptied Subaru (except salvage batteries); T450s2 put away	TA2					20210225
				~	09:40	~	10:40					20210225
		27	Sa	~	11:00	~	11:45	TODO and .ods; TA2 files re-labeled / Reprinted boost box battery bank sticker (Boost is 86.3v Murata)					20210227
2021	Mar	3	We	~	05:00	~	09:00					20210303
				~	13:30	~	16:10	Test UPS TL3_7 moved to storage; Salvaged batteries from RHS installed in TL3_7 and TL3_5 and Float rotation started (can only charge one UPS at a time)	A31 A29 B29_34 B35_40 B41_46 B47_52					20210303
	Jul	21		~	19:30			LMVM Brian Long "time for a water check" and "it's been 5 months" and "let's arrange a time"					20210721
		26	Mo	~	15:00	~	15:05	Appointment for We7/28 14:30; He was on vacation last week; He says he's been keeping the space cool, they charged the A/C and put up a curtain					20210726
		28	We	~	14:30	~	16:00	Onsite: Battery 82.8v Murata, 73°F; Brian reports the loads have not changed (3rd of 4 LEDs blinking) / Electrolyte levels ~+3/8" above plates and ~3/8" below factory (which is where I had it on delivery 2/24/21); Generous fill (top of meniscus to score line, 1" above plates) / I predict that if temperatures and water usage stays the same the maximum time between waterings s/b about 12 months / I forgot to put the new sticker on the boost box (still floating around here, I may try to remember to stop by) / I forgot to run boost after watering; Upon returning to shop later I called and LMVM for Brian to run boost for 3 hrs	TA2					B62-B67		20210728
	Aug	3	Tu					I finally got through to Brian and he reported that he ran 3 hrs boost (probably yesterday Mo8/2)					20210803
	Oct	1	Fr					(24) batteries removed 2/24/21 taken to Midwest Scrap Management; They had been in A29 and A31 for charge rotation, but I don't know why I bothered, they were very weak	BR					20211001
	Nov	16	Tu		10:48		12:52	SMS from Brian Long: "Just letting you know. We had a significant power outage last night. By my estimate, the core equipment was powered up for approximately 3 hours after power was lost. Very impressive" ... / SMS to Brian "Thanks for letting me know! That is impressive, I estimated the run-time at slightly less than 2 hours. Have you reduced the equipment load since my visits in February and July?"	SMS					B62-B67		20211116
				12:53		12:55	SMS from Brian: "I believe just by a small server, but I did add a switch. So figure about the same." ... / SMS to Brian "Well, my estimates are usually conservative. In this case, very conservative. Glad to hear the news."; [Forwarded Brian's first SMS to Mark and Keith]					20211116
	Dec	16	Th	~	12:59	~	13:01	Call to Brian Long (RCWT power loss): No power issues @ RHS except very brief outages yesterday evening	TM21F L3					20211216

## L6
Locations: L6	A					WWT: Wellington Water Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				No Backup	-	-
2017	Sep	6					Installed WISPer Prototype #1 at RCWT and began thinking about designing WISPer #2, but the initial thoughts were all based upon improvements to the dual supply with Schottky design / (see WISPOWER #2 Design Thoughts 9/6/17): This design work for WP2 (W100_1) was done thinking that this better WISPer would be installed at RW, but it eventually got installed at WWT	WRD TW2-3	Design			20170906
2018	Feb	9					White sheet "WISPOWER - new idea": Unregulated DC for Genasun solar input	TW2-3 WRD WS				20180209
		25					Test setup for validating initial idea with Genasun (very encouraging): OK with BK_1, Schottky in air, Genasun_3 (cost from 8/6/15 purchase) and 27TMX battery 20150422 (Wattmon_9 and C252_2 used for observation); Schottky diode destroyed, but Genasun OK without it / Photo sent to Mark and Keith via email "Re: AC at RW?" and mentions "Proof of principle, better DC UPS (WISPOWER) design" and "I think I could sell these initially for about $400 (battery not included)"	IMG TW2-3 WRD EML				20180225
		26					Lexington TurboNet office: I pitch the idea in person and Mark gives me a check for $400 for WISPOWER #2 for RW (including removal of solar system, not including battery) / Mileage 42 miles @ $0.54 [The $400 was later applied towards WISPer #2 at WWT]	TW2-3 WRD L4				20180226
	May	2					Email from Keith "backup power supply": He ordered WISPer for Wellington Water Tower; Details, battery size estimate, battery pricing	EML WRD	On Order	WP2		20180502
		3					$780 20180503 Invoice - Wellington.doc emailed to Mark and Keith with 3/13/18 photo; Mark applied the $400 he paid me on 2/26/18 to it, and will mail me a check on Fr5/4 (I had never given him an invoice, I thought the $400 was for the WISPer for the Rayville Water Tower, but in his mind he's not ready for that one yet)	DBT EML TW2-3 IMG				20180503
		7					Rec'd $380 final payment for Wellington Water Tower	TW2-3				20180507
		8			11:00		14:45	Onsite, Lexington and Wellington: Installed; Photos and video at WWT (W100_1, DE_2, Genasun_3, 20160421_2/4, 20160421_3/4)	IMG	Active		B9-10	20180508
				18:45		20:30	Emailed 4 shots + video to Mark and Keith	EML				20180508
	Nov	30					Email to Keith and Mark "Wellington Water Tower Flooded Trojan T-105 batteries": Have they been watered? - No, but Mark says they will do that soon.					20181130
2019	Apr					Phone conversation with Mark where he mentions in passing that "Yes, we did water them." Not sure when they were watered, and not sure exactly when he told me this, but probably in April 2019	B9-10				20190430
2020	May	7	Th					Mark reports that Keith was onsite "a few days ago" (phone call while returning from BFMS in KC)					20200507
		8	Fr					Keith reports that when he checked the electrolyte levels only "a little" water was needed (maybe 1/8")					20200508
2021	Mar	9	Tu	~	11:00			IP and credentials for Netonix rec'd from Keith; 10.10.10.87, admin, @rrow1963; SMTP configured and tested; Warning voltage 12->13; Float is 13.9v and load is ~170 watts (!) as per Netonix (not calibrated yet)	EML TM21S DBT				20210309
		12	Fr	~	13:30	~	16:05	Onsite for the Backup Power Supply Maintenance Program; Keith was with me and we puzzled over why the Netonix reports ~170 w load; Either the Netonix is not properly reporting the loads or the cabling/loads have power leakages; Port 1 is ~96w (Mimosa from Richmond) and Port 5 showed as ~37w (this is a backup cable run, s/b 0 watts, we disabled PoE and total wattage dropped to ~133w) / Keith said that if anything the total watts s/b less than it was when it was installed (unfortunately I did not record the load watts then, but Keith said in the 5/8/18 video at installation "we're running 2 Mimosas and 2 access points"); 14:18 SSC of Status showing ports; There is no fan filter (WP2 was built without it); W100 was VERY DIRTY and the fan was NOT running (moth/debris blockage) / Load is above the 5.1 amps the BK can put up, otherwise I would have disconnected the battery to clean corrosion build-up on the cable connections; Electrolyte levels down ~5/8" (1/4" above the plates) / ~52°F; Battery 13.93 Fluke, Netonix 13.87, therefore calibrated to remove that very slight error; 20 min discharge to 12.5v (SSC); Notification warning after 9-10 min (threshold 13.0) / Therefore set notification warning threshold of 13.2v for warning at 4-5 mins; Recovery to Absorption 14.7v (SSC); Later at shop I saw the Absorption end after ~2.5 hrs and Float 13.9v	DBT TM21S SMS SSC		WP2	B9-B10	20210312
		13	Sa					Email Report to Mark and Keith; Recommended tshooting high power levels; Run-time Estimate ">12 Hrs @ 133 watts"	EML TM21S				20210313
	May	9	Su	~	05:45	~	07:20	1 hr 35 min power failure; 2-1/2 hr Absorption 14.7v; Float 13.93v	EML SSC TM21S				20210509
		10	Mo					Email to Mark and Keith "Re: Wellington Water Tower, Sunday Power Failure"	EML TM21S				20210510
	Jun	13					(3) Email notifications "Low voltage warning"; IP has changed and I can't log in, email subject says 10.0.0.42	EML				20210613
		23					Since the 13th there have been daily "Low voltage warning" notifications (3-9 per day); Maybe they are spurious, but I doubt it; Perhaps Keith has overloaded the power supply					20210623
	Jul	31	Sa	~	08:48			SMS from Mark Webb: / "Every Friday night early Saturday the power goes off at Wellington and brings our radios down. I need you to check on that and fix it please. With our battery backup I would think it shouldn't go down."	SMS				20210731
				~	13:40	~	13:50	Call to Mark: The link from Odessa goes down and they must reboot it to restore service; Contact Keith; LMVM & SMS; 14:04 SMS from Keith, we'll have to talk on Monday					20210731
				~	15:50	~	16:15	SMS to Keith: "If it is possible for me to login to the Netonix at Wellington, from Rayville, I might be able to learn more about the power system in order to solve this issue. I cannot do that since you changed the IP. At your convenience, please send me the IP and credentials."; "I do not suspect that the power system is causing these problems, but I won't know for sure unless I go on site. I suspect either your Netonix or your Mimosa or your cabling has a defect. I reported anomalies to you in my report from my last visit there. You may have to start by replacing the Netonix."					20210731
	Aug	2	Mo	~	16:14	~	16:20	SMS from Mark "Call Keith in the morning around 9 and let's get a plan for the Wellington water tower battery backup Thanks"; SMS to Mark "I sent this to Keith on Saturday: ... [copy]"					20210802
		3	Tu	~	13:10	~	13:15	Call to Keith (did not LMVM); Call to Mark (did not LMVM); Another call to Keith 13:58 (did not LMVM); ~14:05 Call from Mark "he'll contact me if they have a replacement Netonix for WWT"					20210803
		4	We	~	10:55	~	11:45	09:27 & 10:33 missed calls and 10:27 SMS from Mark; I called Keith and we discussed tshooting for 50 mins; WWT AC power was off for 2 days 1-2 months ago; Netonix is reporting 13.4v, 151.6w total, 96w Mimosa, 39-40w "5A access point", 3w "AC unit"; Keith sent photo of his monitor showing 10 min graph of Power Supply Input Voltage, 13.4v, spike every 9 mins to 370 watts (Netonix is wrong, MAC ec:13:b2:82:08:24) / Keith says he can disable "5A access point" permanently (but I said DON'T DO IT NOW); Keith disabled SMTP notifications; Appt. to go onsite 11am Th8/5 Lexington (TODO)	SMS IMG DBT			B9-B10	20210804
		13	Fr	~	10:40	~	12:10	Onsite with Keith: Battery 13.34v Fluke, 78°F, very high humidity; Logged into Netonix, (2) SSCs; Unplugged port 1 Mimos and port is still showing 96-97 watts (Netonix is bad) / Cleaned battery terminals (much corrosion build up); Keith replaced the Netonix with a new one (he copied the configuration from the old one); 10.0.0.187 admin, @rrow1963 / Port 6 "58-Ap" is not enabled (Keith says they don't need it at all); New Netonix shows ~23 watts total load (SSC); Electrolyte +1/4 to 3/8" above plates, with one cell much higher (20160421_2/4 middle cell) / Generous water fill to +1/8" above cup (top of meniscus @ score line); Compressor, cleaned fan and W100; I set the threshold down from 13.2 to 13.0v; Tested notifications; [Email with invoice sent 8/16]	SMS SSC DBT EML TM21F				20210813
		16	Mo					[L6/13/14] Email to Keith (CC to Mark): Please disable SMTP notifications for Odessa North, Skeeter & Wellington (they are sending daily spurious notifications)	EML TM21F				20210816
		22	Su					[L6/13/14] Approximate date that Keith disabled the SMTP notifications at WWT (last date of spurious email)	EML				20210822
	Dec	28	Tu					20211228 Credit - Richmond City.pdf; Recommendations for Further Discussion (W50/SLA should go to WWT, T-105s from WWT should go to RCWT)	TM21F DBT L3				20211228
		31	Fr					L1-3 L6-7 L10-16; (WWT was not scheduled to be maintained, not mentioned)	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
	Mar	6	Su	~	19:30	~	21:45	Lexington Area Power Outage: [power was off at LWT for ~2h15m]; WWT power also may have been interrupted	TM22 L10				20220306
	Jun	10	Fr					Call from Mark & Keith: New site LSWT; Discussed WWT, now only 4 customers and Keith does not care if no battery backup (customers on WWT could eventually move to LSWT) / W50/SLA (shop) should be installed so that T-105s can go to RCWT (W100 slated as spare); (This move will free-up a 27TMX for LSWT)	T48-3 SMS L17				20220610
		28	Tu	~	14:20	~	14:55	Onsite at TLNB: Keith stated his intentions that WWT would eventually be AC only (3 customers) and that he'd pull the W50/B26 (yet to be installed there today) for use at Carrollton (L18 CFS)	TM22 L16				20220628
				~	15:15	~	16:30	Onsite at WWT: Photo of tower from highway / T-105s ~27⁰C (81⁰F); W100_1 and ambient ~34⁰C; W100 fan is running; T-105s 13.515vM (13.44vF equivalent, good Float V for current battery T); Float ~0.035aE; Electrolyte OK (will fill at RCWT) / Netonix load 1.89aE (~25w); ~15:31 W100 & T-105s removed (internet down); ~16:01 Netonix on B26 SLA (internet up) / W50 AC power connected, initial charge >7aE; BTS silver-taped to top of battery ~35⁰C (~95⁰C); 13.34vM (13.27vF equivalent, good Float V for current battery T); Float ~0.030aE / Netonix load 14.99vM (14.92vF equivalent), 1.70aE (~25w); Call to Keith NA (I was hoping to ask him to login and check the Netonix)	TM22 IMG		WP2	B9/10	20220628
				TM22		WP1	B26	20220628
				~	16:40	~	16:45	Onsite at TLNB: Returned WWT keys and mentioned I was headed next to RCWT	TM22 L16				20220628
	Jul	19	Tu					Call from Keith: Ordered new site CFS; He removed the W50/SLA to take to CFS (sometime while I was in CO in the past two weeks); Site is running on AC Netonix (he does not care about the 3 customers)	T48-4 L18	No Backup	-	-	20220719
	Sep	7	We					L3/6/17	TM22 DBT EML L17				20220907
	Oct	28	Fr					L3/6/17; WWT mentioned in report (prerequisite for LSWT)	T48-3 DBT EML L17				20221028
	Dec	22	Th					L3/6/16-18; WWT mentioned in report (prerequisite for LSWT)	T48-3 DBT EML L17				20221222

## L7
Locations: L7	A					OSWT: Odessa South Water Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	WP4	B1
2018	Jul	14	Sa					Email to Mark & Keith "Potential customer": Nathan Van Duyn referred them to me, and I checked to see if they could get service from OSWT which is ~9.5 miles from their home in Kingsville	EML TW4-5				20180714
2019	Jun	3	Mo		13:51		13:54	Mark Webb called to request I contact Keith to discuss W100 for Odessa					20190603
		4	Tu		08:50	~	15:05	Attempted contact with Keith; Mark Webb called and confirmed order for W100, smallest size battery and onsite installation at Odessa; …; Keith called, Odessa has DC Netonix and a "900" which runs on AC (which he does not care to battery back even though we could buy a small inverter), confirmed order for W100, I have 2-3 weeks (but I told him I needed 1-2 weeks)	SMS	On Order	WP4		20190604
		5	We					Purchased Trojan 27TMX at BFMS; 20190605 (B54)	TW4-5			B54	20190605
		8		~	03:30	~	04:30	Created Invoice for TurboNet "20190604 Invoice - Odessa W100"; Emailed to Mark and Keith	DBT EML TW4-5				20190608
		11		~	11:00			Mark met me @ USB in Richmond and I rec'd $796.50 check in payment of invoice 20190604	TW4-5				20190611
		18		~	15:15	~	15:45	Photo of WP4 and WP5 side by side	IMG				20190618
		28	Fr	~	03:30	~	13:30	Photos of W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2					20190628
	Jul	8		~	14:25	~	15:10	Called Keith Jones about scheduling and the possibility of leaving B54 here and installing B1 from RW @ Odessa: / WP4 and B1 to be installed in Odessa tomorrow, meet in Lexington at 1pm (OK to swap RW/Odessa batteries so that I can continue testing with B54, which is the better battery)				B1	20190708
				~	15:10	~	16:40	Videos and photos of Series Test setup (shows WP4, WP5, B54 and B1)	IMG				20190708
		9			12:45	~	17:25	Loaded Subaru; Travel to Lexington, followed Keith (S on O, cross I-70, continue S on M then W on U ~ 2.8 miles) to Odessa South Water Tower (OSWT, 9271 Donaldson Rd, Odessa, MO 64076, Water Tower "PWSD No. 1 Lafayette"); Onsite 14:05-15:25, Helped Keith install W100_3 (WP4) and B1; Photos; Netonix is currently using 24-28w; Return travel		Active			20190709
		10					SMSs from/to Keith Jones: "Latest power usage" (screenshot); "Seems to bounce between 25-33"; "Assuming 29 watts is the average the battery will go 24 hours to 50% discharge (a safe discharge for the battery) ... Or 48 hours if you don't mind abusing the battery (100% depth of discharge, totally dead)."; "Thanks Jeff" / "Be sure to set a notification SMS from the Netonix if the battery voltage drops below 13.0 volts as otherwise you may not know the AC power is off until 48 hours after happens."; "Gotcha thanks again"	SMS				20190710
2020	May	7					Mark reports that Keith was onsite "a few days ago" (phone call while returning from BFMS in KC)	B1				20200507
		8					Keith reports that on that visit "no water was needed" (discussion while onsite at LWT)	B1				20200508
2021	Mar	9	Tu	~	10:45			IP and credentials for Netonix rec'd from Keith; 10.10.11.216, admin, @arrow2013; NTP and SMTP configured and tested; Warning voltage 12->13; Float is 13.9-14.0v as per Netonix (not calibrated yet)	EML TM21S DBT				20210309
	Apr	5	Mo	~	14:45	~17:15		Onsite for the Backup Power Supply Maintenance Program; Electrolyte levels down 5/8 to 7/8" (very top of cell 5 exposed); 78-79°F, Float was 14.175 Micronta (14.1 Fluke) / 8-port Netonix refused to calibrate, Power Supply Input voltage reads ~1% low; Load ~17 watts (corrected); 25 minute discharge test, notification email sent at ~8', but as the float voltage should not be that high (even though the Netonix reads low) I did not change the threshold from 13.0 volts; New float value after discharge 13.5v (Fluke from Micronta) 13.35v (Netonix) which is exactly to Genasun specs for that temperature	TM21S SMS		WP4	B1	20210405
		7	We					Netonix MAC ec:13:b2:e1:b0:50; Gate key from Mark labeled; Email report for visit of Mo4/5 sent to Mark and Keith	TM21S EML				20210407
	Jun	11					Yesterday and today (17) Low Voltage Warnings; IP has been changed to 10.0.2.223 as per email Subject and I can't login; As of 6/23 there have been no new notifications, perhaps Keith turned them off	EML				20210611
	Dec	1	We	~	09:40	~	09:42	Low voltage warning ...; Unexpected link change on port 6 (spare); Can't log in, of course, and I didn't bring this up with Keith and Mark (it may have been a very short failure, or a spurious notification)					20211201
		31	Fr					L1-3 L6-7 L10-16; OSWT Not Maintained as Hoped (last visit 4/5/21)	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
	Apr	5	Tu					Netonix notification "unexpected link change ..."	TM22 EML				20220405
	Jul	22	Fr					(17) "Low voltage warning" EMLs received from Netonix					20220722
		23	Sa					(8) "Low voltage warning" EMLs received from Netonix; Email to Keith "HI KEITH! ..."					20220723
		24	Su					(14) "Low voltage warning" EMLs received from Netonix					20220724
		25	Mo					(20) "Low voltage warning" EMLs received from Netonix; EML to Keith bounced; SMS to Keith "... reboot ... [or] disable ..."; SMS from Keith "Will do won't be till morning"	TM22 EML SMS				20220725
		26	Tu					(7) "Low voltage warning" EMLs received from Netonix ...; (66) notifications total since Fr7/22; [As of Su5/31 no more have been received, so Keith rebooted or disabled them]	TM22 EML				20220726

## L8
Locations: L8	A					KT: Karen Thomas, 10 Acres near W 174th & Dowdy RD

Date/Time CST/CDT					Description	Other Sources	Status
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Cancelled
2019	May	28	Tu					Initial contact with Karen Thomas	H0	Research	20190528
	Jun	7	Fr	~	03:25	~	06:55	Scans 20050522;20190607 Scan, Platt Map P&Z # 03-10 Maurine's Cedar Ridge.jpg; 20190607 Scan, Cadastral Map 10 Acres on W 174th ST.jpg	KTD SSC	On Order	20190607
				10:20		12:20	Onsite w/KT driving: Met Robert & Roger (816-522-4345) Reynolds	KTD		20190607
		21	Fr	~	10:30	~	12:45	Called Karen Thomas, Long Discussion: Explained hopelessness of meeting the Winter and Summer maximum electric needs; Agreed to a $50,000 budget for solar; Very rough preliminary estimate for Minimum Average			20190621
	Aug	3	Sa	~	07:30	~	11:45	20190803 Initial Quote for Construction Loan.doc; KT @ DVS, detailed discussion of Quote, we are in agreement	KTD KTP		20190803
		5	Mo	~	14:15	~	15:25	Called KT: She wants me to do the site plan; Appt. to meet her and Reynolds onsite Sa8/10 08:00; VM and text followed to confirm OK with Bob	SMS		20190805
		10	Sa	~	07:45	~	09:45	Travel & onsite: Stakes for general house location and solar farm (5 total); Discussions with KT and BR, agreement for a battery bunker like a root cellar; CC/AT&T signal is nonexistent onsite; White sheet '8/10/19-8/11/19'	IMG KTF WS		20190810
		11	Su	~	06:00	~	10:05	KT VM & Missed Call; Called KT (06:20-09:54, 2 Hrs 34 Mins)	KTF H0		20190811
				11:38			SMS from KT: 'I think it will be better for all concerned to table this project indefinitely. As you so eloquently remind everyone that I don't know what I want I am going to prove you right so you can win and I can walk off. Best wishes and good luck in your solar endeavors.' / I'm not surprised; All work on the project halted	SMS EML H0		20190811
		12	Mo	~	03:30	~	04:45	Photos transferred from phone; .xlsm updates; TODO moved to KTD; Notes filed; Case closed (I'm done with KT project)	KTD KTF	Cancelled	20190812

## L9
Locations: L9	A					DF: David C. Fuller, Small House S of 12696 Cave Lane, Excelsior Springs (Wood Heights) MO 64024

Date/Time CST/CDT					Description	Other Sources	Status
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active
2019	Aug	21	We					I rec'd his business card during my Wednesday visit to Opportunity Café: / 20190821;22 DF Business Card Scan 1.jpg; 20190821;22 DF Business Card Scan 2.jpg	DFP DFD SSC	Sales	20190821
		22	Th					Discussion with DF (some particulars, home address by SMS); He wants to pay me for a few hours @ $80 (advice, counsel, help with final assembly); Agreed to meet onsite Fr8/23 08:00	H1	On Order	20190822
		23	Fr	~	07:30	~	10:45	Prep. and onsite	H1 IMG	Assembly	20190823
				~	13:00	~	16:30	Travel and onsite	H1	On Hold	20190823
2019	Sep	4	We	~	12:30	~	12:45	Onsite: Gave him sealed invoice/report, discussed 150/200 choice, scheduling, and my fee		Assembly	20190904
		6	Fr	~	07:30	~	11:45	Solar panel combiner box completed except for ground; Reviewed cables/wire needed and specified wire, grounds, clamps and strain reliefs needed			20190906
		12	Th	~	07:30	~	13:30	Onsite: Almost operational			20190912
		13	Fr	~	07:30	~	12:30	Onsite: Ready to be turned on (but w/o battery monitor)			20190913
				~	15:30	~	19:45	Onsite: Hooked it up and drank wine while charging the batteries (system is operational)		Active	20190913
		18	We	~	12:15	~	16:00	Onsite: System has been reaching Float every day since 9/13; Installed battery monitor and remote is working			20190918
		24	Tu		07:47		13:35	Onsite: Examined Classic 200 logs (last Float was on 18th); Battery room vent system installed and operational; Upstairs 24vdc circuit installed, refrigerator operational			20190924

## L10
Locations: L10	A					LWT: Lexington Water Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Battery			Load Supply
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					Charger	DC-DC
				Active	WP5	B56		V10
2019	Jul	8	Mo	~	14:25	~	15:10	Called Keith Jones about scheduling and the possibility of leaving B54 here and installing B1 from RW @ Odessa: WP4 and B1 to be installed in Odessa tomorrow, meet in Lexington at 1pm (OK to swap RW/Odessa batteries so that I can continue testing with B54, which is the better battery); RW W100, B1 and DC Netonix to be installed next week @ Lexington Water Tower (LWT, currently 29w, see 7/10/19 entry, Keith wants me to bring it to Lexington, labor charges will apply, contact Keith when W100 testing with B54 is completed); Hopefully they'll order WP5 and another battery for RW when tower is completed in about a month [Note added 2/7/20: This didn't happen as predicted (the RW W100 went back to RW with B54; WP4 and B1 went to Odessa)]	L1 WP3 B1 B54	Sales					20190708
		10	We					SMSs From Keith Jones: "Latest power usage; Seems to bounce between 25-33"; SMS to Keith "Assuming 29 watts is the average the battery will go 24 hours to 50% discharge (a safe discharge for the battery) … Or 48 hours if you don't mind abusing the battery (100% depth of discharge, totally dead). Be sure to set notification SMS from the Netonix if the battery voltage drops below 13.0 volts as otherwise you may not know the AC power is off until 48 hours after happens."; From Keith "Thanks Jeff; Gotcha thanks again"	SMS EML TW4-5	On Order					20190710
		16	Tu		08:28		08:30	SMS to Keith Jones, still planning on 10am? …; SMS from Keith "No, tower down in Richmond" …; "I'll be back from Florida Monday night"	SMS					20190716
	Aug	7	We	~	08:15	~	14:55	Called Keith, NA; SMSs …; Call from Keith: He's in California setting up wireless for a wine train; He'll be back from CA and FL in 1-2 weeks / B54 and W100_2 won't be installed at Lexington until he is back and there is time to do it [Note added 2/7/20: This didn't happen as predicted (the RW W100 went back to RW with B54)]	SMS WP3					20190807
	Dec	9	Fr	~	11:52	~	11:54	Call to Keith, NA, LMVM …; Call to Mark: Keith is in CA this week; LWT cost?; I quoted $400 + $150-200 for battery; He wanted to know if they could pick up the battery / He told me to send a quote along with quotes on maintenance for other sites [Note added 2/7/20: I didn't send any quotes]	WP5					20191209
2020	Feb	5	We	~	13:42	~	13:44	Call to Keith, LMVM ...; Call to Mark, LMVM					20200205
		6	Th	~	09:05	~	09:10	Call to Keith, NA, sent SMS "Hi Keith, please give me a call. Thanks!" …; Call to Mark: He'll get with Keith and discuss LWT (and mentioned another site where he's interested in putting a W100) / He's interested in maintenance for all locations (I offered to do for $50 per site or 1/2 month's internet); I offered to send him a list of sites and when installed/maintained); He'll call back / My January invoice for internet ($110) was cancelled because (2) referrals signed up (Rayville 3rd ST neighbors)	SMS					20200206
				10:51		11:05	Call from Keith: "Can you fix a TrippLite power strip that sits in a rack?" ("Yes, probably"); Model No. PDUMV15 with (16) plug-ins, 15A max., won't come on, he wants to use it at Lexington TurboNet office; He'll bring it by tomorrow ~09:30-10:00; We also discussed fixing a rack mounted power supply that goes with it and he said he would send photos of that / He doesn't want to do LWT until it's warmer (too cold for him now) ...; (3) MMS photos received [5/7/20 photos printed and in DBT/TW4-5]	SMS DBT TW4-5					20200206
				White sheet notes "Maintenance, TurboNet Sites, Backup PS"	TM21S WS					20200206
				15:34			SMS from Mark: "I tried to call you several hours ago let's go ahead and move forward on checking those batteries and stuff"	SMS					20200206
		7	Fr					Keith was here and I fixed the TrippLite power strip in return for February's internet ($110, about 3 hours and a bunch of solder)					20200207
				11:29			VM from Keith (soon after leaving shop for repair of power strip): "Hey, Jeff, no big deal here, but, is there any way you can make me something that will turn off one device or appliance that has an IP address that I can access the internet from, and then log in to it and restart the device with the power off, I need it for a couple towers, something like that for a tower site, now I can find but they are $80, but I didn't know if you could program something up like that I could use instead of buying from someone else"	TW4-5					20200207
		10	Mo		15:03			Call to Keith, LMVM: "I have (2) Web Relays I'm not using; I paid $130 each; but for you I'd sell them for <$80					20200210
	May	1	Fr					Letter mailed w/payment $220 for Mar and Apr internet: This letter, signed aka "Sparky" is what got Mark and Keith off their butts (WP5 was ordered almost 10 months ago)	DBT TW4-5					20200501
		4	Mo					SMS from Keith Jones "When would you be able to change the Lexington tower over" and "Everything to do Lexington Darden don't worry I mean he's got it right" / SMS to Keith "I can go to KC on Wednesday and pick up your battery. Thursday?"; SMS from Keith "Ok sounds good text me wed and we will watch the weather"; SMS to Keith "K"	SMS					20200504
		5	Tu					Procurement research, Trojan 27TMX and equivalents at Crown (Solar Biz): See white sheet notes; BFMS doesn't answer the phone or messages very quickly (John called back clueless a day later) / Spoke with Tom Duffy, CEO of Solar Biz and Barbara, who explained that Trojan lead time is 7 weeks (and gave me Trojan dealers) / Barbara mentioned Crown, I did some research (Crown does not have good specifications on their website like Trojan) / The bottom line is that the BFMS Trojans can't be beat by Crown, cuz they want $129 to freight 1-4 of them, and about a week / Crowns are cheaper $131.97 for 27TMX equivalent instead of $166.50; About 2 hours	TW4-5 WS					20200505
		6	We					Although planning on going to BFMS, I was not feeling well, and I slept; I knew this broke my word to Keith, but I just couldn't get out and to KC					20200506
		7	Th		09:06			SMS from Keith "Can you be here today about 11:30 looks like it could be a nice day" / SMSs to Keith "Sorry, no stock on the battery until this afternoon. I'll trickle charge it tonight and be ready in the morning. What are you doing tomorrow?" / SMSs from Keith "I guess that batterie and swapping that tower to dc ... I also have 4 more towers I want to swap over" / SMS to Keith "I'm picking up two batteries today, cuz I think you're going to need the other one soon. That's all the stock they have now. ... After this one for tomorrow I will have to manufacture some more power supplies. I need a week advance notice for that."; SMS from Keith "Ok"	SMS					20200507
				BFMS: 78 miles roundtrip and about 2 hours; purchased two 27TMX ($333.00)	TW4-5 B56 B57					20200507
				18:25			SMS from Mark: "I can't be at the office until 10:30 in the morning so come to my office at 10:30 please"	SMS					20200507
				.xlsm recordkeeping caught up (several hours, I've neglected this system since July 2019)					20200507
		8	Fr					(2) 27TMX from BFMS cleaned, labelled and B56 on Trace (45 mins)	B57			B56				20200508
				Call from Mark: They won't be completely ready to install at LWT because they're still working on shelving and power; He wants me to come anyway and I can get a check and survey all the needs					20200508
				10:00		13:45	Travel, onsite, AB and USB deposits; Keith reports that LWT will probably end up at about 30 watts (25w now, adding ~5w) / Overall time includes ~1 hour discussing/addressing other projects (web relays, Eaton power supply, TL maintenance check, other sites maintenance, (3) more W100s ordered, LWT electrical) / Plans are to install W100/B56 at LWT next week (kept in Subaru for now); Rec'd $690 payment	TW4-5 WP5 IMG	Install …	WP5					20200508
		19	Tu		10:48		11:18	Call from Mark & Keith: Fr10am LWT install	TW4-5 WP5					20200519
		22	Fr	~	11:15	~	14:15	Onsite: Finished install of electrical, WP5 and B56 (battery on float but no load until ~ Mo5/25)	TW4-5	Active	WP5	B56				20200522
2021	Mar	9	Tu					IP and credentials for Netonix rec'd from Keith; 10.0.1.84; Cannot access from shop (different Lexington Network)	EML TM21S DBT					20210309
	Apr	16	Fr	~	14:30	~	16:00	Onsite for the Backup Power Supply Maintenance Program; 10.0.1.84, admin, admin; Electrolyte levels down ~1/4", generous fill to +1/8" (top of meniscus to score line) / 55°F, 13.5v Fluke equivalent (13.54v Micronta, 13.4v Netonix); Netonix power supply input voltage calibrated OK (13.4->13.5v); Load ~34 watts; Test email OK / Notification threshold 11.0->13.0; 11.5 minute discharge test, notification sent at ~1'; Notification threshold 13.0->12.8v; Genasun went to Absorption; MAC ec:13:b2:83:66:32	DBT TM21S EML		WP5	B56				20210416
	May	12	We					Email report for 4/16 maintenance sent to Mark and Keith	EML TM21S					20210512
		15	Sa	~	02:37			(2) Email notifications received (duplicates?); The power failure if any was of unknown duration (can't log in from shop and it could be a glitch, as we've seen before)	EML					20210515
	Dec	31	Fr					L1-3 L6-7 L10-16; (LWT was not scheduled to be maintained, not mentioned)	TM21F DBT					20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
	Feb	23	We	~	09:37	~	09:41	Mark called (about ONWT Emergency): He mentioned in passing that they are having issues at Lexington but we didn't discuss it	TM22 L14					20220223
	Mar	6	Su	~	19:30	~	21:45	Lexington Area Power Outage: SMSs from/to Mark; [See "screenshot" of LWT Netonix Mo3/7 which shows that power was off for ~2h15m] / He's getting calls from people in Odessa, he reported that ONWT and LWT internet is down (LWT "not accessible"); ST, WWT and TLNB also probably ran on battery backup / He reports that "Lexington Tower hasn't changed" (since I was last onsite 4/16/21) [but Keith probably added a MikroTik he doesn't know about, see Tu3/22 FTRs T48S/T48-2 where they ordered a Traco for it]; The most likely cause for the internet outages in the area is LWT [MikroTik not on the battery], as ONWT, ST, WWT and TLNB are all properly battery backed	TM22 SMS L14 L13 L6 L16					20220306
		7	Mo					SMSs from/to Mark and call to Mark 6m: Confirmed power was restored at his house ~21:40 last night / Asked for screenshots (LWT, ONWT, ST, WWT), he will ask Keith to obtain LWT Netonix screenshot / MMS "screenshot" of LWT Netonix received from Mark (.heic) [converted Tu3/8, edited with SSC, printed and annotated for file, Image_3-7-22_at_1009_AM_(LWT_Netonix,_from_Mark) SSC.jpg] / Analysis and conclusions, lengthy SMS to Mark: There has been no "backup power supply" failure (Netonix has been running >24 hrs) / 20.0w load is much less than ~34w recorded Fr4/16/21 [this is evidence that Keith has installed a MikroTik and moved one or more antennas to it] / Input Voltage graph shows spikes to 50v (Netonix errors), power outage (~2.2h) and Absorption (~2.5h); WP5 AOK, Float ~13.8v	TM22 SMS IMG SSC		WP5	B56				20220307
		8	Tu	~	08:10	~	08:40	SMSs from/to Mark: "So could we have stuff out there Not plugged in or hooked up to the backup?"; "Anything is possible, and Keith doesn't tell me anything. Why are you asking me? The last time I was at LWT was almost a year ago. And I was looking at the maintenance on the power supply and battery. I remember there was a rats nest of wires there, you'd have to ask Keith."; "Or go over there and look at what's plugged in where."; "He's out of town BRad ordered some new cables also. Yes. Rodents got in there."; "One reason for better enclosures." / "The damn people have dog and cat food out there. That's why rodents came in."	TM22 SMS					20220308
		9	We	~	14:06			L16	TM22 SMS IMG L16					20220309
		10	Th		07:45		12:02	[L10/16] Two SMSs to Mark: My thoughts on why it would be better NOT to use a modified UPS at LWT; [Lexington Area Power Outage Emergency invoice emailed to Mark and Keith Fr6/3]	TM22 SMS					20220310
		22	Tu					Call from Mark & Keith Concerning Spares: Ordered for LWT "MikroTik to battery cable" (Traco) / They installed a MikroTik (many problems with Netonix), probably in February (powered from AC adapter)	T48S T48-2 L14					20220322
		23	We	~	10:00			MikroTik AC Adapter Delivered to Shop by "The Guys"	T48-2					20220323
		29	Tu					Discussion with Keith; LWT Setup Planned; He's running the Netonix for now, but they plan on transitioning to a setup such as at ONWT; Onsite installation scheduled for "next week" / TurboNet File Folder 0.7x3.25 T48-2.lbx	T48-2 LBX					20220329
	Apr	7	Th					Call from Mark; Proposed Th4/14 for installation	T48-2 SMS					20220407
		13	We					SMSs to/from Mark and Keith: Scheduled onsite with Keith for installation Th4/14 11:00					20220413
		14	Th					TP_2 input/output cabling assembled; Prep to go onsite at LWT, set aside what is needed to drill and mount Traco to inside of metal cabinet; Subaru loaded	T48-2					V10		20220414
				~	10:55	~	11:45	Onsite with Keith: Planned location of Traco (right wall under shelf); Planned new location of W100 (left wall under shelf); Asked Keith about power level changes (none, and MikroTik has no loads yet); Considered possible future upgrade to T-105s/Schauer (wait); Asked Keith if he watered the battery (27TMX) at any time since I was there ~1 year ago (NO)			WP5	B56		V10		20220414
				~	11:45	~	15:25	Onsite alone or with Dakota and Cole: SMSs from/to Keith and Mark (need screws delivered ASAP); Dakota and Cole brought the screws and gave me a ride to town for a dump (-30) / Installed W100 on left wall under shelf; Dakota and Cole returned (I showed Dakota the basics on DC systems; Installed Traco on right wall under shelf (with Dakota's help) / Maintenance, W100 and battery: W100 fan checked and filter cleaned; Battery cleaned and tightened nuts, W100 connections, Netonix power inputs, Traco / Electrolyte levels "Factory" but generous fill / Measured Power Levels 14:35-14:45: Battery 12.5⁰C, Genasun ~15⁰C; 14.65vF (Absorption, T-comp is perfect); Netonix load 2.1aE (~31w); Traco input 0.12aE (idle, output not connected, ~1.8w) / Many photos; SMSs and phone calls to/from Keith and Mark	T48-2 SMS IMG					20220414
				During return to the shop: SMSs from/to Keith (and to Mark, about door being locked at TLNB); Call to Keith (I was at WalMart), he promised to shoot Netonix screenshots and send them to me	T48-2 SMS					20220414
		15	Fr	~	08:35	~	08:36	(5) Netonix screenshots from Keith rec'd 08:40; Images\DC\20220415DC MO, Lexington, From Keith Jones, TurboNet; LWT Netonix Screenshots / [2 printed, analyzed and annotated Fr5/13]: ~70w reported by Netonix is much higher than 31w measured onsite Th4/14 / Float 13.67vN, Genasun T-comp is perfect for 15⁰C, Netonix calibration is OK; [Report and Invoice completed and emailed to Mark & Keith We6/8]	T48-2 EML IMG		WP5	B56				20220415
	Jun	3	Fr					20220310 Report & Invoice - Lexington Emergency.doc; 20220310 Report & Invoice - Lexington Emergency.pdf; 20220603 Email to Mark & Keith 'Report & Invoice - Lexington Emergency'.pdf	TM22 DBT EML SMS					20220603
				~	11:27	~	12:01	33m phone call to Keith: LWT is "the same as it was" (he hasn't had time to go onsite and deal with it); This may mean we still don't have battery backup of the MikroTik (but not sure)	TM22					20220603
		8	We					20220415 Report & Invoice - Lexington Water Tower 48v Installation.doc and .pdf; 20220608 Email to Mark & Keith 'Report & Invoice - Lexington Water Tower'.pdf	T48-2 DBT EML					20220608
	Jul	5	Tu					Lexington Power Failure: As reported by Keith for TLNB; Most likely also impacted LWT (but not known)	TM22 SMS L16			B56				20220705
		19	Tu					Call from Keith: Ordered new site CFS; Keith has not yet returned to load the Traco (and mentioned that if need be we can rob LWT Traco for CFS)	T48-4 L18					20220719
		22	Fr					Lexington Power Failure: As reported by Keith for TLNB; Most likely also impacted LWT (but not known)	T48-4 TM22 L16 L18			B56				20220722
	Aug	10	We					[L10/14/17/18] Finished fabrication of (4) Power Cable Disable Switch Assemblies (LSWT, ONWT, LWT and CFS); Labels printed TurboNet Disable Switch 48V Power Cable ON OFF 0.7.lbx; Photos / [Sa9/10: We now know these Power Cable Switch Assemblies are for WP11/12/13/14 WISPers for LSWT, CFS, Spare and ONWT or LWT]	T48-3 IMG LBX L17					20220810
	Sep	1	Th					[L10/14/17/18] W150 BACKPLATES design s/b as small as possible: / Various sites considered (ONWT, LWT, CFS, LSWT); ~10x14" (<=3.5" high) will fit inside Engel (big advantage, can test at -15 and +50degC)	T48-3 WP11					20220901
		8	Th					L1/3/10/14-18	TM22 L17					20220908
	Oct	9	Su					[L10/14] TFTP/TODO Decision made to order (5) Tracos: Plan to build (7) W150s (WP12-18); 1st Production Run (2), 2nd Production Run (5) using Tracos now at LWT and ONWT / [Mo12/12: Plans were changed after receiving a 2nd Murata meter, the 2nd Production Run will be Quantity 2 (WP14-WP15) and will not use the Tracos at LWT and ONWT]	DWP WP12-18					20221009
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML					20230303

## L11
Locations: L11	A					RWWT: Richmond West Water Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	WP6	B57
2020	May	23	Sa		14:41	~	15:00	Call from Mark: “How soon for another W100? We have an outage at Richmond West (between Richmond and Orrick)”; I said “End of next week (Fr5/29)”; Mark said “… hopefully install w/o Mo 6/1”	WP6	On Order			20200523
	Jun	4	Th	~	09:00	~	10:05	Call from Mark: Discussed scheduling on W100 man’f (Monday soonest); Scheduled Tu6/9 10am installation of WP6 and battery at Richmond West Water Tower (RWWT) / [Note added Fr6/12: that appointment was missed due to major internet outage caused by fiber damage]	WP6				20200604
				~	19:15	~	19:45	Created Summary entry and History sheet for L11					20200604
		12	Fr	~	12:45	~	15:40	[L11-13] Talked with Mark to confirm delivery date/times, etc.; They had tried to contact me that we cannot do any installs this week due to problems they had / Installation scheduled for w/o Mo6/15 (at which time I should get paid); Invoice sent for (3) units for RWWT, RHST and ‘Skeeter’ $1450	WP6				20200612
		15	Mo	~	15:45	~	16:10	[L11-13] Called Keith (Viber Out): Scheduled delivery of WP6-WP8 (B57-B59) starting tomorrow morning Tu6/15 10:30 at RWWT	WP6				20200615
		16	Tu	~	10:30	~	11:00	Onsite with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix); Rec’d $1450 TurboNet check	TW6-10	Active	WP6	B57	20200616
2021	Feb	15	Mo	~	08:38	~	08:48	Missed call and SMS from Mark Webb; "Tower is down"; DC Netonix is dead; W100 has two green lights so battery is probably AOK	SMS				20210215
				~	10:31	~	10:41	MMS from Keith with videos of W100; He was concerned about the blinking status light on the Genasun; I told him that's normal, the battery is fully charged; He said it keeps blowing fuses / I called him and explained that it means that his load is shorted (Netonix); He wanted to use 25 amp fuses, but I told him it is best to use 20 amp as that keeps the fuse in the Genasun from blowing as well, which cannot be fixed without returning it to the shop; Nothing was said about maintenance on the battery					20210215
	Mar	9	Tu	~	11:30			IP and credentials for Netonix rec'd from Keith; 192.168.1.17, admin, admin; NTP and SMTP configured but not working; Warning voltage 11->13; Float 13.9 as per Netonix (not calibrated)	EML TM21S DBT				20210309
	Apr	16	Fr	~	12:00	~	14:00	Onsite for the Backup Power Supply Maintenance Program; Electrolyte levels down 3/4 to 7/8" (top 1/16" to 1/4" of all plates exposed); 87°F, Float was 14.08v Micronta (14.0v Fluke equivalent) / 12-port Netonix refused to calibrate, Power Supply Input voltage reads ~0.8% low; Load ~55 watts; 40 minute discharge test, notification email sent at ~1-2 mins; Warning notification threshold changed 13.0->12.8v (but Netonix will not send emails as per 3/9/21); New float value after discharge 13.7v (Fluke equivalent from Netonix 13.57v); MAC ec:13:b2:84:04:14; Call to Keith, I reported that although outside temperature is ~45°F it was 90°F inside the shed when I arrived, it is being heated by the equipment (most of the power is the Antminer); He directed me to unplug the AntMiner; A/C will not come on (flaky bad duplex outlet)	DBT TM21S		WP6	B57	20210416
		17	Sa					Email report on maintenance visit yesterday sent to Mark and Keith	EML				20210417
	May	11	Tu	~	12:00	~	12:35	Onsite to follow up on flaky duplex outlet; Called Patrick McDaniel who checked with Stan Barr, OK to bring power down long enough to replace outlet; But I discovered that the top outlet is AOK and decided not to replace the duplex outlet; Set A/C 68°F, Energy Saver; Tested power outage and if there is a failure longer than about 10 seconds it will not come back on by itself (must be manually turned back on)	TM21S SMS				20210511
		12	We					Email to Mark and Keith concerning yesterday's visit	EML				20210512
	Dec	27	Mo	~	07:55			Logged into Netonix: Load ~38w; Float ~13.5v (13.38v Netonix adjusted up 0.8% as per onsite error observed 4/16/21) (seems a little low, but the shack does stay warm, especially if AC isn't set to run)	TM21F SSC		WP6	B57	20211227
		31	Fr					L1-3 L6-7 L10-16; RWWT Not Maintained as Hoped (last visit 4/16/21)	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
	Jun	28	Tu	~	14:20	~	14:55	Onsite at TLNB: Keith mentioned that another upcoming 48v site will be RWWT	TM22 L16				20220628
	Sep	11	Su					Considered TurboNet politics for all new orders/requests (T48-3 R&D): RWWT is a special case, install a W150 and install an A/C that always runs at 68degF (20degC)	T48-3 WP11				20220911
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML				20230303

## L12
Locations: L12	A					RHST: Richmond High School Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				No Backup	-	-
2016	Mar	18					L5/12	L5	Inquiries			20160318
2017	Nov	16	Th					Onsite with Mark Webb and Keith Jones; I noticed and mentioned at the time that although the High School will have UPSs for the servers inside, the tower has no backup	L5	Sales			20171116
	Dec	20	We	~	15:00			UPSs (and installed batteries) installed inside on servers at Richmond High School	L5				20171220
2020	Jun	4	Th		09:33		11:22	Another major internet outage caused by loss of power at RHS (1 Hr 49 Mins); SMSs to/from Mark which ended with order to install W100 next week	L1	On Order			20200604
				~	19:45	~	20:25	Created Summary entry and History sheet for L12	WP7				20200604
		12	Fr	~	12:45	~	15:40	L11-13	WP7				20200612
		15	Mo	~	15:45	~	16:10					20200615
		16	Tu	~	11:10	~	11:30	Onsite at RHST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Active	WP7	B58	20200616
2021	Mar	9	Tu					IP and credentials for Netonix not available as Keith says "not finished yet" (no Netonix?)	EML TM21S DBT				20210309
		16	Tu	~	13:00	~	13:45	Onsite for the Backup Power Supply Maintenance Program; No load (no Netonix); There was a short power failure while I was onsite (~1 min) / Electrolyte down -1/2" (<1/4" above plates), filled to +1/8"; 51°F; Float 13.895v (Micronta->Fluke); Email report to Mark and Keith	DBT TM21S SMS EML		WP7	B58	20210316
	Sep	22	We	~	14:45	~	15:15	Onsite for Fall 2021 Maintenance; "Rat's Nest" of wires (photos); 80°F 13.43v M (13.35v F) / Battery removed & W100 AC disconnected (there has been no Netonix load since 6/16/20, will take battery to shop for maintenance); W100 cleaned; Ant trap	TM21F IMG	Available		-	20210922
	Dec	16	Th	~	16:25	~	16:45	Onsite: Met Mark in parking lot and 27TMX to Subaru ...; W100 removed from RHST; B58 and WP7 to be installed at RCWT	TM21F L3	No Backup	-		20211216
		28	Tu					20211228 Credit - Richmond City.pdf; Recommendations for Further Discussion (RHST needs Wiegmann, Schauer and T-105s)	TM21F DBT L3				20211228
		31	Fr					L1-3 L6-7 L10-16; Visited	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML				20230303

## L13
Locations: L13	A					ST: Skeeter Tower

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	WP8	B59
2020	Jun	12	Fr	~	12:45	~	15:40	L11-13	WP8	On Order			20200612
		15	Mo	~	06:00			Created and updated History sheet L13 for ‘Skeeter’	WP8				20200615
		15	Mo	~	15:45	~	16:10	L11-13	WP8				20200615
		16	Tu	~	11:50	~	12:35	Onsite with Keith Jones: “Skeeter” is East of Lexington about 4 miles from 13 and 224 interchange, ~1500 feet South of 24 on Plainview Lane; Installed W100 and battery / No load (Keith will return later to install and configure DC Netonix); This is also about the time that I heard that they had obtained the bank line of credit and were buying a new office building	TW6-10 L16	Active	WP8	B59	20200616
2021	Mar	9	Tu					IP and credentials for Netonix rec'd from Keith; 10.0.1.192; Cannot access from shop (different Lexington Network)	EML TM21S DBT				20210309
	Jun	21	Mo	~	14:35	~	15:30	Onsite for the Backup Power Supply Maintenance Program; NTP enabled; SMTP setup and tested, warning voltage 13.0 / Cell 1/6 plates exposed, all down ~3/4"; 83°F Float 13.63 (Fluke equivalent), 13.6v Netonix (calibration OK, not changed); Load 25 watts; 5 min discharge, new Float 13.3v; MAC ec:13:b2:84:04:30	DBT TM21S			B59	20210621
		23	We					Since the site visit on 6/21 there have been daily notifications (1-4 per day); Can't log in, of course, no idea why; Email report to Mark and Keith for 6/21 visit	EML TM21S				20210623
	Aug	16	Mo					L6/13/14					20210816
		18	We					Approximate date that Keith disabled the SMTP notifications at ST (last date of spurious email)	EML				20210818
	Dec	31	Fr					L1-3 L6-7 L10-16; ST Not Maintained as Hoped (last visit 6/21/21)	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16					20220104
	Mar	6	Su	~	19:30	~	21:45	Lexington Area Power Outage: [power was off at LWT for ~2h15m]; ST power also may have been interrupted	TM22 L10				20220306
	Jun	3	Fr	~	11:27	~	12:01	33m phone call to Keith: "We lost Skeeter tower radios and switch", replaced with same equipment; This probably happened sometime in the past few weeks, not sure; I don't remember if he said he watered the battery	TM22			B59	20220603

## L14
Locations: L14	A					ONWT: Odessa North Water Tower, 7909 Barkertown Rd, Odessa, MO 64076

Date/Time CST/CDT					Description	Other Sources	Status	Charger	Battery	DC-DC	Load Supply	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	BC6	B60 B68/69	V9		WP9
2020	Jun	8	Mo	~	10:50	~	12:15	[L14-15] Drive to Richmond to meet Mark: W100 order extended to all five WP6-WP10 (and in their minds they were envisioning putting them at Odessa N and the “New Tower” [OT])	WP6-10	On Order					20200608
		16	Tu	~	11:50	~	12:35	[L14-15] Onsite at Skeeter [ST] with Keith Jones: Also discussed ONWT and “New Tower” [OT] installations					20200616
		23	Tu	~	19:20	~	19:25	[L14-15] SMSs to Mark and Keith “When can we install the last two W100s and batteries that you ordered, they are ready. This week?”	SMS					20200623
	Jul	1	We		13:42		13:52	[L14-15] Phone call from Mark: Scheduled Mo7/6 09:30 Lexington to go onsite and install WP9/B60; Also discussed “new tower” [OT] which needs electrical work and is slated for WP10/B61	WP9-10					20200701
		6	Mo	~	10:55	~	13:10	Onsite with KJ and MW to install WP9/B60; Many photos and videos TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb / Some electrical work making the AC outlet in the box work (which is not very waterproof); When I left the W100 had not yet been plugged in, but the battery was powering the DC Netonix	TW6-10 IMG	Active		B60			WP9	20200706
2021	Mar	9	Tu	~	12:00			IP and credentials for Netonix rec'd from Keith; 10.10.11.188, admin, admin; NTP and SMTP configured and tested; Warning voltage 11->13; Float is 13.3v as per Netonix (not calibrated yet)	EML TM21S DBT					20210309
	Apr	23					Notification 12.4v	EML					20210423
	May	11	Tu	~	09:50	~	11:10	Onsite for the Backup Power Supply Maintenance Program; The equipment box is a very full rat's nest, could barely get to the battery (tightened OK), but could not tighten the Netonix load connections w/o risking bringing something down; Electrolyte levels down 1/4 to 3/8", generous fill to +1/8" (top of meniscus to score line); 57°F, 13.4v Fluke equivalent (13.48v Micronta, 13.29v Netonix); Netonix power supply input voltage could not be calibrated (wanted 13.29->13.4v), reads 0.7% low; Load ~20 watts; Test email OK; 10 minute discharge test, notification sent at ~1'45"; Notification threshold 13.0->12.9v; Genasun went to 2-1/2 hr Absorption 14.6v then Float 13.8v (2 SSC); MAC ec:13:b2:84:05:64	DBT TM21S EML SSC			B60			WP9	20210511
		12	We					Email report to Mark and Keith for yesterday's visit	EML TM21S					20210512
	Jun	9					Notification 12.9v	EML					20210609
		11					(3) Notifications 12.9v; IP has been changed to 10.0.2.204; I can't log in					20210611
		23					Since 6/11/21 there have been (13) notifications; Netonix glitches?					20210623
	Aug	16	Mo					L6/13/14	EML TM21F					20210816
		21	Sa					Approximate date that Keith disabled the SMTP notifications at ONWT (last date of spurious email)	EML					20210821
	Sep	22	We					Meeting in Lexington with Keith and Mark (to discuss MikroTik 48v systems and quote): Quotes requested on power cable and NEMA box / MikroTik pilot project equipment is slated for ONWT	T48P TPC1 TEDS TOI					20210922
		30	Th	~	10:30	~	10:45	Call from Keith (while driving back from Sutton NE); Photo and video from Keith at ONWT	IMG TPC1 TOI					20210930
	Oct	8	Fr	~	10:35			Mark called from ONWT, with Keith on speakerphone: GET THE BOX; GET THE CABLE; They can install both while I'm working at the shop getting ready / They see the beauty of my proposal: One fiber cable and One power cable, and at the top they can do anything they want up to ~100-150 watts / 10:56- MMSs from/to Mark: (2) Photos at ONWT; New box will go right in front of the big white pipe; "Thanks for the photos. I'll find the box and the cable next, this weekend." / "Try and find them today please and I'll order it. W"; "Thanks; Sorry, many hours of research will be needed, probably cannot do today. And businesses start shutting down in a few hours. These are technical design decisions that will affect many tower sites and should not be rushed into. We need to keep our options open, and make a good first choice."	SMS IMG TEDS TPC1 Z18					20211008
		20					Invoice "48 Volt Power Cable - Design Specifications" ($200 before Nov discount of $55); Specified Belden 88760	TPC1 DBT					20211020
		27					Began $40/hr shop work to prepare for ONWT installation; Wiegmann and Mier boxes discussions with Mark; The wrong power cable was received (~$200)	TOI TEDS TPC1					20211027
		28					I convinced Mark to order the Belden 88760 ($1000)	TOI					20211028
	Nov	11					Keith at shop to discuss Power Cable Assembly; See white sheets pages (1) and (2); Keith says there will be (3) MikroTik PowerBox Pros (PBPs) at the top feeding (8) 48v Mimosa and (3) 24v Ubiquiti antennas (rough estimate 110w); The PBPs are very close together so we agreed to a pigtail splice of power cable to (3) PBP adapter cables	TOI T48S Z19 Z20 WS					20211111
		15	Mo	~	13:39			The Power Cable Assembly is ready to go; On the end of ~492' of Belden 88760; I saved some pieces of the Belden cable for shop work / 20211115 Quote - Spare Parts for ONWT and Future.docx and .pdf	T48S TOI IMG DBT EML Z19 Z20					20211115
		16	Tu	~	10:50	~	11:05	Mark and Keith @ shop: $1720 check (for spares Quote); Power cable is a little short, but they'll make it work and they're happy; They'll probably go to ONWT We11/17 / Next week (Thanksgiving week) they'll be working Mo11/22-We11/24; I told them I'd be ready to go to ONWT in a few days, but probably Mo-We next week	T48S SMS TOI					20211116
		19	Fr					Proposal, 20211119 Email to Keith, Mark & Brad 'Odessa North Remote Monitoring'.pdf; I volunteered to add Wattmon remote monitoring to the new enclosure/system / [DORM project abandoned Su10/23/22]	DBT TOI DORM EML					20211119
		23	Tu	~	12:20	~	15:40	Onsite with Mark, Keith, Dakota and ?; Installed Mier enclosure with Schauer, T-105s, Traco and Dinico fan control system; WP9 and B60 are still Active / Keith saw 52.4v on 2 of 3 PBPs at the top; I forgot to run the outside T sensor for the Dinico to the outside of the enclosure (TODO)	TOI SMS Z18		BC6	B60 B68/69	V9		WP9	20211123
		24	We					20211124 Invoice - MikroTik 48v Systems Equipment and Testing.pdf	T48P DBT					20211124
		28	Su					20211128 Email to Mark, Keith & Brad 'Invoice - MikroTik 48v Systems Pilot Project'.pdf	T48P DBT EML					20211128
		29	Mo	~	13:32			MMS/SMSs from Keith: Screenshot of (3) Mimosas running on one PBP; "Power board hooked up and 3 mimosas running"; Mimosas are seeing 50.0v (2.8v drop), a total of ~41w / See FTR for thoughts on what will happen when we increase the power cable load (currently ~70w, could be ~120w which is a 4.8v drop to 48.0v); Estimate of load on Schauer is now ~95w / If Keith adds a lot more wattage we may be pushing the Schauer's 145w absolute maximum (would require adjustment of VR5 Trip Point to go higher)	SMS IMG TOI					20211129
				20211129 Fan Cooling System, Enclosures Design Specifications, Schematic Scan.jpg	TEDS DBT					20211129
		30	Th					20211130.1 Invoice - Enclosures Design Specifications & Procurement.pdf; 20211130.2 Email to Mark, Keith & Brad 'Invoice - Enclosures Design Specifications & Procurement'.pdf	TEDS DBT EML					20211130
	Dec	10					20211210 Invoice - Spare Parts for ONWT and Future.pdf	T48S DBT					20211210
		31	Fr					20211231.1 Invoice - Odessa North Installation (ONWT).pdf; Power Level Estimates on Page 2, Total load on the battery system estimated as ~113 W	TOI DBT					20211231
				L1-3 L6-7 L10-16; ONWT Older W100 System Not Maintained as Hoped (last visit 5/11/21)	TM21F DBT					20211231
2022	Jan	1	Sa					20220101 Email to Mark, Keith and Brad 'Invoice - Odessa North Installation' (ONWT).pdf; Keith Please pay particular attention to the Power Level Estimates on page 2	TOI DBT EML					20220101
		2	Su					20220102 Email to Mark, Keith & Brad 'Invoice - Spare Parts for ON & Future (MikroTik 48v Systems)'.pdf	T48S DBT EML Z19 Z20					20220102
		4	Tu					L1-3 L6-7 L10-16	TM21F DBT EML					20220104
		5	We					20220105 Email from Mark 'TurboNet Statement'.pdf	DNT DBT EML					20220105
	Feb	19	Sa	~	16:53	~	18:55	VM from Keith "ON down" [went down 10:30-11:00], SMSs from Mark "ON mimosa stuff down", Call to Keith (39m): He cannot see the PBPs at the top of the tower / Keith was onsite (extremely cold, windy and icy); He said "power" was off when he got there (Schauer, Dinico) / He cycled the power to the Schauer, heard fan and saw indicator light [he later reported that the fan only ran on high for <1m, so batteries must have been fully charged] / He may have cycled the fan system (Dinico) AC power [he said later it was working, displaying ~3⁰C] / Keith wants me onsite with spare parts and tools: We checked the weather and agreed to meet in Lexington Mo2/21 9am	TM22 SMS Z18		BC6	B60 B68/69	V9		WP9	20220219
		20	Su					Failed attempt at spare Schauer preparation, and no time to test and prepare a Traco / Call from Mark, I said "We don't know what failed yet, many possibilities" and that Keith and I planned Mo2/21 onsite	TM22 TM48S BC7 Z0 Z19 Z17 B70/71					20220220
		21	Mo	~	07:40	~	08:30	Preparations to go onsite, loaded Subaru: Many tools; Many tracked items and spares; What needs to be done onsite is unknown / "I brought the entire shop" so that I could replace or repair anything as needed	TM22 BC8 V10/V11 B70/71 S13					20220221
				~	08:20	~	09:28	SMSs from/to Keith during prep and enroute to ONWT; Jeff 09:20 Passing Lexington; Keith 09:28 Gotcha we are here	TM22					20220221
				~	09:45	~	11:10	Onsite with Keith and Dakota: Careful repeated questions/answers on Keith's initial observations when onsite Sa2/19; He swears "there were no lights anywhere" when he arrived / I think he may have missed seeing the Schauer lights, they aren't very bright; He insisted that the Dinico temperature display was OFF (see further comments in FTR) / He replugged the power on the Schauer and heard the fan go high, and saw the light(s), but he reports "high fan" only lasted <1m, THEREFORE battery was fully charged / He replugged the cooling system and Dinico reported about 3⁰C / My initial observations (Keith and Dakota watching): Traco output 52.9vM, ~1.42aE (~75w) with MikroTik, ~1.07aE (~56w to top of tower) with MikroTik unplugged / Battery 14.52vM (~14.4vF); Charging ~0.015aE (fully charged); Battery Voltage Float is too high for the temperature observed, see FTR for analysis and "something is wrong" (TODO) / THE FIX (Keith and Dakota watching): Disconnected power to top of tower for ~15s then reapplied / Keith was monitoring with his laptop, all (3) Mimosas came online, reporting 50.0-49.9-50.0v (PBP interface) / I briefly showed Dakota and Keith how to use their meter (reads slightly low, 52.5v=52.9vM (~52.8vF); Dakota departed at 10:30 / Discussions with Keith: His future plans for the new system is to add (3) Mimosas of lower power; Vague talk of other additions; Power requirements may double / The 27TMX in the old system was "topped off" (unknown when) / His future plans for the old system is to clean up the rat's nest and keep it operational for the Netonix and B11 backbone connection to Lexington (as soon as the weather improves) / We can connect directly from the old box to the new box so that we can access web relay(s) and etc. even if the new box Mimosas go down / Keith and I made some initial Power Level Estimates (mostly erroneous, but it was good for Keith to see this process)	TM22 Z18		BC6	B60 B68/69	V9		WP9	20220221
				~	11:10	~	14:00	Onsite Alone (after Keith departed): / Power Level Measurements and Estimates: Battery continuous load (includes Traco losses) 85.0w (with MikroTik), 64.8w (to top of tower); Traco load 75.0w (with Mikrotik), 56.5w (to top of tower); Power cable loss ~3w; (3) PBPs idle power ~12.5w (~4w each); MikroTik in enclosure ~18.5w; (3) Mimosas ~41w / Calculations on what would happen if Keith doubles the antenna load at the top of the tower: Total continuous load on battery would be ~136w / (OK for now, <145w max for BC6 Schauer configuration) / CONCLUSIONS and TODO: Suspect Flaky AC?; Web relay to drop 52.8v remotely; Old system will NOT be retired any time soon / It is likely Keith could eventually increase the load above 145w / Maintenance: Fan control system T-sensor placed under the box; Reprogrammed Dinico for 10⁰C "floor": Tested and adjusted Meir enclosure door switch (it was too "loose") / Electrolyte filled, tightened battery nuts and applied terminal spray (B68/29); Measured for power cable ground that needs to be added; Caulked 1" holes (2x); Many photos	TM22 BC6 Z18 B68/69 IMG					20220221
				~	14:25	~	14:45	Lexington office: Returned Mier enclosure key to Keith; Brief discussion, Keith said "We don't know what happened"	TM22 L16					20220221
		22	Tu	~	12:55	~	13:40	Call to Keith 45m, discussing his onsite visit Sa2/19: He "bounced" the fiber port but didn't restart the Netonix, which might have fixed the problem remotely / Keith agrees the most likely reason for the failure was a fault in communication between the PBPs and the Netonix; We questioned whether or not the AC power is flaky, but this would cause no fluctuations on the power to the top of the tower (TODO trace out the AC power circuit from the building); There was lightning and storms in the area the night of Th2/17, this could have damaged the PBPs or upset the Netonix; I believe that Keith's observation of the Schauer state was in error (low fan is hard to detect, indicator lights are not very bright) / Agreed again we need a web relay (and switch) on the Traco output	TM22 BC6				V9			20220222
				~	18:53	~	18:59	Mark called 6m: ONWT is down again; I told him I had found no fault with the power system and I don't suspect it as causing the problem / Mentioned that problem might be fixed by remotely booting the Netonix					20220222
		23	We	~	09:37	~	09:41	Mark called 4m: Last night Mark was on onsite, the Schauer had red and green lights, he disconnected/reconnected the Traco output (wire nuts) and this did not bring the Mimosas back up / The most likely culprit is the DC Netonix in the "Rat's nest" of the old system box; They are planning on going out there to set up a heated tent and replace the Netonix (very nasty weather)	TM22 SMS BC6 L10					20220223
				~	12:46	~	12:48	Angry call from Keith: "Guys are at Odessa now, all the wire nuts are off, Schauer is off, and I'm still seeing power to the PBPs"; I mentioned that the Schauer has nothing to do with it, on or of / I asked if they have any ethernet or other cables running to the PBPs, "NO, just the fiber from the Netonix to the PBP" / I asked what the PBPs are seeing for voltage and he got angry, cussed at me and hung up; MY THOUGHTS and QUESTIONS	TM22 BC6					20220223
		25	Fr	~	10:04	~	10:18	Called Mark, So what do you know about Odessa North?: "All I know is that all 3 of the PBPs fucking zapped out" / "They tried to undo the power to them, which is weird because they wouldn't go off" (I still question how they knew that, if they were having communication problems with the PBPs or they were "fried" there's no way to know except to climb the tower with a voltmeter) / One Mimosa is now working, (2) need to be replaced; Keith and the guys are going over there soon today / They ran a cable up to the Mimosas to see if they would function and got one of them running / Take all information from Mark "with a grain of salt" / 20220225 Report & Invoice - Odessa North Emergency and Maintenance (ONWT).doc [emailed to Mark and Keith We5/18]	TM22 DBT					20220225
	Mar	6	Su	~	19:30	~	21:45	Lexington Area Power Outage: SMSs from/to Mark; [power was off at LWT for ~2h15m] / He's getting calls from people in Odessa, he reported that ONWT and LWT internet is down (LWT "not accessible") / The most likely cause for the internet outages in the area is LWT [MikroTik not on the battery], as ONWT, ST, WWT and TLNB are all properly battery backed / Mark mentioned that power levels at ONWT haven't changed	TM22 SMS L10					20220306
		22	Tu					Call from Mark & Keith Concerning Spares: For ONWT they want the Schauer and Traco spares in their hands ASAP so that if it goes down they can be replaced without delay / They installed a MikroTik at LWT (many problems with Netonix), probably in February (powered from AC adapter, explains internet outages at ONWT when power dies at LWT)	T48S T48-2 L10					20220322
	May	18	We					20220225 Report & Invoice - Odessa North Emergency and Maintenance (ONWT) 300.pdf; 20220518 Email to Mark & Keith 'Report & Invoice - Odessa North'.pdf	TM22 DBT EML SMS					20220518
	Jun	3	Fr	~	11:27	~	12:01	33m phone call to Keith: ONWT new system "has more on it", two more Mimosa C5Cs (not as much power as 3 Mimosas that were first installed) / Netonix is still being used in old system box, but he has been onsite dealing with it [he may have watered the battery], B11 runs off the Netonix (main backbone connection to Lexington) / All the Ubiquiti except two have been disconnected, but within a week he plans that they'll all be gone; He's still hoping to eliminate the old system box, but it will take time / He's planning on being onsite next week to add/swap/install/cable radios, maybe Tu or We / He promised to contact me when he knows when, because it would be best for me to go onsite and measure the power levels and perhaps replace BC6 with BC7, which is tuned for a higher power level (but currently in BTS testing with Engel, and not labeled yet)	TM22			B60 B68/69				20220603
	Aug	10	We					L10/14/17/18	T48-3 IMG LBX L17					20220810
		17	We					Label edited and printed (10⁰C floor) Dinico DIN-S-CF Settings.lbx (to be applied next time I have to go to ONWT)	T48-3 IMG LBX L17					20220817
	Sep	1	Th					L10/14/17/18	T48-3 WP11					20220901
		8	Th					L1/3/10/14-18	TM22 L17					20220908
		19	Mo					TODO for ONWT: W150 BTS and Z18 T2 in lug s/b on T-105 negative post under Plastic [Foam] Cap	T48-3 PLN WP11 Z18					20220919
		21	We					TODO for ONWT improved: Install 4 Foam Caps; Sensors on +6v T-105 Negative	T48-3 PLN WP11					20220921
	Oct	9	Su					L10/14	DWP WP12-18					20221009
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML					20230303

## L15
Locations: L15	A					OT: Oak Tower, 43364 Walnut Lane, Richmond, MO 64085

Date/Time CST/CDT					Description	Other Sources	Status	WISPer	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	WP10	B61
2020	Jun	4	Th	~	09:00	~	10:05	Call to Mark, LMVM; Call from Mark: ... They need electrical work from me for a “new tower” [OT] in about 2-3 weeks (he has a picture, KCPL will trench, we need a meter base, etc.)	WP6	On Order			20200604
		8	Mo	~	10:50	~	12:15	L14-15	WP6-10				20200608
		16	Tu	~	11:50	~	12:35					20200616
		23	Tu	~	19:20	~	19:25		SMS				20200623
	Jul	1	We		13:42		13:52		WP9-10				20200701
		6	Mo	~	10:55	~	13:10	Onsite at TL to go to install WP9/B60 at ONWT; Rec'd KCPL printouts of SERVICE CHECKLIST and details on requirements for electrical drop at New Tower [I never bothered to study this information which is about 50 pages]	TW6-10				20200706
		13	Mo		14:54			[L15-16] Missed call from Mark: Most likely concerning New Tower [OT] or New Building [TLNB] Electrical; I did not return this call until Mo7/27	L16				20200713
		27	Mo	~	11:29	~	12:15	Calls to/from Mark and Keith: "Hopefully they're going to get the power run to the new tower in the next week"; "Waiting KCPL"	WP10				20200727
		31	Fr	~	15:10	~	15:30	Onsite: Notes and photos of needs; See white sheet for TW6-10 for details; TurboNet Electrical Planning Onsite Visits; New Tower, Evans Heating & Cooling; New Building, Keith Jones; Subaru	TW6-10 SMS IMG WP10 WS				20200731
	Aug	3	Mo	~	17:13	~	17:29	Call from Mark: Amongst other projects discussed New Tower [OT] (wants to get it done this week)	WP10				20200803
		4	Tu	~	06:20	~	08:30	TODO and .ods related to New Building [TLNB] and New Tower [OT] / Phone calls/SMSs to Keith and Mark (amongst other projects discussed New Tower [OT]); TODO Priorities rearranged; See TW6-10 printouts of research and phone calls	TW6-10 SMS WP10				20200804
				~	09:00	~	10:00					20200804
		10	Mo	~	10:28	~	10:31	Call from Mark: Discussed Swafford, but New Tower [OT] also discussed, Mark will check to see if meter is in place and wants to do it We8/12	WP10				20200810
		12	We	~	13:05	~	13:30	TODO and .ods related to New Tower [OT]; Called Stanion Electric to confirm stock and hold on box (YES) / SMS to Keith "Keith, again, something has come up and I didn't get to KC today to get the box. I can go there tomorrow morning. How are you with doing new tower on Friday morning?"	WP10 SMS				20200812
				~	14:35	~	14:40	SMS from/to Keith regarding New Tower [OT]: "Friday is fine"; "Tx"					20200812
		14	Fr	~	10:15	~	17:10	Onsite 2x; Keith not there; Had to return to shop for tools esp. Makita drill (Milwaukee batteries dead); Mark stopped by only for a few minutes; Installed box and electrical service; Installed WP10 and B61; Photos	IMG	Active	WP10	B61	20200814
		21	Fr	~	09:50	~	12:00	Onsite: Tried to install relief clamp for 1/2" knockout but Ethernet cables won't fit; Plugged top of 1" conduit; Installed ant trap; Photo			WP10		20200821
		25	Tu	~	09:45	~	11:25	Onsite: Rec'd check for $610.62 from Mark for "Oak tower Electrical and Box work" (Short Name and Description changed); Discussions with Mark and Keith concerning future projects (see WP10); Photos	SMS IMG		WP10		20200825
2021	Mar	9	Tu					IP and credentials for Netonix rec'd from Keith; 10.10.11.201, admin, admin; NTP and SMTP configured and tested; Warning voltage 11->13; Float is 14.1v as per Netonix (not calibrated yet)	EML TM21S DBT				20210309
		16	Tu	~	14:10	~	15:50	Onsite for the Backup Power Supply Maintenance Program; The box lock combo is 109; Equipment very dusty (the tower is next to a dirt road, photo); Electrolyte down -3/8" (+3/8" above plates), filled to +1/8" / 51°F; Float 14.255v (Micronta->Fluke); Netonix Power Supply Input Voltage reads low and could not be calibrated (8 port variety), in Float 14.26v Fluke, 14.0v Netonix (SSC1), Netonix is -1.8% (Fluke is Netonix+1.8%) / 10 min discharge OK (SSC2); On recovery the Genasun went to a new Float 13.9v Fluke 13.67v Netonix (due to warmer temperatures since the last power failure, SSC3)	DBT TM21S SMS IMG SSC		WP10	B61	20210316
		19	Fr					Load 18.3 watts (corrected +1.8% from graph); Set Email Notification Threshold 13.0->12.8v for 5-6 mins delay after power failure (mostly due to Netonix calibration being 1.8% low) / Run-time estimate >76 Hrs, but reported ">48 Hrs"; Email report to Mark and Keith	TM21S EML				20210319
	Aug	24	Tu	~	18:51			Email notification; We8/25 00:26 SSC; Power was down for ~1.4 hrs; Email to Keith and Mark "The Oaks had A REAL POWER FAILURE lasting more than one hour..."	EML SSC TM21F			B61	20210824
	Sep	22	We	~	13:20	~	14:30	Onsite for Fall 2021 Maintenance; Bird's nest; W100 cleaned; Electrolyte -1/8" to +1/8" above plates, cell 2/6 plates exposed; 75°F, 13.34v M (13.25v F); Removed AC & warning email sent / Disconnected battery for 1 min (internet down ~2 mins); Absorption 14.37v M (14.3v F); Photos before and after; Screenshots of 2.5 hr Absorption (14.05v N) and Float (13.25v N)	TM21F IMG EML SSC				20210922
		30	Th	~	13:00	~	19:30	Email notifications (6) 13:11-18:14; 18:20 screenshot shows sudden drop from 13.25v to 12.8v N; SMS to Keith & Mark; Call from Mark; Mark onsite, W100 lights are both solid green; I logged in again, 12.8vN / Mark removed & reapplied AC, then 13.25vN (where it was from before ~13:00); Evidently W100 needed to be reset; (3) screenshots 10min/1hr/24hrs	EML SSC SMS TM21F		WP10		20210930
	Dec	31	Fr					L1-3 L6-7 L10-16; Visited	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16	TM21F DBT EML				20220104
	Jun	8	We					See DNT for notes on Call from Mark, where he mentions that no sites came down because of the tornado weather (01:00-02:00) except OT (fixed by Netonix reboot)	DNT TM22				20220608
	Sep	8	Th					L1/3/10/14-18	TM22 L17				20220908

## L16
Locations: L16	A					TLNB: TurboNet Lexington New Building, 109 S 10th ST

Date/Time CST/CDT					Description	Other Sources	Status	UPS	Batteries
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	A2	B27_28
2020	Jun	16	Tu	~	11:50	~	12:35	Onsite with Keith at Skeeter Tower [ST]: This is about the time that I started hearing that they had obtained the bank line of credit and were buying a new office building in Lexington [TLNB]	L13	Moving			20200616
	Jul	13	Mo		14:54			L15-16	L15				20200713
		27	Mo	~	11:29	~	12:15	Calls to/from Mark and Keith: Among other topics we also discussed the new office building electrical (3-phase power, "come over and reroute some stuff") / New Tower Electrical and New Building Electrical are direct spinoffs from WP10, where times/costs are recorded	WP10				20200727
		30	Th	~	10:27	~	10:30	Call from Mark, the H&C work in the new building is done, "please come discuss the electrical changes/improvements needed," 109 S 10th ST, W of courthouse, 2 story brick building, Fr7/31 09:30 appointment					20200730
		31	Fr	~	16:00	~	17:15	Onsite: Notes and photos of needs; See white sheet for TW6-10 for details; They are trying to move in to the new building by end of August / TurboNet Electrical Planning Onsite Visits; New Tower, Evans Heating & Cooling; New Building, Keith Jones; Subaru	TW6-10 SMS IMG WP10 WS				20200731
	Aug	3	Mo	~	17:13	~	17:29	Call from Mark: Discussed Building Electrical (I gave him a rough estimate, but I will send something more concrete tomorrow morning), other projects discussed	WP10				20200803
		4	Tu	~	06:20	~	08:30	TODO and .ods related to New Building and New Tower [OT]; Research for quote on New Building Electrical (decided to "pass"); Phone calls/SMSs to Keith and Mark; TODO Priorities rearranged / See TW6-10 printouts of research and phone calls	TW6-10 SMS WP10				20200804
				~	09:00	~	10:00					20200804
		11	Tu	~	12:05	~	13:45	While with Keith onsite at Swafford tower [RN] he related that he had just gotten the fiber setup with UPS moved to the New Building (A2/B27_28 L4->L16)	L4	Active	A2	B27_28	20200811
2021	Mar	14	Su	~	12:20	~	13:30	Onsite for the Backup Power Supply Maintenance Program; Ambient 85°F; Float 27.3v (Fluke equivalent) / Load 1/4 bars (0-25% or 0-112.5w or ~56w); Run-time estimate >=10 hours (112.5 watts, capacity derated to 90% for age and 50% for Liebert SLA discharge limit); 10 min discharge test AOK (estimated 98.5% SoC)	DBT TM21S SMS				20210314
		16	Tu					Email report to Mark and Keith summarizing visit to TLNB Su3/14	EML TM21S				20210316
	Aug	13					Lexington office discussion with Keith (MikroTik); Note added 12/27/21 (during .ods General Review): I remember checking on the server room and found that they had installed an air conditioner to lower the ambient / It was about 75°F (Keith had a thermostat reading this) and I recommended he set it to 68°F (which I saw him do)	TM21F		A2	B27_28	20210813
	Sep	22					Lexington Meeting with Keith and Mark (MikroTik) / [Note added 12/27/21 (during .ods General Review): I remember checking on the server room and it was nice and cool (I had asked Keith to set the A/C thermostat at 68°F)]					20210922
	Dec	31	Fr					L1-3 L6-7 L10-16; (TLNB was not scheduled to be maintained, not mentioned)	TM21F DBT				20211231
2022	Jan	4	Tu					L1-3 L6-7 L10-16	TM21F DBT EML				20220104
	Feb	21	Mo	~	14:25	~	14:45	In return from ONWT I stopped at the Lexington office to return the Mier enclosure key to Keith	TM22 L14				20220221
	Mar	6	Su	~	19:30	~	21:45	Lexington Area Power Outage: [power was off at LWT for ~2h15m]; TLNB power also may have been interrupted	TM22 L10				20220306
		9	We	~	14:06			SMS from Mark "I think we need this at the Lexington tower" and photo of Liebert UPS and batteries on fiber backbone / Images\DC\20220307;09DC MO, Lexington, From Mark Webb, TurboNet; LWT Power Outage, TLNB Server Room [O]\20220309 1503 From Mark Webb, MMS, TLNB Server Room IMG_0039.heic and .jpeg	TM22 SMS IMG L10		A2	B27_28	20220309
		10	Th		07:45		12:02	L10/16	TM22 SMS				20220310
	Apr	14	Th	~	15:30	~	15:35	I went to the office after installing the Traco at LWT to see if I could get Dakota or Keith to make screenshots of the LWT Netonix; But office was locked	T48-2				20220414
	Jun	28	Tu	~	14:20	~	14:55	Onsite at TLNB: Rec'd $1840 and keys to WWT; Discussed new site(s) coming up in Carrollton (W50/B26 to go there soon), WWT (will be AC only), and 48v for RWWT	TM22 L18 L6 L11 WP1 B26				20220628
				~	16:40	~	16:45	Onsite at TLNB: As I was driving up Mark was leaving, we met in the middle of the street (car to car); Returned WWT keys and mentioned I was headed next to RCWT	TM22 L6				20220628
	Jul	5	Tu					Lexington Power Failure: While travelling in CO I rec'd MMS/SMS from Keith; "Should this be all the way up at the shop" / Photo of Liebert at TLNB: G:\Images\DC\20220705DC MO, Lexington, From Keith Jones, TurboNet; Liebert at TLNB [O]\20220705 1113 IMG_3488.jpeg / Call to Keith: Power loss for several hours in Lexington; He had to reset the fiber stuff; I explained to him how the 4 bar indicator on the Liebert works (photo shows load is 1/4 bars, as it was 3/14/21, ~56w) / Keith requested visit to look at TLNB & improve (TODO at bottom of list)	TM22 SMS IMG L10		A2	B27_28	20220705
		22	Fr					Lexington Power Failure: Keith notified me of this when he was here at the shop to pickup the power cable for CFS / When he left the Lexington shop at about 11:00 the power had been off for about 30m and the Liebert was showing 4/4 bars battery remaining; I didn't hear about when the power was restored	T48-4 TM22 L10 L18				20220722
	Sep	8	Th					L1/3/10/14-18	TM22 L17				20220908
	Oct	21	Fr					Onsite at TLNB after LSWT Installation: Rec'd $813.00 for W150_1 invoice; Photos of Mark in his office; Discussions with Keith (CFS, the W150s, business and Ukraine)	T48-3 IMG L17				20221021
	Dec	22	Th					L3/6/16-18; Includes Fr10/21 photo of Mark in office	T48-3 DBT EML L17				20221222
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML				20230303

## L17
Locations: L17	A					LSWT: Lexington South Water Tower ("Big Blue"), 16245 Locust Grove Ln

Date/Time CST/CDT					Description	Other Sources	Status	Charger	Battery		Load Supply	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					DC-DC
				Active	BC9	B58	V11	S17	WP11
2022	Jun	10	Fr					Call from Mark & Keith: Requested Wiegmann enclosure be setup for new site LSWT ("Big Blue"); Enclosure was purchased Fall 2021, and is in storage in the garage / Exposed outdoor site, 48v and Power Cable needed for MikroTik switch and (1) PBP with (2) 48v Mimosas / Estimated battery load ~50w, because it must be less than the ~85w last seen at ONWT that has (3) PBPs and (3) Mimosas; T-105s will not be needed, a 27TMX will do (~24h runtime at 50w) / Briefly discussed Schauer charger problems, I just today discovered the problems with the T-comp reversed above 35degF (95degF) / I didn't mention that we could use a W100, as I'm not happy to install those in outdoor exposed sites anymore, due to the T-comp reset problem (resets only at power failures) / Discussed WWT, T-105s and W100 should be replaced with W50 and SLA (only 4 customers there, low power) / Discussed RCWT, 27TMX should be replaced with T-105s from WWT (site power is still expected to be >75w) / Need a new battery charger / power supply design for LSWT: / Planning on Float Only "Dual Supply" design with Traco isolation; SMS to Mark & Keith "Wiegmann enclosure is 30x30x12 inches HxWxD"; New Project "MikroTik 48v System LSWT" / [Tu8/30: Charger, DC-DC and Load Supply integrated into WP11/W150_1; WISPer column added and history sheet started]	T48S T48-3 SMS L6 L3 BC9/10	On Order					WP11	20220610
		14	Tu					Created FTR and paper files: 20220610^… T48-3 MikroTik 48v System LSWT FTR.docx; TurboNet File Folder 0.7x3.25 T48-3.lbx	T48-3 DBT LBX					20220614
		16	Th					Proof of Principle tests of Traco and ~54v power supply on output: / BK as "Battery": TP_3 as prepped ~52.8v output; MW_1 with output adjusted ~54v; ITECH 85w "load" with sense at MW_1 output / Initial results promising but BK doesn't have enough current for Traco startup into 85w / T-105s on floor on ENC (clip leads): At ITECH 85w transitions OK when MW_1 OFF/ON; Traco idle power 0.03-0.05aE (0.4~0.7w) (13.5~14.5v ENC Float~Absorption) / MW_1 can supply 180w (~54.1v @ ~3.3a) but won't start above 10w if Traco is not up (hiccup overload) / [Note added Mo6/20: This is not a fair test; ITECH CW is a direct short at startup, and the MikroTik/Mimosa loads are not like that, they are more resistive below the operating voltage input range (18-57v); I had no problems starting S13 into a 165w load with Traco not up when ITECH was set for Von=10v] / 20220616 1714 IMG_2597 PSE.jpg / SUMMARY CONCLUSIONS: The only way to find out what the limits are with this approach is to build a solid setup / TODO when we have a good test setup; We need to order (will propose plan to TurboNet)	T48-3 IMG S2 Z17 B70/71 BC3 BC9/10	R&D			V11	S13	WP11	20220616
		20	Mo					Many TFTP and notes added to FTR and TODO during the past few days: Dual Supply design advantages are "Easy Prep" and "Total Redundancy" (Su6/19 FTR updated today) / Experiments with ITECH Von and S13: S13 will start into ITECH 165w load if Von=10v, but not if Von=5v / S13 may be useable for LSWT and the future, ITECH 165w is 54.1vI @ 3.05aI which is not above the S13 current spec (3.3a) but slightly above the S13 power spec (158.4w) / Yet TODO availability research for Battery Charger and 54v Supply	T48-3 Z17					20220620
				Researched Availability of a higher powered Battery Charger for Dual Supply Design (Mean Well): Desired specifications ~150~200w, BTS -5mV/cell/degC, Bulk CC + Float CV / SCP-75-12 (in stock MOU/DKE) is the highest power seen in that series (no 150 or 200w versions); Mean Well has nothing as simple as SCP series above 75w (many other offerings investigated briefly) / TFTP: For LSWT we can propose using SCP-75-12 (order), 27TMX (RCWT/WWT), LRS-150F-48 (stock)	T48-3 BC9/10					20220620
		21	Tu					Began draft of LSWT Proposal, Schedule Estimate and Request for Advance: 20220621 Proposal - LSWT Installation.doc; 20220621 Diagram 'Dual Supply with Traco Isolation' SSC Scan.jpg	T48-3 SSC DBT					20220621
		23	Th					Completed 20220621 Proposal - LSWT Installation.pdf; 20220623 Email to Mark & Keith 'Proposal - Lexington South Water Tower Installation'.pdf / Calls and SMSs Mark & Keith: Mark will pay $1,600 advance Mo-Tu next week and "go ahead and order"	T48-3 DBT EML SMS BC9/10	Assembly					WP11	20220623
		24	Fr					DigiKey order placed for battery chargers and NTCs	T48-3 EML DKE BC9/10					20220624
		26	Su					Procurement planning for other items needed (review of entire design/installation): Working Copy of diagram "Dual Supply / Traco Isolation"; Checked stock and compiled list of items to order / TFTP "Standardization is the wave of the future for TurboNet": We need a 200w Float Battery Charger with BTS; Even indoor sites should have an enclosure / Keep looking for Dinico that doesn't need reversing relay; Need LRS-200F-48; Need to gear up to provide the MikroTik power plugs w/o robbing the adapters; Need fancy strippers for the Belden cable / Need weatherproof crimps for power cable assembly onsite by the guys [or a small NEMA 3R enclosure mounted on antenna mast]	T48-3					20220626
		27	Mo					DigiKey orders placed: / Fuses (SCP-75-12 10a) / (4) Power cable disable switches (LSWT, ONWT, LWT and spare [which will be needed at CSF]) / [Sa9/10/22: Power Cable Switches are slated for WP11/12/13/14 WISPers for LSWT, CFS, Spare and ONWT or LWT] / 5/16" ring connectors / Reversing relay for bench Dinico; Shrink Tubing / Received DigiKey order placed Fr6/24 (battery chargers and NTCs)	T48-3 EML DKE BC9/10 WP12 WP13 WP14					WP11	20220627
		28	Tu					Dismantled Proof of Principle test setup / Call from Mark & Keith as they were driving to LSWT, rent starts at LSWT the day they get something installed, new sites coming up (Carrollton, not exposed, see TM22) / Onsite visits to TLNB, WWT and RCWT to swap out equipment and obtain 27TMX for LSWT (TM22)	T48-3 TM22 L18				V11	S13		20220628
		29	We					DigiKey orders received (DKE and WEC Marketplace)	T48-3 DKE					20220629
2022	Jul	19	Tu					Call from Keith: Ordered new site CFS / LSWT has no AC power yet (they need to trench) and so the pressure is off to complete T48-3; Keith to be at the shop Th7/21 10:30-11:00 with a switch/router for LSWT	T48-4 L18					WP11	20220719
		21	Th	~	11:05	~	11:35	With Keith at shop to discuss Power Cable Assembly for CFS: / He forgot to bring a MikroTik switch/router for LSWT back plate fitting, he'll bring it tomorrow ~11:00~11:30 when he comes to pick up the Power Cable Assembly					20220721
		22	Fr	~	11:25	~	11:35	Keith here to pick up the Power Cable Assembly for CFS: He brought me a MikroTik switch/router, for mounting hole fabrication of back-plate for LSWT	T48-4 T48-3 L18					20220722
2022	Aug	9	Tu					Finished fabrication of two brackets for Dinico Fan Controller Assemblies; Ordered epoxy (Amazon) and fuse holders (DigiKey); Assemblies to be finished when fuse holders are received	T48-3 EML DKE Z20 Z19					20220809
		10	We					L10/14/17/18	T48-3 IMG LBX L14 L10 L18 WP12 WP13 WP14					WP11	20220810
		12	Fr					Wiegmann Back Panel design and layout: Scale tracing/drawing of MikroTik Cloud Core Router showing underside mounting hole slots; 25.8cm separation for 6-32x1/2" RHMS / 20220812 MikroTik Cloud Core Router Mounting Holes; Tracing-Drawing; T48-3; Scan 8.5x11.0.jpg / 20220812 MikroTik Cloud Core Router Mounting Holes; Tracing-Drawing; T48-3; Scan.jpg / Power Cable Disable Switch will be mounted upside down at top; Printed 4x TurboNet Disable Switch 48V Power Cable OFF ON 0.7.lbx / Photos of layout work on garage bench; Design and layout finished in pencil on white paint of back panel; Center punched all holes	T48-3 SSC DBT LBX IMG					20220812
		17	We					Wiegmann Back Panel ready for test bench (photos); (2) Dinico Fan Controller Assemblies completed (photos)	T48-3 IMG LBX Z20 Z19 L14					20220817
		18	Th					Prep of Supplies/Chargers: L/N/G AC Plugs, BC9 12", S13 24" and (2) longer utility plugs for bench use, Battery Charger - Wire Label 0.5 in.lbx, Load Supply - Wire Label 0.5 in.lbx / S14 and S13: Adjusted for target 54.000vI; 54V Load Supply.lbx printed (to be applied to Wiegmann back plate) / BC9 and BC10: Printed and applied Inventory Sticker 0.47.lbx; Battery Charger.lbx printed (to be applied to Wiegmann back plate); Assembled and soldered BTSs to CN2 connector pins, BC9 photos / Epoxied BC9 BTS into 5/16" lug and covered with shrink	T48-3 LBX S14 BC10 IMG		BC9			S13		20220818
		19	Fr					Further Prep of SCP-75-12 Chargers: Fabricated battery connections; Adjusted BC9 and BC10 for target of 13.500vI at 25.0⁰C (no battery, BTS metal pipe in Engel, ITECH CC 150mA)	T48-3 PLN BC10 Z0					20220819
		20	Sa					Dual Supply Bench Testing Setup Assembled: Wiegmann Back Panel on bench; Traco cabling fabricated; Back Panel wired up; Instrumentation connections / Stabilizing towards +25.0⁰C	T48-3 PLN W10 Z0 Z20	Testing		B58	V11	S13	WP11	20220820
		21	Su					Test setup dissasembled briefly to add shrink to Z20 T2 and BC9 BTS; Stable at +25.0⁰C (Z20 T2), BC9 T-Compensated Float data recorded (agrees perfectly with Fr8/19 adjustment)	T48-3 PLN Z0 Z20					20220821
		22	Mo					Bench Testing: Problems discovered immediately / By varying ITECH Von Living settings I was able to determine that the Traco transition from idle (Load Supply) to battery drops the output below 5v (120w load) / Experimented with capacitance on load and setting S13 output closer to V11 output (no improvements) / Paradigm Shift: Back to R&D; New Design "Isolation at INPUT of Traco"; Started availability research (Load Power Supplies and Diodes)	T48-3 PLN S14 S17	R&D		B58	V11	S13	WP11	20220822
		23	Tu					Free-thinking and research on new design "Isolation at INPUT of Traco": Diode properties (can they be put in parallel? How do they fail?); Initial Schottky diode availability research / Another good idea, white sheet diagram "Dual Supply Isolation at Traco INPUT" showing relay contact in parallel with diode / Can use a standard diode instead of a Schottky; Began Failure Modes Analysis	T48-3 WS					20220823
		24	We					Tested Traco Maximum Power Limits in range 169-187w: Test setup improved (replaced #18 with #14 solid) / 175w is a very safe limit close to the Traco specification of "105% of Iout" (3.36a, 52.8v, 177.4w); At 175w we need ~206w at Traco input (observed, measured) / More Load Supply Availability Research: Multiple CONCLUSIONs including settings for Load Supply and fixing an overall system design limit of 165w (Traco Output) / Silicon Diode and Relay Failure Modes Analysis completed: We do NOT want a relay or diode failure, battery damage and safety issues could be extreme / THEREFORE source high reliability over-rated components; Various TFTP including "LSWT must use isolation at Traco INPUT and relay/diode design" / Missed call and SMS from Mark, who wants status on LSWT	T48-3 PLN			B58	V11	S13		20220824
		25	Th					R&D: TFTP Two diodes in series? (idea rejected, many standard diodes have high PIV) / Continued Availability Research, load supplies / Reexamined Mean Well RSP-200-13.5 [ordered Sa8/27], TFTP big advantage due to higher power level possible at voltage trimmed up to ~14.7v [Sa10/1 Design changed to 13.8v] / The Current Design Embodiment (summary); Availability Research, relays, discovered Omron MJN1Z-E-RP-AC120 [ordered Sa8/27]; Began Availability Research, diodes / Prepared thoughts about what to say to Mark, calls from Mark and Keith: CFS is up and running on WP1/B26; LSWT should be installed first, then CFS / I estimated LSWT installation could be Sa9/3 to Sa9/10; Mark to order more Belden 88760; Call from Mark (who was Belden cable supplier last year?)	T48-3 PLN L18					S17		20220825
		26	Fr					Followed up on call from Mark Yesterday: Email to Mark "Belden 88760" (11/1/21 Interstate Wire $1000, watch out for "similar" and "equivalent" listings)	T48-3 EML SMS					20220826
		27	Sa					Availability Research finalized for Load Supply, Diode and Relay: Selected diode Vishay VS-80PF80, Stud Cathode will be tied to FG (Field Ground, Equipment Ground) (at battery negative) / White sheet diagram: Dual Supply with Cathode Grounded Diode Isolation, also shows Traco Output diagram with FG for Power Cable Shield / 20220827 Dual Supply with Cathode Grounded Diode Isolation; Traco Output; Schematics; T48-3; Scan.jpg / Did some thinking and research on surge protection devices for the Traco (possible improvement but not now); Some confusion on Omron MJN1Z-E-RP-AC120 [cleared up on Th9/1 Orders Receiving] / Placed DigiKey and Mouser Orders ($124.44) / [Su9/11: We now know the diodes are slated for WP11/12; The 2nd diode was ordered in case I blew the first one in Testing, but I'll most likely use it for WP12] / Saved datasheets to Library: / Mean Well > 20220827 RSP-200 Series Data Sheet.pdf / Vishay > 20220827 Vishay Standard Diodes VS-80PF Series.pdf / Omron > 20220827 MJN Series Relays 090600_OMRON_MJNdatasheet_J34I-E-01[1]-1189366 (from Mouser, best found).pdf	T48-3 SSC DBT EML DKE MOU LIB WP12 PLN WS					S17	WP11	20220827
		29	Mo					Orders invoices received, printed and annotated; Billable Hours Revised: / Removed all R&D and extraneous costs, current estimated billing total $1,524.77 with parts and materials; Reduced Rate R&D will probably all be "No Charge" (currently >100 hours)	T48-3 EML DKE MOU					20220829
		30	Tu					"W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; From now on, R&D and Assembly details of the prototype for LSWT should pivot from WP11	T48-3 L18 BC10	WP11 R&D	BC9	B58	V11	S17	WP11	20220830
2022	Sep	1	Th					L10/14/17/18	T48-3					WP11	20220901
		2	Fr					Phone calls with Mark concerning AC power at site: "Electrician will be onsite at LSWT next week, can we get the box there by then?"; NO, estimated installation week of Mo9/12 / The "guys" are trenching today and will place the support posts soon / They thought to face the box East, but I told him to make it face North (they can), recommended they place 3 poles 13.5" centers tops 5 feet above ground / He's planning on installing a 30A breaker on the pole about 100' from our box; 1" conduit will be used at pole and Wiegmann ends (most of the distance no conduit) / They already bought 250' of #10 Romex (orange), this is not UF (Underground Feed) and it s/b #12; Recommended 20A breaker at pole and #12-3 UF Romex / He said they already buried the wire, but he'll see if they can straighten it out					20220902
		3	Sa					SMSs from/to Mark: The only thing they have is 250ft of 12/3 grey. I'm buying that. Ok; To Mark That's the right stuff. Direct Bury, UV Resistant (conduit not needed). 20A breaker at pole. Perfect.	T48-3 SMS					20220903
		7	We	~	13:30	~	14:10	Visit from Brandon and Dakota: Appointment for Th9/8 10:30 / They will pickup the MikroTik switch/router and PBP tomorrow, and they can bring me a check from Mark ($638, I was working on Report & Invoice when they showed up)	T48-3 TM22					WP11	20220907
				L3/6/17	TM22 T48-3 TPC2 T48S TM21F DNT T48-4 DBT IMG SMS EML L6 L3 L18					20220907
		8	Th					Brandon and Dakota at Shop: (Upgraded DVS equipment on roof from Ubiquiti to Mimosa, see L Shop) / Genuine Belden 88760 cable spool (500') and MikroTik adapter from Keith; Gave them boxed MikroTik (complete) and PBP (minus adapter) to take to Keith / $638 check from Mark (TM22 We9/7 Invoice for WWT/RCWT Equipment Swaps); L1/3/10/14-18	T48-3 L TM22 TM21F TPC2 T48-2 T48S T48-3 T48-4 L15 L3 L10 L1 L14 L16 L18					20220908
		11	Su					"Stay the Course" (R&D TFTP): / Priorities Considered: Stick to my plan to get the .ods work and the T48-4 invoice done before starting assembly and testing of the prototype W150 / New ETA for LSWT installation week of Mo9/12-Sa9/17	T48-3					WP11	20220911
		13	Tu					White Sheet "If Mark calls about LSWT": Estimated prototype assembly, bench testing and Wiegmann assembly schedule; Earliest onsite install estimated ~Th9/22 to Sa9/24 (end of next week)	T48-3 WS					WP11	20220913
		15	Th					LSWT mentioned in Report, photos and email: / 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 DBT EML L18					20220915
		16	Fr					Billable Hours Revised: Procurement, Parts and Assembly Separated, W150_1 and Wiegmann; Printed and applied new label TurboNet File Folder 0.7x3.25 T48-3.lbx	T48-3 LBX					WP11	20220916
		17	Sa					Billable Hours Revised > New Totals Fr6/10 to Fr9/16: See WP11	T48-3					20220917
		21	We					Mark and Keith: Mark wanted to know if we can install "early next week"; TODO priorities shifted (postponed .ods recordkeeping, invoicing, WP11A); Earliest onsite install estimated ~We9/28 to Sa10/1 / SMSs to Mark and Keith "Maybe, but late next week is more likely. I promise you it will be worth the wait, the W150 modular dual power supply is impressive (we enter a new era)"	T48-3 SMS					WP11	20220921
		23	Fr					Sent EML to Mark & Keith: Project set back another 2 days due to fabrication method change [actual schedule delay turned out to be 5 days]; I said "could be ready the week of Mo10/3"	T48-3 EML					WP11	20220923
		27	Tu					Started Assembly of W150_1 (backplate fabrication)	T48-3	Assembly					WP11	20220927
		30	Fr					Parts Assembled Onto Backplate, Started Point to Point Wiring and Cabling: Marked Wiegmann backplate for W150 mounting stud locations; BTS cable is short but OK for Wiegmann/LSWT					WP11	20220930
2022	Oct	2	Su					... Point to Point Wiring and Cabling FINISHED; Assembly FINISHED (minus labels): Prepared MikroTik adapter for LSWT Enclosure / Bench Testing Started (+25⁰C): Proof of Principle Tests Passed / TFTP Political/Financial/Scheduling Concerns: Changes in plans, will not do full environmental testing now (W150_1 in Engel), postponed until we have W150_3 and 27TMX spares		Testing					WP11	20221002
		3	Mo					Bench Testing (-15⁰C): Stabilizing, looking for PSP; Burn-In Test Passed / Mark and Keith Communications: SMS from Mark asking if we can do LSWT installation We10/5 or Th10/6? / EML to Mark and Keith with photo of bench setup, W150_1 next to Engel (IMG_3273 PSE.jpg), I proposed Tu10/11; They insist must be Th10/6 [I purposely waited until We10/5 to say anything more]	T48-3 SMS IMG EML					20221003
		4	Tu					… Mark and Keith Communications: Other options for LSWT briefly considered (W100? T-105s? LWT V10?); Bench Testing (-15 and +50⁰C) / Say nothing today; Planned message for We10/5 "Sorry, I'm sick, I guess I haven't been getting enough sleep lately. I'll let you know when I feel better and can install at LSWT"	T48-3					20221004
		5	We					Mark and Keith Communications: "Sorry, I'm sick, I haven't been getting enough sleep lately (I've worked 70.1 hours in the past 7 days)."; Mark agrees to Tu10/11 11:00 installation at LSWT / Mark will come here to help move Wiegmann; Other scheduling and preparation communications; W150_1 Bench Test Setup photos and video (A Hard Day's Night, sent to Mark and Keith)	T48-3 SMS IMG					20221005
		6	Th					Bench Testing (~25⁰C): Bench Testing Finished / Mark Communications: Mark helped me move the Wiegmann enclosure to the garage bench (received $178 check for CFS Power Cable Assembly)	T48-3 SMS	Assembly					20221006
		7	Fr					W150_1 Final Assembly and Invoice Date: Labels applied; [Invoice emailed to Keith and Mark Fr10/21]; Beginning Wiegmann and Power Cable Assemblies Prep	T48-3	Prep					20221007
		9	Su					Wiegmann Prep: Holes drilled/punched (4" Integra stuff and holes in bottom); Installed W150 mounting bolts on back panel					20221009
		10	Mo					Wiegmann Prep: List of miscellaneous items to be billed at cost; Backpanel (AC outlets prep), installed in Wiegmann; Photos; Installed exit vent Integra shroud (window screen, silver tape); Installed Z20 Dinico and intake fan assembly, tested; (2x) DO NOT LIFT HERE Plastic Shrouds 0.94 Yellow.lbx; Applied labels Dinico DIN-S-CF Settings.lbx and Dinico Caution! 120 VAC.lbx; B58 battery spacers, right side of battery centered on the fan; Wiegmann Mounting Bolts, found (4) 3/8-16 HH old bolts with lockwashers, washers and nuts; Printed and applied labels for enclosure, Front TurboNet & Data Vision Services Phone #s 1.4.lbx, Inside Front Wiegmann Inside Cover LSWT W150_1 Prototype 1.4.lbx; Photos; Wiegmann Enclosure Fabrication and Assembly COMPLETED	T48-3 IMG Z20 LBX			B58				20221010
		11	Tu					Power Cable Assembly: One MikroTik adapter; Labels Power Cable Splice Down 0.94.lbx and Power Cable Splice Up 0.7.lbx; Photos / Mark, Installation Postponed (1st): Raining, rescheduled for Th10/13; Applied replacement label Wiegmann Inside Cover LSWT W150_1 Prototype 1.4.lbx / Loaded Subaru for Onsite: B58; W150_1; Info for inside cover (fan cooling system schematic copy, Dinico instruction sheet) / Brandon and Dakota Here: Wiegmann, Mounting Bolts and Power Cable Assembly picked up (to be taken to LSWT); Invoice Date [emailed to Keith and Mark Fr10/28]	T48-3 LBX IMG Z20	Install					WP11	20221011
		12	We					Mark, Installation Postponed (2nd): High winds, rescheduled for Fr10/14	T48-3 SMS					20221012
		13	Th					Mark, Installation Postponed (3rd): The guys are onsite installing the Wiegmann; Meeting with Mark, USB parking lot, high winds continue, tentatively rescheduled for Mo10/17					WP11	20221013
		17	Mo					Mark, Installation Postponed (4th and 5th): Early in the morning we agreed to install Tu10/18; But later Mark thought it would be too cold and we rescheduled for Th10/20	T48-3 SMS L18					20221017
		19	We					Mark, Installation Postponed (6th): Now they want time to get the other stuff placed on the tower before I show up; Rescheduled for Fr10/21 (assuming 10am onsite)	T48-3 SMS					20221019
		20	Th					Mark, Installation Time Changed (7th): He wants me at office at 11am (Fr10/21)					20221020
		21	Fr					20221007 Report, Photos & Invoice - W150_1 for LSWT.pdf emailed to Keith and Mark: Includes "Ha ha" 20221008 1036 IMG_3315 PSE Backplate and Eggs.jpg / Prep to go onsite, Prints for inside of Wiegmann door: New label with today's date Wiegmann Inside Cover LSWT W150_1 Prototype 1.4.lbx; Pages 3 to 5 of Report, Photos and Invoice / Mark Communications: He wants me to go directly onsite and not to the office, shooting for 11:00; Google Maps has the site as 16245 Locust Grove Ln / Onsite at LSWT: Windy but warm; Photos; Breaker at pole is 20A; AC outlets wired up and tested; Installed spacers and B58 / T1 sensor silver taped through 1/4" hole; Fan control system plugged in and tested / Installed WP11; Connected B58, BTS and Z20 T2 on negative post, foam caps, battery terminal spray / Installed enclosure MikroTik plug (wired to the barrier strip, ready to be used, but Keith is not planning on installing a MikroTik in the enclosure); Mark finished installing the PBP and two antennas / Attached power cable and Keith turned on the Power Cable Switch; Power levels measured, Traco Input 32.6w (27TMX runtime estimate ~>36h), Output 27.5w / Photos, some with Keith; Discussions with Keith (future plans for CFS, the W150s and other potential customers) / Onsite at TLNB: Rec'd $813.00 for W150_1 invoice; Photos of Mark in his office; Discussions with Keith (CFS, the W150s, business and Ukraine)	T48-3 DBT IMG EML LBX SMS Z20 L16	Active	BC9	B58	V11	S17	WP11	20221021
		22	Sa	~	15:15			Missed call from Mark [see T48-3 Su10/23]	T48-3					20221022
		25	Tu					Started Wiegmann Invoice Draft; DVS Letterhead Redesigned (see WP11)	T48-3 DBT					WP11	20221025
		28	Fr					L3/6/17; «Drilling those two 4" holes was a Son-Of-A-Bitch»	T48-3 DBT EML L6 L3 Z19 Z20			B58				20221028
2022	Nov	1	Tu					Call from Mark: He's cutting a check for last weeks invoice ($959, Wiegmann prep); I asked if we could meet in Richmond, he said perhaps We11/2 and he'll contact me	T48-3 T48-4 L18					20221101
		15	Tu					Met Mark in lobby of USB, rec'd $959 (Wiegmann prep)	T48-4 T48-3 SMS L18					20221115
2022	Dec	22	Th					L3/6/16-18; Includes Fr10/21 photos at Big Blue; In email I wrote "... towers do have addresses."	T48-3 DBT EML L6 L3 WP14-18 L16 L18					WP11	20221222
2023	Feb	8	We					Invoice EML to Keith and Mark: 20230130 Report & Invoice - W150_2 and W150_3 for CFS and Spare.pdf; LSWT mentioned in report	T48-4 DBT EML WP12-13					20230208

## L18
Locations: L18	A					CFS: Carrollton Fire Station Water Tower, 708 Harvest Hills DR

Date/Time CST/CDT					Description	Other Sources	Status	Battery	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Active	B26 B70-71	WP1 WP12
2022	Jun	28	Tu					Call from Mark & Keith (while they were driving on the way to check out the new site LSWT): There's new sites coming up, They mentioned Carrollton (not exposed) / Keith mentioned it again when I was onsite at TLNB	T48-3 TM22 L17 L16	Mentioned			20220628
2022	Jul	19	Tu					Birth Date of New Project T48-4, Call from Keith: Ordered Power Cable for Carrollton Fire Station, (2) PBP connectors / Keith to be here Th7/21 10:30-11:00 with Belden cable spool, 2 adapters, PBP and a switch/router for LSWT; Keith will install the Power Cable soon, but we have 60 days to complete the site / CFS is an indoor site (under the water tower which is next to the fire station) / Standard equipment rack "4 feet high" IMG from Keith: Images\DC > 20220714 0827 From Keith MMS, Equipment Box for CFS; 99C8D30E-13FA-4F2C-9577-6ED662623844IMG_3503.jpeg / Keith said it's 4' high, but it looks to be more like 2.5' high; I asked for the bottom 2' for the power components (including batteries) / Eventual plans are for B11, B5, A5 and (2) B24 (all Mimosa 48v); This is an important site with a fiber backbone and s/b (2) T-105s with Dual Supply for up to 165w load / W50/B26 will be used temporarily / If need be can pull Traco from LWT (Keith has not yet returned to load it yet); LSWT has no AC power yet (they need to trench) and so the pressure is off to complete T48-3 / Keith notified me that he removed the W50/SLA from WWT (sometime in the past few weeks while I was in Colorado) and the W50 is partially installed at CFS (B26 is in Keith's service vehicle) / [Tu8/30: New charger, DC-DC and Load Supply integrated into WP12/W150_2; WISPer column added and history sheet started] / [Sa9/10: WP13 slated for emergency Spare; WP14 slated for W150 Production Run #2]	T48-4 SMS IMG L10 / L17 L6 / WP11 / WP13 / WP14	On Order	B26	WP1 WP12	20220719
		21	Th	~	11:05	~	11:35	With Keith at shop to discuss Power Cable Assembly for CFS: He delivered the Belden Cable (~340') and (2) adapters for MikroTik / He forgot to bring a PBP and a switch (for LSWT), he'll bring them tomorrow ~11:00~11:30 when he comes to pick up the Power Cable Assembly / I saw B26 (from WWT) in the back of his vehicle (HOT!) and he confirmed again that the W50 is partially installed at CFS / He plans to be onsite at CFS Mo7/25 to install cables and hookup the W50/B26/Netonix/antenna (temporary, they haven't installed the fiber yet) / We'll have 30-60 days to finish CFS (I asked again for the bottom 2' of the "4 foot" rack, but IMG rec'd Tu7/19 shows it is probably only ~2.5 to 3' high); Discussed his recent visit to RW	T48-4 L17 L1				20220721
		22	Fr	~	08:35	~	10:35	Assembled Power Cable: Saved a 3' sample of Belden 88760; Cut adapters 20" from tip of male plug; Ground wire for shield 20" green 14 AWG stranded; Injected with silicon caulk; Photo	T48-4 IMG				20220722
				Worked on improving the PBP-at-the-top-of-the-tower connection problems: Dimensions of male MikroTik adapter plugs; Sorted through discarded adapters (none useable, need to order) ... / Keith brought me a PBP (test fit feel); Proposed small NEMA 3R box for top-of-tower connections (Keith says he'll send me a picture of the fiber boxes mounted on his house, they're small and cheap)	T48-4 TPC2				20220722
				~	11:25	~	11:35	Keith here to pick up the Power Cable Assembly: Keith is still planning on installing the Power Cable at CFS on Monday / In addition to a PBP he brought me a MikroTik router, for mounting hole fabrication of back-plate for LSWT (T48-3); Power is OFF in Lexington (TM22, TLNB, LWT) / [DBT: 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf emailed to Keith and Mark Th9/15]	T48-4 T48-3 L17 TM22 L16 L10 DBT				20220722
2022	Aug	10	We					L10/14/17/18	T48-3 IMG LBX L17				20220810
		25	Th					Call from Mark and Keith: CFS is up and running on W50/B26; He's happy with this site for now, so LSWT should be installed first, then CFS / Keith saw ~78w (MikroTik and Mimosa interfaces), I wouldn't be surprised if it was actually higher than that, as he's not seeing the total battery load / He knew that WP1 is rated 75w, so he took some stuff off and dropped it down	T48-3 L17		B26	WP1 WP12	20220825
		30	Tu					"W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; From now on, Assembly details of the first production unit for CFS should pivot from WP12	T48-3 L17			WP1 WP12	20220830
2022	Sep	1	Th					L10/14/17/18	T48-3 WP11				20220901
		7	We					20220630 Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps.pdf; 20220907 Email to Mark & Keith 'Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps'.pdf; CFS mentioned in email	TM22 DBT EML L17				20220907
		8	Th					L1/3/10/14-18	TM22 L17				20220908
		15	Th					20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 TPC2 DBT EML L17 L1 WP13 WP14		B26	WP1 WP12	20220915
2022	Oct	12	We					Stock Checks and Additions to Carts (SPSE, DKE, MOU): Tracos (5); Charger (1); Load Supplies (2); Diode (1); Contactor (2); 30A Battery Cable Fuses (25) / Proposal/Estimate/Advance, W150s for CFS and Spare: List of Orders Needed and Estimated Total ~$1500 (out-of-pocket); Other Cash Flow Considerations; WP12 and B70/71 slated for CFS / Mark and Keith EML and SMS: 20221012 Proposal - CFS Installation.pdf (request for $1600 advance)	T48-4 EML SSC DBT SMS WP13			WP1 WP12	20221012
		17	Mo					SMSs from/to Keith (also to Mark): "Is Carrolton close to being ready?"; I referred him to the estimated schedule in the proposal emailed to them on We10/12	T48-4 SMS L17 WP13			WP1 WP12	20221017
2022	Nov	1	Tu					Call from Mark: Will CFS be ready soon?: "Within about 2 weeks" (including spare)	T48-3 T48-4 L17 WP13			WP1 WP12	20221101
		15	Tu					SMS from Mark: "Is the stuff for Carrollton ready? ..."; What to say to Mark? (still working on WP11A/P, priorities examined) / Met Mark in lobby of USB, rec'd $959 (Wiegmann prep for LSWT), discussed scheduling ("After Thanksgiving"); [Mark relayed this to Keith who had asked for the status update]	T48-4 T48-3 SMS L17 WP13			WP1 WP12	20221115
		18	Fr					SMS from/to Keith: "Will that power supply be done the week after thanksgiving"; "Yes, Keith, that's what the schedule looks like" (still working on WP11A/P); SMS from Keith "Awesome"	T48-4 SMS WP13				20221118
		28	Mo					SMS from Mark: "Hey, is that all that stuff ready we're going to go to Carrollton tomorrow if it is call me let me know. Thanks." ...	T48-4 SMS WP13			WP1 WP12	20221128
		29	Tu					... Mark and Keith: Apologies, can't deliver CFS today, orders delayed; Keith disgruntled "So ... We have been waiting all this time for this"; Mark proposes We12/7 installation at CFS / DKE Marketplace items shipped today (NTE/Remington), no ETA yet / DKE, PTD and MOU orders received: S18/19, BC11 and many other parts	T48-4 SMS DKE PTD MOU WP13				20221129
2022	Dec	5	Mo					SMS from/to Keith (and Mark): "Any update on the he [sic] power supply for Carrolton"; 1 or 2 days remain; "... I'll contact you when it's done"	T48-4 SMS			WP1 WP12	20221205
		7	We					SMS from Mark: Wanted to know if Carrollton is done and ready for Th12/8 installation				WP1 WP12	20221207
		8	Th					EML to Mark and Keith: W150 Production Status and Proposals for Temporary 48V; Attached SSC of WP12-13P; Keith angry; Mark continues to ask "When will it be ready for Carrollton?" / TFTP; ""I'll contact you when it's done."; "We've lost a couple thousand worth of equipment because we didn't have the battery backup. So I need it"; TFTP	T48-4 SSC EML SMS				20221208
		14	We					SMS to Mark and Keith "W150 #2 is ready. I can go to CFS tomorrow if that works for you."; Mark scheduled the installation for We12/21 because "It's too cold to go over there this week ..." / [See T48-4 Th12/15: Mark had said it's supposed to be 50⁰F on We12/21, but forecast is for a high of 21⁰F]	T48-4 SMS			WP1 WP12	20221214
		15	Th					Mark said the forecast was for 50degF on We12/21, BUT I'm seeing a high of 21degF on We12/21, in fact, the temperatures don't look like they'll go above 36degF for the next ten days	T48-4 Z0				20221215
		20	Tu					SMS from Mark: Too cold tomorrow; Installation rescheduled for We12/28 which looks to be much nicer weather	T48-4 SMS			WP1 WP12	20221220
		22	Th					L3/6/16-18; Report and EML mentions installation at CFS	T48-3 DBT EML L17				20221222
		27	Tu					Prep for installation at CFS: W150 mounting stud bolt sets prepared	T48-4			WP1 WP12	20221227
		28	We					Prep for installation at CFS, T-105s: Removed from ENC; On bench; Cleaned; Electrolyte checked/filled; Attempted fabrication of Foam Caps for terminals (abandoned); Loaded Subaru	T48-4 PLN SMS B70-71				20221228
				12:00		14:00	Onsite at CFS: Keith had reserved only about 12" space at the bottom of the enclosure, but he angrily removed the bottom shelf to provide almost 24" / Installed W150_2, vertical on left side of enclosure (side panel is removeable); T-105s installed in bottom front (with just enough space above to get your head above the cells); B26 behind T-105s; Photos / WP1 is sandwiched behind the enclosure up against the wall, on edge horizontal, powers the DC Netonix / No loads could be attached, Keith plans to come back "maybe next week" to move all loads to the W150 (some now on AC, some now on WP1/B26) / Keith may move WP1/B26 to CCC (new Location L19) after he gets done with it at CFS; He may leave the DC Netonix at CFS, and I told him to put it on the T-105s, not the W150 / Power Cable stripped but not attached (ends insulated, it is connected to the PBPs at the top) / There are two MikroTiks in the enclosure, I told Keith what he needs to do to the adapters and how to hook them up to the W150; Did not measure power levels (Traco idle) / Did not check to be sure the W150 is charging (all I know is that Keith plugged it into the AC power strip at the back top of the enclosure) / Discussions with Keith revealed information about RCWT and why the internet drops out at RW / Keith read the W150 Operating Range label and questioned what will happen below the "rated" 4degF / TODO for WP13 onwards: There's really no reason not to state -20⁰C as the bottom end; Look up specs on Charger, Load Supply, Contactor and Traco; We might state even lower than -20⁰C	T48-4 IMG L19 L3 L1 WP13-18	Active	B26 B70-71	WP1 WP12	20221228
		29	Th					Installation Followup at Shop: SMSs and IMGs from Keith of MikroTik adapter cutoffs; Verified wire colors; SMSs to Keith explained colors and more; Keith complains of lack of adapters ("I can't help you there for now")	T48-4 SMS IMG				20221229
2023	Jan	10	Tu					Installation Followup at Shop, Communications with Keith TFTP TODO: / On We12/28/22 when onsite at CFS Keith wanted to know where to attach the Netonix if he left it installed, and I told him he should put it on the T-105s and not the W150 output / In telling him this I made a serious error which should be corrected (I didn't think it out) / If a continuous load is placed on the battery, the battery charging is not optimum (and the Netonix load will be limited to <90w or the battery will discharge while AC) / I should have told him "Do NOT place any other loads on the battery being charged by a W150, it must remain isolated" (TODO for owner's manual) / I plan to write to him and explain this, apologize for the error, recommend the Netonix should be placed on the Load Supply (Traco input), and that I can easily provide cables for this purpose / Another advantage of putting the Netonix on the Load Supply is that it can remotely report whether or not there is AC power at the site (for the W150): / If AC is lost or the Load Supply dies the voltage will drop from 13.7 to the battery voltage	T48-4			WP1 WP12	20230110
		14	Sa					R&D TODO: Load Supply Output Cables Option (offer cables to Keith)	DWP				20230114
	Feb	8	We					Invoice EML to Keith and Mark: 20230130 Report & Invoice - W150_2 and W150_3 for CFS and Spare.pdf	T48-4 DBT EML			WP1 WP12	20230208
	Mar	3	Fr					[L10/11/12/14/16/18/19] SMS to Keith requesting communication: Topics I'd like to discuss with him: / CFS final results?; Plans, hopes, desires or ideas for 48V Power Cable installations this year? (list of sites we should discuss includes LWT, RWWT, RHST, ONWT, TLNB and CCC); Production Planning for W150s / Invoice EML to Keith and Mark: 20221229 Report & Invoice - CFS Installation (W150_2).pdf	T48-4 SMS DBT EML			WP1 WP12	20230303

## L19
Locations: L19	A					CCC: Carrollton Country Club Water Tower, Country Club Drive, 9FJX+7Q7, Carrollton, MO 64633

Date/Time CST/CDT					Description	Other Sources	Status	Battery	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				No Backup
2022	Dec	28	We		12:00		14:00	Onsite at CFS: Keith mentions new location (it can be seen from CFS); He may move WP1/B26 there after he gets done with it at CFS, which he says he will try to do within a few weeks	T48-4 L18	No Backup			20221228
2023	Mar	3	Fr					L10/11/12/14/16/18/19 (questions to ask Keith)	T48-4 SMS DBT EML				20230303

## M1
Modules: M1	A					C252_1: 25 Amp Dual Channel Current Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	W10	6/29/19
2015	Jun	18					Ordered	EML WCA	On Order				20150618
		24					Received	WCA	Available	L			20150624
	Jul	3					On the bench with Wattmon_1 for initial test & configuration …	AED	Testing	L0	W1		20150703
		5					Calibrated zero offset only					7/5/15	20150705
		6					Installed at RW	TSP IMG	Applied	L1			20150706
		19					Wattmon_2 installed at tower	AED			W2		20150719
		27					Wattmon_2 brought back to shop, but C252_1 left in place					20150727
	Sep	3					Onsite at RW with Juliya	IMG					20150903
		16					Onsite at RW with Juliya (Sasha's iPhone)					20150916
		19					C252_1 returned to shop	AED	Available	L			20150919
2016	Jun	1					Calibrated with Wattmon_6			L0	W6	6/1/16	20160601
				Installed at RW (with Wattmon_6)		Applied	L1			20160601
		16	Th	>	11:10			Wattmon_6 removed and Wattmon_8 installed at RW	AED IMG			W8		20160616
2017	Jan	19					Onsite at RW to install 3rd Genasun	IMG					20170119
2018	Apr	24					Onsite at RW (to remove W8 for a few days of correction on the bench): Current loop routing (RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery)	AED IMG					20180424
	Aug	13					Onsite at RW 09:15; AC OK; Photos (before); Removed C252_1; Removed W8; Photos (after)	IMG		L			20180813
		15					Used on Wattmon_8 to simulate load during A1/Vin calibration; Deleted Device from Wattmon_8; Now in stock and available		Available				20180815
2019	Jun	25	Tu					[M1-2] Attached to Wattmon_10 for use on W100 Project; Calibration with BK_1 …; [M1] Sheet "20190625 C252_1"	WCX	W100 Test	L0	W10	6/25/19	20190625
		27	Th					C252_1 Current 2 Divider 200 -> 100 (using one loop to double range to 30 amps, this should not affect accuracy of calibration, but at this point I don't care if it does)					6/27/19	20190627
		28	Fr					C252_1 Current 2 Invert 0 -> 1 (this should not affect the calibration, as I'm still using positive upward flow, but group Grid is positive and needs to be negative)					6/28/19	20190628
				[M1-3 M9] W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG					20190628
		29	Sa	~	11:30			Calibration modified: Divider 100 -> 200 (back to using 2 loops and calibrated range of 0-15 amps for the Series Test); Except for Invert this is the way it was calibrated on 6/25/19	WCX				6/29/19	20190629
	Jul	8					[M1-3 M9] W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG					20190708
		14					[M1-3 M9] W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)					20190714
	Sep	26					[M1-3 M9] On or after 9/26/19: Powered down (6-pack is so poor could not keep >=6 volts)	W10	Available	L			20190926
2020	Jun	13		~	17:15			[M1-3 M9] Used for quick DR tests of WP6-WP10 (B57-B61)		W100 Test		W10		20200613
		15	Mo		03:00			[M1-3 M9] Wattmon_10 powered down	WP6-WP10	Available				20200615
2021	Jan	16	Sa					[M1-3 M9] Seen in videos and photos of TurboNet/RHS bench testing	IMG					20210116
	Oct	19	Tu					[M1 M9] On the bench to use for TurboNet MikroTik project (Schauer 2512, Traco DC-DC); [M1] Quick check of calibration using BK, AOK for what I need to do	T48P	Applied	L0	W10		20211019
		24	Su					[M1 M9] Video sent to Pavel via Viber	IMG		L			20211024
	Nov	13	Sa					[M1 M9] Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup					20211113
		14	Su	~	00:13	~	00:22	[M1 M9] Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)					20211114

## M2
Modules: M2	A					C252_2: 25 Amp Dual Channel Current Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	W10	7/17/19
2015	Jul	13					Ordered	EML WCA	On Order				20150713
		15					Received	WCA	Available	L			20150715
		19					Set up for use on Wattmon_1	AED		L0	W1		20150719
		28					Set up for use on Wattmon_2 (to be reinstalled at RW)		Slated for RW		W2		20150728
	Sep	18					Calibrated both loops with BK Precision 9110: zero offsets; 5.000 Amps in 4 loops, best multiplier reads 9.99 Amps (for 0-12.5 A with 2 loops)					9/18/15	20150918
		19					Installed at RW		Applied	L1			20150919
2016	Mar	16					Onsite at RW (to install web relay)	IMG					20160316
	Jun	1					Removed from RW (also removed Wattmon_2)	AED	Calibration	L			20160601
2017	Aug	3	Th					Being used on Wattmon_9 (bench test unit); Intermittent use (not always on)	AED IMG	Applied	L0	W9		20170803
		4	Fr					Calibration as per method used for W7 (see Master Configuration): The biggest correction was in the zero	AED				8/4/17	20170804
		7					WISPer#1 bench testing	IMG					20170807
2018	Feb	25					C252_2 in WISPer#2 test setup		WISPer#2 Testing				20180225
		28	We					Calibration (see Master Configuration); Set up for upward current flow both sensors 0-12.5 Amps (2 loops)	AED	DR Testing (W100)			2/28/18	20180228
	Mar	13					W100 Testing (Trace used as CW load, B1, WP2, Delta 200W, Genasun mounted under fan, C252, BK)	IMG					20180313
		15					W100 Testing (Trace used as CW load, B1, WP2, Delta 200W, Genasun mounted under fan, C252, BK, Heathkit)					20180315
		20	Tu					Calibration (see Master Configuration), very carefully done for doubled loops in 0-15 Amps range (upward current flow), to optimize for WISPOWER#2 testing, to be installed at RW; Photos 'W100 Testing' (WP2, Delta 200W, Genasun mounted under fan, B1, BK, Trace being used as CW load)	AED IMG				3/20/18	20180320
	Apr	2		~	15:15			[M2-3] Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	IMG EML					20180402
	Aug	9	Th					Calibration tweaked for balance at ~26 watts in Genasun float with Charge Efficiency 100% (loop 1 gain increased slightly, see Master Configuration)	AED WRD	W100_2 Testing			8/9/18	20180809
		12	Su	~	06:50			Removed from DR Test Setup (and Wattmon_9), to go to RW and Wattmon_8	WRD	Slated for RW				20180812
		13	Mo					Installed at RW (on W100_2), but Wattmon_8 was brought back to shop for Tshooting	IMG	Available	L1			20180813
2019	Apr	29	Mo		12:05		12:50	Travel & onsite at RW: Battery watered; Checked AC outlet & installed cover plate; Removed the last of the Wattmon stuff; Cleaned W100 fan/filter (compressor); Ant trap installed			L			20190429
	Jun	25	Tu	~	23:15	~	01:15	M1-2; M2 Sheet "20190626 C252_2"	WCX	W100 Test	L0	W10	6/26/19	20190625
		28	Fr					M1-3 M9	IMG AED					20190628
	Jul	8					M1-3 M9	IMG					20190708
		11					Calibration modified Current_2 Invert 0->1	WCX				7/11/19	20190711
		14					M1-3 M9	IMG					20190714
		17	We					Complete calibration with BK_1, Sheet "20190717 C252_2"	WCX				7/17/19	20190717
	Sep	26					M1-3 M9	W10	Available	L			20190926
2020	Jun	13		~	17:15					W100 Test		W10		20200613
		15	Mo		03:00				WP6-WP10	Available				20200615
2021	Jan	16	Sa					IMG					20210116

## M3
Modules: M3	A					I3O2_1: Input and Output Module

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	W10
2015	Jul	27					[M3-4] Ordered	EML WCA	On Order			20150727
		31					[M3-4] Received	WCA	Available	L		20150731
2018	Apr	2		~	15:15			M2-3 / I302_1 shown but not hooked up yet	IMG EML	DR Testing (W100)	L0		20180402
		6	Fr					Attached to Wattmon_9	AED			W9	20180406
2019	Aug	12	Su	~	06:50			Not attached to Wattmon_9, but available for DR Test Setup		Available	L		20190812
2019	Jun	28					M1-3 M9	IMG				20190628
		30	Su					Attached to Wattmon_10 as part of W100 Test setup		W100 Test	L0	W10	20190630
2019	Jul	8					M1-3 M9	IMG				20190708
		14					20190714
2019	Sep	26					W10	Available	L		20190926
2020	Jun	13		~	17:15					W100 Test		W10	20200613
		15	Mo		03:00				WP6-WP10	Available			20200615
2021	Jan	16	Sa					IMG				20210116

## M4
Modules: M4	A					I3O2_2: Input and Output Module

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2015	Jul	27					M3-4	EML WCA	On Order			20150727
		31					WCA	Available	L		20150731
2016	Jun	1					Noticed that connector is missing (maybe somewhere around here, but a quick look around didn't find it)		Missing Connector			20160601
2018	Apr	12					Received interface connector (Akash shipped it at no charge in conjunction with my work on the documentation)		Available			20180412
	Jul	1					Attached to Wattmon_10 but not detected (probably device ID conflict); Busy with other priorities, will get back to this later	AED	Slated for SAPS	L0	W10	20180701
		3					Plans for SAPS changed to eliminate use of this module		Available	L	-	20180703

## M5
Modules: M5	A					C752_1: 75 Amp Dual Channel Current Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2	-	6/24/18
2015	Aug	15					Ordered	EML WCA	On Order				20150815
		24					Received	WCA	Available	L			20150824
2018	Jun	23					Attached to Wattmon_10 and calibrated (see Master Configuration, AED) …	AED	Slated for SAPS	L0	W10		20180623
		24					… Calibration completed		Assembly	MA2		6/24/18	20180624
2019	Jun	25					Wattmon_10 redone and C752_1 is no longer in Devices (but device is yet slated for SAPS)				-		20190625
2020	May	30					[M5 M8 M10] Bench cleaned and parts for assembly boxed with labels “MA2”	MA2					20200530

## M6
Modules: M6	A					C252_3: 25 Amp Dual Channel Current Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-	9/19/15
2015	Sep	11					[M6-7] Ordered	EML WCA	On Order				20150911
		14					[M6-7] Received	WCA	Available	L			20150914
		19					Approximate date of installation at RN (with Wattmon_3); Both loops calibrated onsite with BK Precision; zero offset and 4 loops, 20A = 10A (2 loops will be 0-12.5A); Forgot to double loops	AED	Applied	L2	W3	9/19/15	20150919
				Returned to RN tower to double the current loops, as everything was reading 1/2 the actual current					20150919
2016	Mar	16					Onsite at RN (to install web relay)	IMG					20160316
	Jul	16	Sa		08:08		09:22	Removed from RN	AED	Available	L	-		20160716
2021	Nov	20					Selected for ONWT Remote Monitoring project	DORM	ONWT Prep		W6		20211120
2022	Oct	23					ONWT Remote Monitoring project abandoned		Available		-		20221023

## M7
Modules: M7	A					C252_4: 25 Amp Dual Channel Current Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	W7	6/11/16
2015	Sep	11					M6-7	EML WCA	On Order				20150911
		14					WCA	Available	L			20150914
2016	Jun	1					Calibrated with Wattmon_7	AED		L0	W7	6/1/16	20160601
		11			12:58	>	20:10	On Pasha T450s with Wattmon_7, stabilizing temperatures in laboratory …; Checked calibration … it has deviated a little bit from 6/1/16 Calibration.		Calibrating				20160611
				20:55	~	21:45	Calibrated		Slated for RN			6/11/16	20160611
		12			11:24			Removed from Wattmon_7				-		20160612
				11:40		12:12	Wattmon_8 attached for tests & experiments; Quick calibration checks ("spot-on"); Wattmon_8 removed from calibration bench				W8		20160612
				>	12:16			Wattmon_7 attached; Calibrations checked AOK				W7		20160612
		13		~	01:30		05:55	Observations of calibration accuracy as a function of temperature …; Removed from calibration bench		Install…	L			20160613
	Jul	16	Sa		08:08		09:22	Installed at RN	AED IMG	Sold	L2			20160716
2019	Jan	22	Tu					Onsite at RN; Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)		Available	L			20190122

## M8
Modules: M8	A					I8O8_1: 8-Channel Digital I/O Module with Relay Board and AC Adapter

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2	-
2018	Apr	2					[M8-10] "Ordered": Date when Akash offered to send me this as a "no charge sample" in conjunction with my documentation work	EML WCA	On Order			20180402
		10					[M8-10] Shipped	EML				20180410
		12					[M8-10] Received	WCA	Test …	L0		20180412
		15					[M8-10] Labels; [M8-9] Attached to Wattmon_10; Quick Test; [M8] Questions/Conclusions	AED	Burn In		W10	20180415
				Temporarily disconnected and disabled I8O8_1 on W10 in order to complete "Quick Test" of LCD_1 (but will reattach and enable as soon as possible)		Waiting LCD_1 Test OK			20180415
		19	Th					[M8-10] LCD_1 now functioning as it should; I8O8_1 and A10_1 also functioning; L0W10M8M9M10 "4/15/18-4/20/18 ‘Quick Test’ [sic] of LCD_1 (SD Card Corruption)"		Burn-In			20180419
		20	Fr			~	15:07	[M8-10] Powered off		Slated for SAPS			20180420
	Jun	19					[M8-10] Powered up (configuration for Mini SAPS) …					20180619
		28					Bench testing, power for relay board: Quiescent 0.005 A @ 9.6v (0.05w), 0.009 A @ 13.0v (0.12w), 0.011 A @ 15.3v (0.17w) …					20180628
		29					… Bench testing, power for relay board: All 8 relays energized 0.273 A @ 13.0v (3.5w); Relays will not energize reliably below ~10.7v (will have to place it on PS_3 V6 12.0v); All 8 relays energized 0.242 A @ 12.0v (2.9w)					20180629
				Testing with TEC_1 on Relay 1, worked for a couple of times, then Relay 1 NO contacts blown; Several of these operations using TEC_1 on Relay 2 and Relay 3 OK (assuming infant mortality of Relay 1) / Note that TEC_1/2 coil requires <3 Amps, are diode protected, and relays are rated at 7.5 to 10 Amps; Labeled Relay 1 as "NO Contact Defective"		Assembly	MA2		20180629
2019	Jun	25					Wattmon_10 redone and I8O8_1 is no longer in Devices (but device is yet slated for SAPS)				-	20190625
2020	May	30					M5 M8 M10	MA2				20200530

## M9
Modules: M9	A					A10_1: 10-Channel ADC Module

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon	Calibration
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	W10	6/26/19
2018	Apr	2					M8-10	EML WCA	On Order				20180402
		10					EML					20180410
		12					WCA	Test …	L0			20180412
		15					M8-10; M9 Conclusions	AED	Burn In		W10		20180415
				Temporarily disconnected and disabled A10_1 on W10 in order to complete "Quick Test" of LCD_1 (but will reattach and enable as soon as possible)		Waiting LCD_1 Test OK				20180415
		19	Th					M8-10		Burn-In				20180419
		20	Fr			~	15:07			Slated for SAPS				20180420
	Jun	19					20180619
		26					Calibration …	AED WCX					20180626
		27					… Calibration completed		Assembly	MA2		6/27/18	20180627
2019	Jun	26	We	~	01:30	~	03:30	Attached to Wattmon_10 for use on W100 Project; Calibration of V1 checked with BK_1 …; Sheet "20190626 A10_1" (no changes made)		W100 Test	L0	W10	6/26/19	20190626
		28	Fr					M1-3 M9	IMG					20190628
	Jul	8					M1-3 M9					20190708
		14					20190714
		17					W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, A10, 6-pack (Heathkit)					20190717
	Sep	26					M1-3 M9	W10	Available	L			20190926
2020	Jun	13		~	17:15					W100 Test		W10		20200613
		15	Mo		03:00				WP6-WP10	Available				20200615
2021	Jan	16	Sa					IMG					20210116
	Oct	19	Tu					M1 M9; M9 Quick check of calibration of V1 against Fluke, AOK for what I need to do	T48P	Applied	L0	W10		20211019
		24	Su					M1 M9	IMG		L			20211024
	Nov	13	Sa					20211113
		14	Su	~	00:13	~	00:22					20211114
2022	Aug	20	Sa					Dual Supply Bench Testing Setup Assembled: W10 and A10_1 not needed, removed from bench, boxed on N bench	T48-3			W10		20220820

## M10
Modules: M10	A					LCD_1: LCD Screen 20x4

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2	-
2018	Apr	2					M8-10	EML WCA	On Order			20180402
		10					EML				20180410
		12					WCA	Test …	L0		20180412
		15					M8-10; M10 Attached to Wattmon_10 for "Quick Test" … but it didn't go well: / LCD Module is not being detected in Devices; Tried restoring "As From India" but SD card now corrupted and unreadable (needs to be formatted, but Windows format fails); To/From Akash into 4/16/18 AM ...	AED EML	"Quick Test"		W10	20180415
		19	Th					M8-10		Burn-In			20180419
		20	Fr			~	15:07			Slated for SAPS			20180420
	Jun	19					Assembly	MA2		20180619
2019	Jun	25					Wattmon_10 redone and LCD_1 is no longer in Devices (but device is yet slated for SAPS)				-	20190625
2020	May	30					M5 M8 M10	MA2				20200530

## MA1
MobileApps: MA1	A					HAPS: Honda Auxiliary Power System

Date/Time CST/CDT					Description	Other Sources	Status	Batteries	Charger
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	Deep Cycle	-
2004	Nov	7					HAPS system in Honda Civic Wagon (file transfer dates 11/7/04 to 11/10/04); The Trace was used in the Honda Auxiliary Power System for many years after that (on the floor behind the driver's seat)	IMG	Applied	Deep Cycle	BC1	20041107
2006	Oct	22					Honda showing rooftop mounted battery (file transfer date, 'Kaweah Trip Cellphone Camera')					20061022
		23					Honda showing rooftop mounted battery, in the driveway at 1804 Ptarmigan, 'Klute Last Resort' ('20061023 pictures from AK's camera')					20061023
2007	Jan	26					Honda and HAPS on trip to Mule Auction with Philip Ropp, Tom McConnell and Art Morrill; Of particular interest is the photo of the HAPS plugged in for charging the rooftop battery outside a motel room / Photos shot 1/26/07 and 1/27/07 on AWM Nikon					20070126
2008	Jun	12					Honda in Colorado: In front of motel room at Heritage Inn, Greeley; Behind the Empire Grange, Ft. Collins; Classic by moonlight near midnight, East of Ft. Collins					20080612
		13					Honda on Parkwood Avenue, Ft. Collins, Colorado (previous Klute home)					20080613
		18					Honda in daylight at the same location as 6/12/08 moonlight shots					20080618
		19					Honda in downtown Ft. Collins, Colorado					20080619
		20					Honda and HAPS at 1804 Ptarmigan, Estes Park, Colorado: Refrigerator outside on the ground					20080620
		22					Honda and HAPS in Colorado: Estes Park (1804 Ptarmigan, me, "Ready for church in Greeley") / In front of Grace Reformed Church, Greeley; Trail Ridge Road (interesting details of Honda interior showing full sized computer, LCD monitor, refrigerator and Trace on the right front floor)					20080622
		25					Honda behind The Empire Grange, Ft. Collins, Colorado: HAPS is plugged in					20080625
		29					Honda and HAPS in Colorado: Between Boulder and Lyons; In parking garage at Swedish Medical Center, Englewood					20080629
2008	Jul	4					Classic "me and the Honda RV" in garage at 1804 Ptarmigan, Estes Park, Colorado					20080704
		10					Honda and HAPS in action: "Tailgate dinner at sunset" behind the Empire Grange, Ft. Collins, Colorado					20080710
		15					Honda and HAPS behind the Empire Grange, Ft. Collins, Colorado					20080715
		17					Honda and HAPS parked in front of the Good Shepherd Bible Chapel, Ft. Collins, Colorado					20080717
		21					Honda and HAPS in Estes Park, Colorado					20080721
		23					Honda and HAPS behind the Empire Grange, Ft. Collins, Colorado					20080723
		28					Honda RV in Colorado: Camping and cooking behind the Empire Grange in Ft. Collins; On the road to Nebraska (Eastern plains)					20080728
		29					Honda RV at Winfield's Coffee in North Platte, Nebraska					20080729
		30					the Honda RV joining the other RVs at an RV park in Iowa					20080730
		31					Honda RV parked at Paul Dorr's in Ocheyedan, Iowa					20080731
2008	Aug	2					Honda RV: Parked at Paul Dorr's in Ocheyedan, Iowa; Parked at Zion Evangelical & Reformed Church in Garner, Iowa					20080802
		10					Honda and HAPS parked at Pisgah Baptist Church, Wood Heights, Missouri					20080810
		15					Honda RV at Gene Franklin's house in Hockley, Texas (including shots of children playing in the front seat). (Christine Martin home is next property to the West.)					20080815
		19					Honda RV parked in the driveway of Matthew and Stacy Davis' house in Louisiana					20080819
		27					Honda RV in Virginia: Dominion Truss; Across the street from Martha Washington Inn in Abingdon					20080827
		28					Honda RV in Virginia: Camping in the rain					20080828
2008	Sep	4					Honda parked in front of the house of Steve Murphy, Publisher, Homeshooling Today, Virginia					20080904
		8					Honda RV in Virginia: At a campground owned by Buz and Debbie DuPont, who let me stay there three nights for free; Parked next to The Reformed Bible Church in Central Virginia, Pastor Paul Michael Raymond					20080908
		12					Honda RV at Hawk's Nest, West Virginia					20080912
		13					Honda RV in Urbana, Illinois (where I grew up): Crystal Lake Park; 2103 Cureton Avenue (previous Klute home)					20080913
2009	Sep	12					Honda in Iowa: Aaron Dorr residence, 1623 Rose Avenue, Allendorf; Holiday Inn Express, Sheldon					20090912
		13					Honda in Iowa: At "Obadiah's Meeting Room", Sheldon (Pastor Paul Michael Raymond conference sponsored by Paul Dorr); Starbucks Coffee					20090913
		14					Honda in Nebraska: The Mormon Trail Motel, North Omaha (on 75); Panera Bread; Pastor Phil Kayser's home in Omaha / The Thompson Alumni Center, University of Nebraska (where Phil Kayser's church meets, Dominion Covenant)					20090914
2010	May	25					Honda and HAPS operating as a mobile generator to run the sump pump at 204 W 3rd ST home: Bumper sticker "ARE YOU SURE THERE'S A BOX ON MY ROOF?"					20100525
2010	Jun	1					Honda and HAPS in Colorado (trip with Ben): Trail Ridge Road; Campsite on West Slope (near Winter Park, South of Berthoud Pass)					20100601
		2					Honda and HAPS in Colorado (trip with Ben): Campsite on West Slope (early in the morning); Campsite West side of Loveland Pass					20100602
		4					Honda and HAPS in Colorado (trip with Ben): Elias Motors in Silverthorne; Climax; Cottonwood Pass					20100604
		5					Honda and HAPS in Colorado (trip with Ben): Campsite West of Cottonwood Pass					20100605
		7					Honda and HAPS in Colorado (trip with Ben): West of Gunnison					20100607
		8					Honda and HAPS in Colorado (trip with Ben): North of Ouray, camping on the road (engine overheated and we stopped where we were for the night): North of Ouray, engine cooldown stop / South of Ouray on the way up Red Mountain Pass (engine cooldown stops); Campsite North of Red Mountain Pass					20100608
		9					Honda and HAPS in Colorado (trip with Ben): Red Mountain Pass					20100609
		10					Honda and HAPS in Colorado (trip with Ben): Silverton					20100610
		11					Honda and HAPS in Colorado (trip with Ben): Heading North to Telluride					20100611
		12					Honda and HAPS in Colorado (trip with Ben): Campsite SouthWest of Ouray (on road to Mt Sneffels trailhead) (timelapse photos); Further up the road to Mt Sneffels trailhead; Antlers Motel, Ouray					20100612
		13					Honda and HAPS in Colorado (trip with Ben): Mt Sneffels trailhead					20100613
		14					Honda and HAPS in Colorado (trip with Ben): Peak to Peak Highway South of Estes Park					20100614
		16					Honda and HAPS in Colorado (trip with Ben): Odometer at 250,000.0 miles; Ben at Denver International Airport for flight back to Michigan					20100616
		17					Honda and HAPS in Colorado at Estes Park Medical Center					20100617
		20					Honda and HAPS in Colorado at campsite South of Estes Park where Dad and I met for dinner (timelapse photos)					20100620
		21					Honda and HAPS in Colorado at Brainard Lake and campsite near the road below it					20100621
		22					Honda and HAPS in Ward, Colorado					20100622
		23					Honda and HAPS near Cameron Pass, Colorado					20100623
		24					20100624
		26					Honda and HAPS in Colorado at campsite (trailhead, timelapse)					20100626
		27					Honda and HAPS in Colorado at campsite (trailhead); Another campsite by the road					20100627
		28					Honda and HAPS in Colorado near trailhead to Cameron Peak					20100628
2010	Jul	3					Honda and HAPS in Colorado: Sunrise on the Eastern Plains (on the way home to Missouri); Other shots					20100703
2010	Nov	19					Honda and HAPS in Kansas at Scofield Grave plots, Mount Calvary Cemetery, Atchison					20101119
2011	Sep	30					Honda and HAPS in Colorado: Dad rides in the Honda, probably for the first time; Engel cooler behind driver's seat (first photo of Engel in use, which was purchased 8/29/11); Guanella Pass above Georgetown					20110930
2011	Oct	1					Honda and HAPS in Colorado: Campsite along the road from Ward to Brainard Lake; Engel cooler more clearly shown behind driver's seat					20111001
		4					Honda and HAPS in Colorado: Dad, about 4 miles West up Magnolia Road, which leaves the Boulder Canyon Highway 119 about 3-4 miles West of Canyon Boulevard, Boulder / The engine overheated and we stopped for lunch; Engel cooler					20111004
		5					Honda and HAPS in Colorado: Brainard Lake; Campsite near road below Brainard Lake; Engel just visible					20111005
		7					Honda and HAPS in Colorado: Nederland Happy Trails Bicycle and Coffee Shop; Brainard Lake (later I used these photos in the CraigsList ad to sell the Honda); Campsite below Brainard Lake					20111007
		9					Honda and HAPS in Colorado: Pingree Park; Dirt road over pass returning to Ft. Collins					20111009
		15					Honda and HAPS in Colorado: Lake Eldora ski resort. Engel just barely visible.					20111015
		16					Honda and HAPS in Colorado: 4 miles below 4th of July trailhead at Hessie Trailhead					20111016
		17					Honda and HAPS in Colorado: Dad, Garden of the Gods; Engel behind driver's seat					20111017
		19					Honda and HAPS in Colorado: Diane Montgomery's garage in Ft. Collins (clutch cable broken), shows T400s laptop platform to the right of the driver's seat (and HAPS control switches, red and green)					20111019
		21					Honda and HAPS in Colorado: 4th of July trailhead; Engel behind driver's seat					20111021
2011	Nov	9					Honda and HAPS in Iowa: Pat McGrath dealership, Subaru purchased; Engel behind driver's seat					20111109
		10					Honda and HAPS in Iowa: Pat McGrath dealership, comparisons of Honda and Subaru (Honda was left parked there for several weeks until I returned with a tow dolly)					20111110
		24					Honda and HAPS the day after bringing the Honda home, towed behind the Subaru on the EZE-Tow Dolly					20111124
2011	Dec	24					Honda and HAPS for CraigsList ad: The Honda had 278,000 miles on it, the head gasket leaked, and the Subaru was working fine (Trace removed) / Nice details of the meters and the laptop platform construction, which were sold with the Honda					20111224
2012	Feb	25					Honda and HAPS sold (approximate date, Trace TS_1 not included in sale)		Sold		-	20120225

## MA2
MobileApps: MA2	A					SAPS: Subaru Auxiliary Power System					Batteries	Router	Relay 1	Relay 2	Genasun	Convertor	Shunt 1	Shunt 2	Ammeter 1	Ammeter 2	Voltmeter 1	Voltmeter 2	Panel 1	Thermostat	Inverter	Wattmon	I/O Module	ADC Module	LCD Module	Charger	C752_1

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$4634.81	574.08	Tabled	B8/11	Z2	Z3	Z4	-	V6	Z5	Z6	Z7	Z8	Z9	Z10	P3	-	-	W10	M8	M9	M10	BC1	M5
2011	Nov	9					Honda and HAPS in Iowa: Pat McGrath dealership, Subaru purchased	IMG					20111109
		11					Ordered Hidden Hitch and accessories from Hitchmart.com: / SAPS related part of order is the 7 way female socket/bracket $5.95 + $19.95	EML SSRP	$25.90	1.00	$25.90	1.00					20111111
		24					Subaru towing the Honda on the EZE-Tow Dolly (the day after returning from Iowa)	IMG					20111124
2012	May	13					Removed rear seats (5/13/12 to 5/17/12): I had begun designing the Subaru RV with an improved Auxiliary Power System / Engel cooler had already been purchased; Also spent a day looking at how to mount the batteries on the rear			36.00		37.00	Design					20120513
	?	?					Built a wooden platform for the Engel in the Subaru, right side behind passenger seat / (unknown exactly when, but after removing rear seats and before taking another road trip)			3.00		40.00					2012MM?
2015	Aug	6					Colored diagram "Subaru Aux. Elec. System"	SOW		8.00		48.00	Parts on Order					20150806
		8					Purchased (2) T-105 batteries from BFMS KC + some battery cable connectors ($322.89, 20150808_1/2, 20150808_2/2)	SSRP	$322.89	5.00	$348.79	53.00		B4-5					20150808
		13					Ordered (2) battery boxes from Automation Direct (PSC)	EML SSRP	$262.00	4.00	$610.79	57.00					20150813
		14					Battery boxes received; battery boxes installation: About 3 days with hired help (Sasha or Butch)	IMG		36.00		93.00	Install					20150814
		15					General schematic "Subaru Aux. Elec. System" showing MAIN to AUX path with metering connections, fuses, shunts, latching relays and load distribution bus	SOW		8.00		101.00	Design					20150815
		16					"Devices Descriptions": 2 pages + 4 pages yellow sheets with notes on "Water Tight Conduit & Fittings" and "Wire/Cable Runs"; Ordered CradlePoint MBR95 Wireless Router from eBay ($88.00, CP_2); Ordered 260A latching relays from DigiKey ($136.07, TEC_1 & TEC_2); Ordered 4 position plug assemblies for latching relays from Mouser ($9.69); Ordered 10 gang fuse block from eBay ($20.99); Ordered (3) Stinger 250A fuses from Amazon.com ($21.77); Ordered Stinger 4 gauge wire, grommets and fuse holders from Amazon.com ($158.03); Ordered (2) 250A 50MV shunts from eBay ($40.00, later returned); Ordered long terminal bus bars (Red and Black) from SPS ($40.02); Ordered Leviton power inlet receptacle from Amazon.com ($47.49); Ordered Genasun_3 from altE Store ($111.53); Ordered "Car Charger for MBR95" from Super Power Supply ($6.39, SPS_1, hoping to use for CradlePoint router)	SOW EML SSRP MOU	$679.98	16.00	$1290.77	117.00	Parts on Order		Z2	Z3	Z4	C4	V5					20150816
		19					Latching relays, connectors and Stinger fuses, wire, grommets and fuse holders rec'd; SPS Terminal Bus Bars rec'd; Ordered Murata Shunts and Digital Panel Meters from Mouser ($296.99, MS_1, MS_2, MA_1, MA_2, MV_1, MV_2); Ordered Hook & Loop tape (Velcro) for flexible solar panel on hood of Subaru, from R.S. Hughes ($70.55); Ordered flexible solar panel from AFP Power ($212.99, P_3)	EML SSRP MOU	$580.53	11.50	$1871.30	128.50					Z5	Z6	Z7	Z8	Z9	Z10	P3					20150819
		20					Rec'd CradlePoint router; Rec'd shunts and returned (no return shipping cost); Rec'd flexible solar panel; Rec'd SPS_1 "Car Charger for MBR95", not happy, not suitable for CradlePoint router, complained, $6.39 credit rec'd (no return necessary, SPS_1)	EML SSRP	-$6.39	5.00	$1864.91	133.50					-					20150820
		21					10 gang fuse block rec'd; Leviton power inlet receptacle rec'd	SSRP		2.00		135.50					20150821
		22					Murata shunts and meters rec'd			1.00		136.50					20150822
		23					Rec'd Genasun_3 from altE store			1.00		137.50					20150823
		24					Ordered 10x8x6 Equipment Box (with clear door) and 5x3x2 box for shunt/fuse near MAIN battery, from Automation Direct	EML SSRP	$134.00	4.00	$1998.91	141.50					20150824
		25					Colored diagram "Subaru Aux. Elec. Syst. (SAPS), Physical Locations (Devices/boxes), Wire Routing"; Rec'd Hook & Loop tape from R.S. Hughes (Velcro)	SOW SSRP		7.00		148.50	Assembly/Orders					20150825
		26					Schematic snippets of MAIN (Subaru) and AUX battery connections; Boxes ordered 8/24/15 rec'd from Automation Direct			4.00		152.50					20150826
		27					Purchases at Scotts Bargain Barn ($128.82, probably mostly wire); Purchases at WalMart (silicon, fuses, flex wrap)	SSRP	$158.79	4.00	$2157.70	156.50					20150827
		28					Juliya, Mark Hall & Red Porsche (SAPS parts in background on bench); Rec'd refund for shunts returned 8/20/15; Ordered (2) short red bus bars from Colorado Solar ($36.62)	IMG EML SSRP	-$3.38	3.00	$2154.32	159.50					20150828
		30					Ordered Battery Temperature Sensor (BTS) supposedly for Trace, from EcoVantage ($45.08, later returned); Ordered 12v DC/DC buck/boost converter from PowerStream ($95.15, PS_3)	EML SSRP	$140.23	6.00	$2294.55	165.50					V6					20150830
		31					Ordered miscellaneous parts from DigiKey: / Small relays, LEDs, small box for dashboard, switches ($254.40)	EML SSRP DKE	$254.40	5.00	$2548.95	170.50					20150831
2015	Sep	1					Purchases at Scotts Bargain Barn (probably mostly wire, $71.05); Purchased water tight conduit and fittings from Stanion Wholesale Electric Company ($216.60); Purchased wire and electrical parts from Lowe's ($450.09)	SSRP EML	$737.74	12.00	$3286.69	182.50					20150901
		2					Rec'd short red bus bars from Colorado Solar; Rec'd BTS from EcoVantage; Rec'd misc. parts from DigiKey; Purchased (3) watertight 6x6x4 junction boxes from Lowe's ($38.20, Lacey pickup); Purchased Southwire 9-piece Knockout Punch Set from Lowe's ($269.17)		$307.37	8.00	$3594.06	190.50					20150902
		4					Ordered (6) Marine Grade Cigarette Lighter Sockets from Amazon.com ($40.38); Rec'd 12v DC/DC converter from PowerStream	EML SSRP	$40.38	5.00	$3634.44	195.50					20150904
		8					Ordered Dremel mandrels and wheels from Amazon.com ($78.99); Ordered Dwyer PLVT1 Thermostat from Amazon.com ($38.89, DI_1); Ordered 24vac inverter from PowerStream ($106.15, PS_4)		$224.03	6.00	$3858.47	201.50					Z11	I1					20150908
		10					Rec'd Cigarette Lighter Sockets from Amazon.com; Rec'd Dwyer Thermostat from Amazon.com	SSRP		2.00		203.50					20150910
		14					Big Bob's Flooring, KC, black carpet ordered for finishing out the Subaru rear area ($213.04); TearDrop Camper purchase, Nebraska (Subaru and SAPS boxes shown undamaged)	SSRP IMG	$213.04	6.00	$4071.51	209.50					20150914
		15					Rec'd Dremel mandrels and wheels from Amazon.com	SSRP		1.00		210.50					20150915
		16					Rayville Tower visits, Juliya (Subaru and SAPS boxes, Shasha iphone)	IMG				210.50					20150916
		18					RMA EcoVantage (ordered 8/30/15), BTS returned ($2.94 USPS); Rec'd 24vac inverter from PowerStream	EML SSRP	$2.94	3.00	$4074.45	213.50					20150918
		21					Ordered replacement battery box from Automation Direct (one of them was damaged by TearDrop trailer, $131)		$131.00	2.00	$4205.45	215.50					20150921
		22					Ordered new Dremel from Lowe's (needed for rear bumper work, $129.70)		$129.70	2.00	$4335.15	217.50	Assembly					20150922
		23					Picked up black carpet from Big Bob's Flooring (ordered 9/14/15); Picked up Dremel from Lowe's; Rec'd replacement battery box from Automation Direct (damaged one because "First Aid" box in hallway, 4 hrs to replace with hired help)	SSRP		10.00		227.50					20150923
		24					Returns and purchases from Scott's Bargain Barn ($18.70); More purchases from Scott's Bargain Barn ($51.53)		$70.23	6.00	$4405.38	233.50					20150924
		25					Refund rec'd from EcoVantage for BTS (ordered 8/30/15, RMA 9/18/15, -$45.08); 1/2" steel rod stock purchased at Lowe's ($15.15)	EML SSRP	-$29.93	5.00	$4375.45	238.50					20150925
		26					Purchased aluminum flat bar from Metal by the Foot in KC (for reinforcing battery boxes, $43.17)	SSRP	$43.17	8.00	$4418.62	246.50					20150926
2015	Oct	2					Purchased metal for skid plates under battery boxes, Scott's Bargain Barn ($56.94); Purchased torch gas at Westlake Ace Hardware ($15.20)		$72.14	12.00	$4490.76	258.50					20151002
		5					Subaru with undamaged battery boxes and TearDrop camper, crossing Kansas with Juliya (especially classic sunset photo near Wilson, KS on I-70 W)	IMG					Project Tabled (Incomplete)					20151005
		23					Wilcox Residence, Loveland, CO: Subaru, Engel plugged in					20151023
		31					TearDrop Camping, Fourth of July Campground and Trailhead: Subaru and undamaged SAPS box					20151031
2015	Nov	1					TearDrop Camping, behind Jamoka Joe's, Loveland: Subaru and SAPS box					20151101
		7					Alamosa, Juliya: Subaru and TearDrop					20151107
		30					(2) T-105s purchased for SAPS installed at RW (-$288)	SSRP	-$288.00		$4202.76			(none chosen yet)					20151130
2016	Feb	12					Photos: Sunset from the porch showing Subaru with damaged spoiler, PWSD #2 tower and jet trails in the sky	IMG					20160212
	Jun	16					Subaru with battery boxes (completely installed, not damaged yet): At RW (L1); Flexible solar panel that was bought for SAPS 8/19/15 installed at RW, but we are yet planning to bring it back for the SAPS					20160616
	Dec	22					Subaru with battery boxes (completely installed, not damaged yet): photos at RW (L1)					20161222
2017	Jul	20					Subaru with battery boxes (left side box is damaged): Rayville corner store and shop East side lawn, EZ-Tow Dolly					20170720
	Sep	6					Subaru with battery boxes (left side box is damaged): Richmond City Water Tower (L3, RCWT)					20170906
		24					TearDrop sold: Buyers in front of shop, Subaru parked to the East (damaged battery box)					20170924
	Oct	31					Preparing to go camping (which I later chose to abort): Subaru in garage (damaged SAPS battery box) and stuff to load on the garage bench					20171031
2018	Feb	17					4 pages: "SAPS, Feb. 2018" schematic snippets and thoughts on shunt locations; "SAPS, Marketing - (2) magnetic signs" / "SAPS, Cash Flow" (sell the Porsche); "SAPS" shunts and dashboard I & V meters	SOW		8.00		266.50	Redesign					20180217
		19					Further notes on dashboard I meters and shunts; TODO "Describe in general the desired features"			6.00		272.50					20180219
		20					"SAPS - simplification Ideas" notes and schematics snippets; "SAPS - Wattmon purposes" notes			6.00		278.50					20180220
		25					Genasun_3 removed from this project for use on W100_1 (WP2), removed $111.53 paid 8/16/15	SSRP	-$111.53		$4091.23					-					20180225
		27					"SAPS Main/Aux - How best to do this? Wattmon"	SOW		6.00		284.50					20180227
2018	Mar	7					"SAPS [observations from] Fully charged 27TMX" with notes/thoughts on MAIN/AUX contactor algorithm			6.00		290.50					20180307
		9					"Dashboard Meter Switch - 3 position? - NO!" with schematic snippet and "We must have meter disable switch" / Schematic "Dashboard Metering"; "WISPOWER #2 & SAPS, How did I manage to read 190 W with +- 12.5 Amp Current loop ?" / (answer, the C252s are pretty good in +- 50 Amp range)			8.00		298.50					20180309
		10					Printout of TE Connectivity data sheet on BDS-A latching relays with notes, TODO and schematic snippet			6.00		304.50					20180310
		20					New info. In Library concerning relay outputs on Wattmon Pro, i3O2, Mega, i8O8	LIB		2.00		306.50	Project Tabled					20180320
2018	Apr	2					"Ordered" Wattmon_10 ($81.50), I808_1 ($23.50), A10_1 ($21.50) and LCD_1 ($23.50): Akash agreed to send these to me in conjunction with documentation work, but all of them are slated for SAPS (costs are his customs declaration amount)	EML SSRP	$150.00		$4241.23	306.50					W10	M8	M9	M10			20180402
		12					Rec'd Wattmon stuff	SSRP		2.00		308.50					20180412
		20					Initial labelling and testing of Wattmon stuff completed (7 days at about 5 hrs/day)			35.00		343.50					20180420
2018	May	22					Photos: "2008 Subaru OBD-II +" showing connector and instrument panel (problems with Cruise Control, TPMS and "Check Engine"); Downloaded FreeSSM; Ordered OBD-II adapter (VC_1, Z12) / Improvements to this workbook (Summary sheet MobileApps and etc.)	IMG EML SSRP	$19.88	8.25	$4261.11	351.75					20180522
		23			07:15		08:00	Improvements to this workbook			0.75		352.50					20180523
		24			22:45		01:25	Improvements to this workbook (Summary sheet Miscellaneous and etc.)			2.67		355.17					20180524
		26			09:30		10:00	VagCom OBD-II Adapter rec'd yesterday (VC_1, Z12): Inventory stickers applied	SSRP		0.50		355.67					20180526
		29					Adapter used to successfully "fix" Cruise Control by Clear Memory					355.67					20180529
		30	We					Adapter semi-permanently installed in Subaru (will explore possibilities for SAPS)			0.50		356.17					20180530
2018	Jun	9	Sa					White sheet "Mini SAPS"; Hunted down parts and began looking at where to put things in Subaru	SOW WS		2.00		358.17	Mini SAPS Assembly					20180609
		11	Mo	~	04:00	~	05:00	(2) T-105s installed in Subaru, Right Rear foot well ($288, 20160421_1/4 and 20160421_4/4)	SSRP	$288.00	1.00	$4549.11	359.17	Assembly	B8/11					20180611
				~	06:20	~	06:50	Trace "fit tested" on board above batteries (in front of space for Engel, ~$78 in ~2004)		$78.00	0.50	$4627.11	359.67					BC1		20180611
				~	07:00	~	07:15	White sheet "Mini SAPS" showing Bus Bars (4), C252 loops and connections to battery	SOW WS		0.25		359.92					20180611
				~	08:00	~	08:40	Started to prepare equipment box that goes in Left Rear foot well (~2" hole) …			0.67		360.58					20180611
		15	Fr	~	03:45	~	06:15	Downloaded and studied specs on PS_3 (V6); Bench test of PS_3 …			2.50		363.08					20180615
				~	17:45	~	18:00	Bench test of PS_3 (V6): CradlePoint 4w @ startup, 3w continuous			0.25		363.33					20180615
		19	Tu	~	06:00	~	07:15	Attempted to setup my.wattmon.com for Wattmon_10 but "Device does not exist" (AED) / To Akash "Portals: new MAC addresses please" …	AED EML		1.25		364.58					20180619
				~	07:45	~	09:15	From Akash “Re: Portals: new MAC addresses please” (must 1st get it exporting to portal) / Wattmon_10 powered up and configured; Now logging on my.wattmon.com			1.50		366.08					20180619
		20	We	~	02:00	~	03:45	Attempted to setup ems.wattmon.com for Wattmon_10 but errors; To Akash "Re: Portals: new MAC addresses please" and “Problem setting up ems.wattmon.com for MEGA” …; [05:19 response from Akash "Set the custom data export URL to ems.wattmon.com/data/setdatacsv or if you are using my.wattmon then my.wattmon.com/data/setdatacsv"] ...			1.75		367.83					20180620
				~	04:00	~	09:30	CradlePoint history sheet started (and summaries for Miscellaneous Equipment purchased for SAPS) ... / Found discarded wall worts with appropriate plug to power (2) BlacX …			5.50		373.33					20180620
		21	Th	~	01:45	~	11:30	… Miscellaneous Equipment Summary and History Sheets, equipment purchased for SAPS (paper file done through 8/19/15) …	SSRP		9.75		383.08					20180621
				~	22:30	~	06:45	… finished filling out this history sheet including Miscellaneous Equipment histories			8.25		391.33					20180621
		22	Fr	~	14:55	~	17:15	… setup ems.wattmon.com: Wattmon_10 Custom Export URL ems.wattmon.com/data/setdatacsv (now Actively exporting but spurious errors in System log); To Akash “MEGA now exporting to ems ... but weird errors for ip.cgi and portal data” …	AED EML		2.33		393.67					20180622
				~	18:00	~	18:30	… exports are caught up, and now new type of ip.cgi system log entry (To Akash, AED) ...			0.50		394.17					20180622
		23	Sa	~	03:00	~	04:00	… ip.cgi and ip_export_custom.cgi from Akash uploaded to Wattmon_10 but export errors continue (To Akash, AED) / From Akash (he'll check it remotely) …			1.00		395.17					20180623
				~	04:00	~	06:30	(2) cords for (2) BlacX prepared from discarded wall worts; Bench test for PS_3 DC/DC converter concluded; To Akash "DIN rail type for mounting MEGA, I808, A10"; Trace rewired (TS_1) …; To Akash "S5 5-Channel Shunt Module"; From Akash "we don't have the S5 anymore"; To Akash "do you have the A5S1 or the C1002?"; From Akash "No A5S1, but do have C1002"	EML		2.50		397.67					20180623
				~	06:30	~	06:45	… 06:08 From Akash (he logged in and fixed the ems export issue by modifying ip_export_custom.cgi)			0.25		397.92					20180623
				~	06:45	~	16:00	… Trace rewired with longer #4 battery connections (TS_1); 2x4s cut and installed to prop Engel board above battery tops / C752_1 ($107.18 8/16/15) attached to Wattmon_10 and calibration started …	SSRP AED	$107.18	9.25	$4734.29	407.17					M5	20180623
		24	Su	~	00:30	~	01:30	… C752_1 Calibration …	AED		1.00		408.17					20180624
				~	17:30	~	00:30	… C752_1 Calibration completed; Wattmon_10 roles renamed for C752_1; Setup to calibrate Wattmon_10 VIN/A1 and A10_1 …			7.00		415.17					20180624
		25	Mo	~	08:00	~	11:15	… Wattmon_10 VIN/A1 calibration completed			3.25		418.42					20180625
		26	Tu	~	05:00	~	13:30	Wattmon_10 SD card copy; Configuration; A10 Calibration …			8.50		426.92					20180626
				23:20	~	03:50	… A10 Calibration completed			4.50		431.42					20180626
		27	We		03:50		05:55	Emails and WhatsApp with Akash concerning "DIN rail type …"; Ordered DIN Rail from SkyCraftSurplus.com ($8.75) / Design choices, TODO and hunted up parts from SAPS box	EML SSRP	$8.75	2.08	$4743.04	433.50					20180627
				15:00		17:50	Schematic "SAPS Power Components"; TODO	SOW		2.83		436.33					20180627
		28	Th		03:15		08:30	Improvements to "SAPS Power Components" schematic; TODO; I8O8_1 testing … "FireFox prompts to download System Log" / FW downgraded; To Akash ...	SOW AED EML		5.25		441.58					20180628
				15:50		17:00	W10 SD Card Copy; Corrected uphp.ini; Problem with FireFox is gone!; FW upgraded; No problem with FireFox and .txt files / To Akash	AED EML		1.17		442.75					20180628
		29	Fr		03:00		06:45	From/To Akash; … I8O8_1 and TEC_1/2 testing …			3.75		446.50					20180629
				19:00		00:30	Rec'd DIN Rail from SkyCraftSurplus.com; I8O8_1 and TEC_1/2 preparation and testing / Improvements to "SAPS Power Components" schematic; Another 12vdc jack prepared for I8O8_1 relay board / Marked all (4) 12vdc jacks with red zip tie on positive; PS_4 and DI_1 test; TODO	SSRP SOW		5.50		452.00					20180629
		30	Sa	~	06:45		11:35	TODO, refined "Essential Features"			4.83		456.83					20180630
2018	Jul	1	Su	~	00:00	~	04:30	24vac inverter (PS_4) and thermostat (DI_1) removed from this project (but Cost remains, as they were bought specifically for SAPS); W10 is rebooting itself very 4-8 mins (emails with Akash, tshooting) ... / I302_2 attached to Wattmon_10 but Not Detected ...	SSRP AED		4.50		461.33					-	-					20180701
				~	16:30	~	17:15	… Frequent Reboots tshooting …	AED		0.75		462.08					20180701
		2	Mo	~	04:00	~	06:00	… Frequent Reboots tshooting …; Research, OW Tsensors bus bars (need $ to order)			2.00		464.08					20180702
				~	06:45	~	07:00	… Frequent Reboots tshooting …			0.25		464.33					20180702
				~	10:15	~	10:45				0.50		464.83					20180702
		3	Tu	~	01:30	~	03:40	… Frequent Reboots tshooting concluded; "SAPS Power Components" schematic modifications (to eliminate I3O2): / TODO and Essential Features	AED SOW		2.17		467.00					20180703
		4	We	~	05:45	~	09:00	Wattmon Connections List; "SAPS Power Components" schematic additions; Equipment box assembly …	SOW		3.25		470.25					20180704
		5	Th	~	05:00	~	09:00	Chassis GND will be used (NO connection to Negative Post of MAIN battery), "SAPS Power Components" schematic modified / Physical Layout of Equipment Box …			4.00		474.25					20180705
		6	Fr	~	03:00	~	11:00	Physical Layout of Equipment Box (mock up complete, see photos)	IMG		8.00		482.25					20180706
		7	Sa	~	03:15	~	14:00	Equipment Box Assembly			10.75		493.00					20180707
		8	Su	~	01:45	~	13:00	Equipment Box Assembly; Tested 12v electromechanical buzzer for SAPS dashboard: / 40-80 mA @ 9 to 16 vdc (can be driven from DO1-DO4 which are 500 mA capable) / Improvements to relay outputs configuration (working on possibility of using DO for powering Wattmon, test setup on bench)	SOW		11.25		504.25					20180708
		9	Mo	~	01:30		06:30	Researched Open Collector outputs; Tested 12v buzzer on DO1; Redesigned Wattmon power circuit, see schematic "SAPS - Wattmon Power"; Changes to "SAPS Power Components" schematic and Wattmon connections list			5.00		509.25					20180709
		10	Tu	~	02:30	~	07:00	Minor change to schematic "SAPS - Wattmon Power" (E.Box switch on interior) / TODO, Essential Features and Wattmon Connections List changes; Explored how to modify LCD for backlight control / Emails and WhatsApp with Akash; Photo of Equipment Box; "SAPS LCD Backlight"; TODO	SOW IMG EML		4.50		513.75					20180710
		11	We	~	03:45		07:00	Notes on "How to control LCD_1 display power" (for when I assemble the dashboard box) / Schematic "SAPS Dashboard Display Power"	SOW		3.25		517.00					20180711
		12	Th	~	02:00		05:00	Redo, use DIs for (6) items on A10, DIs for dashboard "Menu/Exit/+/-", Wattmon Connections List and "SAPS Power Components" schematic modified; 2A relay PCB layout …			3.00		520.00					20180712
		13	Fr	~	02:00		05:15	Wire colors for Power Components (see updated schematic); 2A relay PCB layout …			3.25		523.25					20180713
		14	Sa		02:15		05:00	2A Relay Board: Researched Dashboard Fuse/Connector Array …			2.75		526.00					20180714
2018	Jul	15	Su	~	01:30	~	04:30	2A Relay Board: Researched Dashboard Fuse/Connector Array (will go with ATC fuse panel I already have for Loads, and make a pico fuse PCB strip for the dashboard); Looked for diodes, found old RS Digital Meter (RSDM), found old T Monitor (1995) and charged battery to test it (sidetracked, diodes not found yet)			3.00		529.00					20180715
		16	Mo	~	02:00	~	04:00	RSDM: Research (pdfs to library)	LIB		2.00		531.00					20180716
				~	23:45	~	00:00	RSDM: Essential Features			0.25		531.25					20180716
		17	Tu	~	03:15		04:30	RSDM: Essential Features; Searched for 14 pin header w/ribbon cable … found one			1.25		532.50					20180717
		19	Th	~	03:00		04:30	RSDM: Tested backlight (225 mA at 5.00v); Added Ra and Rb resistors to PCB			1.50		534.00					20180719
				~	06:00	~	06:45	RSDM: Tested with BK (5v Vdd) and Heathkit (INHI, 0-20vdc), no matter how I adjust Vr pot it doesn't read right (reads very low), but then suddenly started working (Heathkit 10v, display 1048, not very adjustable)			0.75		534.75					20180719
		20	Fr	~	00:00	~	06:45	RSDM: Replaced Vr with 2 Kohm 10-turn, now adjustable and stable / TODO and Essential Features updated; Planned out physical locations for RS Meter, switches and 2A Relay PCB; (-1hr)			5.75		540.50					20180720
		21	Sa	~	01:00	~	04:30	RSDM: Rough plan location and mounting of meter, switches (3) and 2A Relay/7805 PCB (rough sketch "E. Box Control Assembly" physical); Found switch for RSDM (AUX/OFF/MAIN); Found 7805s; Schematic "RS Digital Meter"	SOW		3.50		544.00					20180721
		22	Su	~	00:00	~	06:30	(2) Rough sketches of schematic "E. Box Control Assembly" showing PCB, switches, RSDM and GND post / Found diodes and 2A Pico fuse; Added 3 switches to design (V6 disable, TEC_1/2) / Modifications to sketch "E. Box Control Assembly" (physical length 5.25" long, GND post)			6.50		550.50					20180722
2018	Sep	13	Th					Reviewed schematic "E. Box Control Assembly"			0.50		551.00					20180913
		14	Fr					Improved schematic "E. Box Control Assembly"			0.50		551.50					20180914
		20	Th	~	03:00		06:00				3.00		554.50					20180920
		21	Fr	~	07:30	~	08:00	Decided to simplify E. Box Control Assembly by deleting SW4-SW6 (V6 disable, MAIN/AUX & MAJOR LOADS) and reducing it to one 7805 for RSDM power, RSDM backlight and PLCD (dashboard)			0.50		555.00					20180921
		24	Mo	~	02:00	~	04:30	Reviewed and corrected Wattmon Connections List and Essential Features: I8O8 DI2/3/4/5 for detection of TEC_1/2 manual assertion moved to A10 (for 2=Max mode detection); I8O8 DI6 moved to I8O8 DI2 (Major Loads detection); DI2/3/4 for dashboard Wattmon control moved to A10 (for 2=Max mode detection); Schematics corrected/annotated for these changes			2.50		557.50					20180924
				~	04:30	~	07:00	E. Box Control Assembly schematic redo to eliminate SW4-6 and 7805 #2; Shared with Gem and Pasha			2.50		560.00					20180924
		25	Tu					E. Box Control Assembly PCB Routing, drawn and shared with Gem and Pasha	SOW VIB		3.00		563.00					20180925
		27	Th	~	04:00	~	04:45	E. Box Control Assembly Bracket: Copied July version, shared w/Pasha & Gem, began thinking about it			0.75		563.75					20180927
		29	Sa	~	03:15	~	06:00	E. Box Control Assembly Bracket: Re-placed PCB mounting hole (to fit 1.5" Aluminum, redo on PCB routing diagram) / 2x dimensional drawing ...	SOW		2.75		566.50					20180929
				Main shop video, 360 degree pan to the music "Here I am Baby" (while working on the SAPS)	IMG					20180929
		30	Su	~	03:15	~	04:50	E. Box Control Assembly Bracket: 2x dimensional drawing (top view); DigiKey Shopping Cart for switch needed	SOW		1.58		568.08					20180930
2018	Oct	1	Mo	~	08:15	~	10:15	Shrink tubing inventoried / Ordered switch and shrink (DigiKey)	EML SSRP DKE	$39.31	2.00	$4782.35	570.08					20181001
		3	We					DigiKey order rec'd: Bonus, they sent 2 switches although I ordered only 1	SSRP DKE		0.25		570.33					20181003
		?					Other priorities took me away from this project, at some point in Oct 2018 I stopped working on it					Tabled					201810?
2019	Mar	15	Fr	~	08:00			System as is (20160421_1/4 and 20160421_4/4, TS_1) used during trip to Iowa, no charging, Engel cooler, laptop and phone charging					20190315
		17	Su			~	22:30	Returned and batteries charged again					20190317
		19					Subaru Bumper Stickers THE STATE IS NOT GOD, DEFYTYRANTS.COM, in garage, SAPS	IMG					20190319
	Apr	9					Security Camera, Main Shop Test, Dancing to the music of "Don't Worry Be Happy", SAPS main equipment box shown on bench					20190409
	Jul	8					SAPS main equipment box shown in background on N bench					20190708
		9					Odessa South Water Tower, Subaru and SAPS					20190709
	Aug	23					Subaru onsite at DF in Excelsior Springs, David Fuller Home Solar					20190823
	Sep	5	Th	~	10:00	~	12:30	T-105s installed in W100 Test Setup	WP5					20190905
2020	Jan	14					Garage: Subaru Gasoline Tank Repair (shows left side battery box damage, right side OK)	IMG					20200114
	May	10	Su	~	14:00	~	14:45	Cleaned, Watered and Reinstalled T-105s from the W100 Test Setup	WP5		0.75		571.08		B8/11					20200510
		23	Sa	~	11:30			Reinstalled Trace (from the W100 Test Setup)	WP5					BC1		20200523
		30	Sa	~	01:15	~	03:30	Bench cleaned and parts for assembly boxed with labels “MA2” / (P3 is in the garage, W10/M9 are on the bench with the DR test setup)	WP6-WP10		2.25		573.33			Z2	Z3	Z4		V6	Z5	Z6	Z7	Z8	Z9	Z10					M8		M10		M5	20200530
2021	Oct	1	Fr					Returned extra liquid tight connectors to Stanion Wholesale Electric (no restocking fee) / Minimal labor (same trip as purchase T-105s from EBC KS)	SSRP	-$147.54	0.25	$4634.81	573.58					20211001
		4	Mo					Reboxed all parts/pieces for project; All together on shelf in W storage (lots of extras that won't be needed for project)			0.50		574.08					20211004
2022	Jul	3					Shop and Subaru at CO Trip Departure; [mini-SAPS in use during entire trip]	IMG					20220703
		18					Returned from CO Trip (very early AM)					20220718
	Sep	15					Subaru in parking lot: Kansas City, Metal By The Foot (MBTF)	IMG					20220915

## O1
OneWires: O1	A					T_1: DS18B20 (?) Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				OK, Harness	L	-
2015	Jul	13					Ordered (but I'm not too sure about this, this is the most probable order date, Akash probably gave it to me as a free sample on this order)	EML WCA	On Order			20150713
		15					Received; Battery lug type	WCA	Available			20150715
2018	Apr	22	Su					Installed on Wattmon_9	AED	DR Testing	L	W9	20180422
	Aug	12	Su					Just being used to record lab temperature on Wattmon_9		Applied			20180812
2019	May	8	We		13:46			Applied to monitor temperature inside my desiccant regeneration oven (Dad's old camp box, having returned from RW where it was used as a battery box) / Desired temperature 118.3⁰C, and the DS18B20 sensors should read to 125⁰C					20190508
	Jun	4					Monitoring NiCad temperature during charge	S2 IMG				20190604
		16	Su	~	10:10	~	20:30	Monitoring NiCad temperature during charge; Action to end charging when T>30⁰C	S2				20190616
		17	Mo	~	01:35	~	09:55					20190617
		28	Fr					W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG				20190628
2021	Dec	13					Two quick tests at shop ambient	DRD	OK, Harness	L0	W10	20211213
				Removed			L	-	20211213
				[O1-11] CONCLUSION for this day "I have a lot of bad sensors and they all need to be tested individually"; See white sheet drawing "W10 Sensor Rack", assembled, T-Sensor Rack	DRD IMG WS				20211213
2023	Jan	20	Fr					[O1-18] Cleaned the bench and put all the OneWire T sensors, sensor rack and assembled harnesses in a box (while finishing description linking as part of T48-4) / I've pretty much abandoned the use of these sensors on the Wattmons, although there are a couple that are probably OK if needed (O1 and O2, not tested at all temperatures) / There are better ways to get temperature logging with multiple sensors, I just need the time and money to buy a better system (probably not Wattmon based) (TODO DRD Temperature Control PID Su3/6/22)	T48-4 / W10				20230120

## O2
OneWires: O2	A					T_2: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				OK, Harness	L	-
2015	Jul	27					[O2-5] Ordered (but I'm not too sure about this, this is the most probable order date)	EML WCA	On Order			20150727
		31					[O2-5] Received	WCA	Available	L		20150731
2018	Apr	24	Tu					Epoxied into battery lug	Slated for RW		L0		20180424
		25	We					Soldered it up with resistor; Attached to W8	AED			W8	20180425
		26	Th					Installed at RW		Applied	L1		20180426
	Aug	13					Onsite at RW: Removed Wattmon_8 but left T sensor	IMG	Available		-	20180813
2019	Apr	29	Mo					Onsite at RW: Removed the last of the Wattmon stuff including T_2	TW2-3		L		20190429
2021	Dec	13	Mo					Quick test at shop ambient	DRD	OK, Harness	L0	W10	20211213
				Removed			L	-	20211213
				O1-11	DRD IMG WS				20211213
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O3
OneWires: O3	A					T_3: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Jul	27					O2-5	EML WCA	On Order			20150727
		31					WCA	Available	L		20150731
2021	Dec	13	Mo					Quick test, alone, shop ambient: Not detected in scan	DRD	Bad?	L0	W10	20211213
				Removed				-	20211213
				O1-11; (O3 mounted but not tested yet)	DRD IMG WS				20211213
		14	Tu					Tested on T-Sensor Rack (alone, at or above shop ambient): Not detected in scan	DRD IMG	BAD		W10	20211214
				Removed; Labeled as "Bad"	DRD		L	-	20211214
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O4
OneWires: O4	A					T_4: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Jul	27					O2-5	EML WCA	On Order			20150727
		31					WCA	Available	L		20150731
2021	Dec	13	Mo					Tested by itself for several hours at shop ambient	DRD	OK	L0	W10	20211213
				O1-11	DRD IMG WS			-	20211213
		14	Tu	~	15:48	~	16:38	Tested by itself on Sensor Rack at shop ambient (~22-20⁰C)	DRD			W10	20211214
				Removed				-	20211214
				~	19:41	~	23:51	Tested by itself at shop ambient on Sensor Rack (~21⁰C): Then added O5, O7, O8 and O11 (at or above shop ambient); Isolated one time data errors ... / [O4-5 O7-8 O11] Sensors placed in meaningful spots for Engel Battery Enclosure (O4,O5,O7,O8 in Engel set 25⁰C, O11 above bench)	DRD SSC IMG	OK?		W10	20211214
		15	We	~	11:35			[O4-5 O7-8 O11] All (5) sensors on the Sensor Rack are functioning but are MIN logging isolated one time data errors (at or above shop ambient); Changed the polling intervals from 300ms to 6000ms (6s)	DRD SSC				20211215
				[O4-5 O7-8 O11] Except for one-time data errors the sensors were OK through the night: O4,O5,O7,O8 in Engel set 25⁰C (reading ~24⁰C); O11 above bench (started reading ~23⁰C, then dropping when shop heat turned off)	DRD				20211215
		16	Th	~	04:30			[O4-5 O7-8 O11] Shop heat ON: O11 low ~19.5⁰C, rising quickly as shop ambient rises (O4,O5,O7,O8 in Engel continue to read ~24⁰C)					20211216
				~	06:42			[O4-5 O7-8 O11] 20211216 064221 Screenshot.jpg [analyzed and annotated Mo2/28/22]; The (5) sensors on the Sensor Rack continue functioning at or above shop ambient with one time data errors / Polling interval 6000ms may have helped but I can't say it completely removed the data spike problems	DRD SSC				20211216
				~	08:32			[O4-5 O7-8 O11] Dinico set -15⁰C	DRD				20211216
				~	09:00	~	09:07	[O4-5 O7-8 O11] Many zeroes and data errors started when the sensors inside the Engel cooled down to ~5⁰C; Dinico set +5⁰C to stay at this temperature for further observations					20211216
				~	09:07	~	11:50	[O4-5 O7-8 O11] Sensors are reading correctly most of the time but with cyclic patterns of zeroes					20211216
				~	11:50	~	13:52	[O4-5 O7-8 O11] Sensors are reading zeroes most of the time, cyclic patterns are gone (just "noise", ambient 0-10⁰C, sensors in Engel 0-2⁰C); 20211216 135209 Screenshot.jpg [analyzed and annotated Mo2/28/22]	DRD SSC				20211216
				~	13:56	~	22:30	[O4-5 O7-8 O11] Disabled O11 and rebooted (O11 is still soldered to the sensor rack); O4,O5,O7,O8 "mostly" reading again but with a curious cyclic pattern of zeroes (period ~22m)	DRD				20211216
				~	22:30	~	22:54	[O4-5 O7-8 O11] Sensors are reading zeroes most of the time again, cyclic patterns are gone (just "noise" 0-2⁰C); 20211216_225354 Screenshot.jpg shows the entire day [analyzed and annotated Mo2/28/22]	DRD SSC				20211216
				~	23:05			[O4-5 O7-8 O11] W10 powered down: Further troubleshooting of the T-sensors was stopped by the RCWT Emergency [and I didn't get back to it until February]	DRD TM21F				20211216
		20	Mo					[O4-5 O7-8 O11] Disconnected the Sensor Rack from the Wattmon (W10 is needed for the W50 Autopsy Test)	TM21F			-	20211220
2022	Feb	17	Th	~	08:42	~	13:05	[O4-5 O7-8 O11] Sensor Rack attached (O4,O5,O7,O8,O11) and W10 powered up; O11 is soldered but disabled; O4,O5,O7,O8 are logging with some isolated one time errors (shop ambient)	DRD			W10	20220217
				~	13:05			[O4-5 O7-8 O11] Finished placing O4,O5,O7,O8,O11 in Engel and Dinico set 0⁰C					20220217
				~	13:33	~	13:37	[O4-5 O7-8 O11] The (4) sensors stopped reporting when T dropped to ~10⁰C					20220217
				~	14:05	~	14:20	[O4-5 O7-8 O11] Dinico set 15⁰C then 25⁰C					20220217
				~	14:20	~	14:49	[O4-5 O7-8 O11] The (4) sensors started reporting when T came up to ~8⁰C; Dinico setting lowered and sensors stopped reporting when T dropped to ~11⁰C					20220217
				[O4-5 O7-8 O11] W10 power cycled (no effect); Unsoldered and disabled O11,O8,O7,O5 (no effect); O4 alone on the sensor rack and not reporting (in Engel ~5⁰C)		Bad?			20220217
				[O4-5 O7-8 O11] Tested in Engel, by itself on Sensor Rack, by raising and lowering temperature (Dinico setting): [O4] Drops out below ~5⁰C	DRD SSC	BAD			20220217
		18	Fr					[O4-5 O7-8 O11] Removed from Engel and Sensor Rack; Labeled "Bad"	DRD		L	-	20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O5
OneWires: O5	A					T_5: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Jul	27					O2-5	EML WCA	On Order			20150727
		31					WCA	Available	L		20150731
2021	Dec	13					O1-11	DRD IMG WS				20211213
		14	Tu	~	17:03	~	17:28	Tested by itself on Sensor Rack at or above shop ambient	DRD	OK	L0	W10	20211214
				Removed				-	20211214
				~	19:49	~	23:51	Tested at or above shop ambient on Sensor Rack with O4; Then added O7, O8 and O11 (at or above shop ambient) ...; O4-5 O7-8 O11	DRD SSC IMG			W10	20211214
		15	We	~	11:35			O4-5 O7-8 O11	DRD SSC	OK?			20211215
				DRD				20211215
		16	Th	~	04:30					20211216
				~	06:42				DRD SSC				20211216
				~	08:32				DRD				20211216
				~	09:00	~	09:07					20211216
				~	09:07	~	11:50					20211216
				~	11:50	~	13:52		DRD SSC				20211216
				~	13:56	~	22:30		DRD				20211216
				~	22:30	~	22:54		DRD SSC				20211216
				~	23:05				DRD TM21F				20211216
		20	Mo					TM21F			-	20211220
2022	Feb	17	Th	~	08:42	~	13:05		DRD			W10	20220217
				~	13:05					20220217
				~	13:33	~	13:37					20220217
				~	14:05	~	14:20					20220217
				~	14:20	~	14:49					20220217
				20220217
				O4-5 O7-8 O11: O5 Drops out below ~11⁰C	DRD SSC	BAD			20220217
		18	Fr					O4-5 O7-8 O11	DRD		L	-	20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O6
OneWires: O6	A					T_6: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Sep	11					[O6-11] Ordered	EML WCA	On Order			20150911
		14					[O6-11] Received	WCA	Available	L		20150914
2021	Dec	8	We					[O6-9] Assembled (pigtail/solder/shrink bundle); Extended cable length to ~46" (from lower right corner of W10) by adding 18awg stranded red/yellow/black; 2.7Kohm resistor / See drawing "Wattmon T-Sensor Assemblies"; All (4) sensors are being detected in scan	DRD	Applied	L0	W10	20211208
		9	Th					[O6-9] Wattmon_10 configured for (4) sensors; All (4) sensors have intermittent and random problems "reading zeroes" (not communicating properly)	DRD SSC	OK?			20211209
		10	Fr					[O6-9] General Research "1-Wire" (see FTR and SSCs); Powered up Wattmon_10 and observed Ts again; Still getting zeroes; We're "right on the edge" of proper operation / Thoughts to redo the cable assembly, see white sheet "W10 T-Sensors" [I didn't need to do it that way, instead later I hit on fabricating a Sensor Rack]	DRD SSC WS				20211210
		11	Sa					[O6-9] Wattmon_10 FW update made no difference (still getting isolated zeroes); OS update may have fixed it, as for a while I had all (4) Ts stable with no zeroes, then only occasional dropped readings	DRD				20211211
				~	05:10			[O6-9] Shop heat turned off and I went to bed					20211211
				~	09:10			[O6-9] (4) sensors logging nothing but noise (started while I was sleeping); As analyzed later, the major errors most likely started because of the dropping shop ambient					20211211
				~	12:05	~	12:19	[O6-9] I awoke and turned on the shop heat ...; SSC	DRD SSC				20211211
				~	12:55			[O6-9] (4) sensors started logging (but with isolated one-time errors); As analyzed later, the sensors most likely started working again because of the rising shop ambient	DRD				20211211
				~	14:30			[O6-9] Added 2.7Kohm resistor between 5V and OW pins (so now the pullup is ~1.35K); Set Wattmon T datalog points AVG-->MIN / Unfortunately, both of these changes were done about the same time, which helps to confuse the analysis of the graph from this day					20211211
				~	14:45			[O6-9] Freeze spray on T_9 clearly shows in graph					20211211
				[O6-9] This day as analyzed Fr2/25/22: The lower value pullup resistor may have helped clean up the isolated errors (or made no difference at all), but it didn't restore the overall operation of the (4) sensors / The sensors were logging for more than an hour before I changed the resistor, with just isolated one time errors / I believe the logging was restored because the shop ambient rose enough about 50 mins after I turned it up!; See printed and annotated copy of 20211212 071559 Screenshot.jpg					20211211
		12	Su	~	07:15			[O6-9] W10 was on last night, logging, (shop ambient dropping); No intermittent/random problems reading the temperatures / Two SSCs, one for this early morning and one for yesterday [both SSCs printed and analyzed Fr2/25/22] / Lowest temperature logged ~18⁰C [as found out later, these temperatures were probably above the temperatures where these sensors were found to drop out and stop reading] / See printed and annotated copy of 20211212 071528 Screenshot.jpg	DRD SSC				20211212
				~	08:22	~	08:23	[O6-9] A few zeroes for two minutes, after that all OK (sensors near shop ambient)	DRD				20211212
				~	14:00	~	18:22	[O6-9] Engel/Dinico testing at high temperatures up to ~60⁰C (one or more sensors in enclosure, logging OK) ...; Engel/Dinico set -24.0⁰C to start testing at low temperatures	DRD Z0				20211212
				~	18:57			[O6-9] Temperatures had been logging AOK (Engel enclosure temperature dropping), then suddenly O6-O9 reading zeroes (this happened when enclosure temperature dropped below ~20degC) / Cycled power W10 and scanned OW bus; W10 powered off for ~10m; Nothing helped (all zeroes) ...; W10 off for the night					20211212
		13	Mo	~	06:05	~	06:30	[O6-9] W10 on; A few non-zero results from O8 and O7 (-20⁰C) but mostly malfunctioning (zeroes for O6 and O9)	DRD				20211213
				~	06:19	~	06:31	[O6-9] Engel/Dinico set 22⁰C (cover opened) ...; Temperature rose to ~22⁰C [Temperature was regulated at ~20degC for the rest of the day until ~20:08]	DRD Z0				20211213
				[O6-9] Disconnected O6-O9 from W10 (to try O1, which was found to be OK)	DRD O1			-	20211213
				[O6-9] Reinstalled O6-O9 (no extra 2.7K, pullup is 2.7K); O6-O9 inop (all zeroes, all sensors near shop ambient)	DRD			W10	20211213
				[O6-9] Removed two of the individual sensors by cutting them off near the pigtail/solder/shrink bundle: Cut off O9; O6-O8 inop; Cut of O6; O7-O8 OK (logging with no errors for >30m at ~20⁰C)		Bad?		-	20211213
				[O6-9] Disconnected O7-O8 bundle from W10					20211213
				Tested O6 by itself near shop ambient; Wired to W10 pins with 2.7K and DIGND wire nut extension; Not detected in scan				W10	20211213
				Removed				-	20211213
				O1-11	DRD IMG WS				20211213
		14	Tu					Tested by itself on T-Sensor Rack (at or above shop ambient): Not detected in scan	DRD IMG	BAD		W10	20211214
				Removed; Labeled as "Bad"	DRD		L	-	20211214
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O7
OneWires: O7	A					T_7: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Sep	11					O6-11	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914
2021	Dec	8	We					O6-9	DRD	Applied	L0	W10	20211208
		9	Th					DRD SSC	OK?			20211209
		10	Fr					DRD SSC WS				20211210
		11	Sa					DRD				20211211
				~	05:10					20211211
				~	09:10					20211211
				~	12:05	~	12:19		DRD SSC				20211211
				~	12:55				DRD				20211211
				~	14:30					20211211
				~	14:45					20211211
				20211211
		12	Su	~	07:15				DRD SSC				20211212
				~	08:22	~	08:23		DRD				20211212
				~	14:00	~	18:22		DRD Z0				20211212
				~	18:57					20211212
		13	Mo	~	06:05	~	06:30		DRD				20211213
				~	06:19	~	06:31		DRD Z0				20211213
				DRD O1			-	20211213
				DRD			W10	20211213
				20211213
				-	20211213
				O1-11	DRD IMG WS				20211213
				~	14:00			[O7-8] Reinstalled O7-O8 bundle on W10 and configured for more lengthy testing	DRD			W10	20211213
		14	Tu	~	08:53			[O7-8] Temperature Graphs: Two SSCs, one for yesterday and one for this morning; O7/O8 flawless logging without errors (20->60⁰C)	DRD SSC				20211214
				~	09:51			[O7-8] Engel 60⁰C, Dinico set -20⁰C	DRD				20211214
				~	10:34			[O7-8] O8 and O7 started logging all zeroes when the T dropped to <=~20⁰C; O7 removed from harness by cutting; O8 by itself is not working, removed from W10; Put both in box of sensors that need to be tested		Bad?		-	20211214
				~	17:49	~	18:02	[O7-8] Tested by itself on Sensor Rack at ~30 to ~32⁰C; Probably OK, but because it tested this morning as "Bad?" Status is "OK?"		OK?		W10	20211214
				[O7-8] Removed				-	20211214
				~	20:23	~	23:51	Tested at or above shop ambient on Sensor Rack with O4 and O5; Then added O8 and O11 (at or above shop ambient) ...; O4-5 O7-8 O11	DRD SSC IMG			W10	20211214
		15	We	~	11:35			O4-5 O7-8 O11	DRD SSC				20211215
				DRD				20211215
		16	Th	~	04:30					20211216
				~	06:42				DRD SSC				20211216
				~	08:32				DRD				20211216
				~	09:00	~	09:07					20211216
				~	09:07	~	11:50					20211216
				~	11:50	~	13:52		DRD SSC				20211216
				~	13:56	~	22:30		DRD				20211216
				~	22:30	~	22:54		DRD SSC				20211216
				~	23:05				DRD TM21F				20211216
		20	Mo					TM21F			-	20211220
2022	Feb	17	Th	~	08:42	~	13:05		DRD			W10	20220217
				~	13:05					20220217
				~	13:33	~	13:37					20220217
				~	14:05	~	14:20					20220217
				~	14:20	~	14:49					20220217
				20220217
				O4-5 O7-8 O11: O7 Drops out below ~20⁰C	DRD SSC	BAD			20220217
		18	Fr					O4-5 O7-8 O11	DRD		L	-	20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O8
OneWires: O8	A					T_8: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Sep	11					O6-11	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914
2021	Dec	8	We					O6-9	DRD	Applied	L0	W10	20211208
		9	Th					DRD SSC	OK?			20211209
		10	Fr					DRD SSC WS				20211210
		11	Sa					DRD				20211211
				~	05:10					20211211
				~	09:10					20211211
				~	12:05	~	12:19		DRD SSC				20211211
				~	12:55				DRD				20211211
				~	14:30					20211211
				~	14:45					20211211
				20211211
		12	Su	~	07:15				DRD SSC				20211212
				~	08:22	~	08:23		DRD				20211212
				~	14:00	~	18:22		DRD Z0				20211212
				~	18:57					20211212
		13	Mo	~	06:05	~	06:30		DRD				20211213
				~	06:19	~	06:31		DRD Z0				20211213
				DRD O1			-	20211213
				DRD			W10	20211213
				20211213
				-	20211213
				O1-11	DRD IMG WS				20211213
				~	14:00			O7-8	DRD			W10	20211213
		14	Tu	~	08:53				DRD SSC				20211214
				~	09:51				DRD				20211214
				~	10:34					Bad?		-	20211214
				~	18:19	~	18:47			OK?		W10	20211214
				-	20211214
				~	22:44	~	23:51	Tested at or above shop ambient on Sensor Rack with O4, O5 and O7; Then added O11 (at or above shop ambient) ...; O4-5 O7-8 O11	DRD SSC IMG			W10	20211214
		15	We	~	11:35			O4-5 O7-8 O11	DRD SSC				20211215
				DRD				20211215
		16	Th	~	04:30					20211216
				~	06:42				DRD SSC				20211216
				~	08:32				DRD				20211216
				~	09:00	~	09:07					20211216
				~	09:07	~	11:50					20211216
				~	11:50	~	13:52		DRD SSC				20211216
				~	13:56	~	22:30		DRD				20211216
				~	22:30	~	22:54		DRD SSC				20211216
				~	23:05				DRD TM21F				20211216
		20	Mo					TM21F			-	20211220
2022	Feb	17	Th	~	08:42	~	13:05		DRD			W10	20220217
				~	13:05					20220217
				~	13:33	~	13:37					20220217
				~	14:05	~	14:20					20220217
				~	14:20	~	14:49					20220217
				20220217
				O4-5 O7-8 O11: O8 Drops out below ~17⁰C	DRD SSC	BAD			20220217
		18	Fr					O4-5 O7-8 O11	DRD		L	-	20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O9
OneWires: O9	A					T_9: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Sep	11					O6-11	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914
2021	Dec	8	We					O6-9	DRD	Applied	L0	W10	20211208
		9	Th					DRD SSC	OK?			20211209
		10	Fr					DRD SSC WS				20211210
		11	Sa					DRD				20211211
				~	05:10					20211211
				~	09:10					20211211
				~	12:05	~	12:19		DRD SSC				20211211
				~	12:55				DRD				20211211
				~	14:30					20211211
				~	14:45					20211211
				20211211
		12	Su	~	07:15				DRD SSC				20211212
				~	08:22	~	08:23		DRD				20211212
				~	14:00	~	18:22		DRD Z0				20211212
				~	18:57					20211212
		13	Mo	~	06:05	~	06:30		DRD				20211213
				~	06:19	~	06:31		DRD Z0				20211213
				DRD O1			-	20211213
				DRD			W10	20211213
				Bad?		-	20211213
				20211213
				Tested O9 by itself near shop ambient; Wired to W10 pins with 4.7K and DIGND wire nut extension; Not detected in scan; Tested again with 2.7K (not detected); And again with 2.7K (not detected)				W10	20211213
				Removed				-	20211213
				O1-11	DRD IMG WS				20211213
		14	Tu					Tested by itself on T-Sensor Rack (at or above shop ambient): Not detected in scan	DRD IMG	BAD		W10	20211214
				Removed; Labeled as "Bad"	DRD		L	-	20211214
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O10
OneWires: O10	A					T_10: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD, Cut Off	L	-
2015	Sep	11					O6-11	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914
2021	Dec	13	Mo					Quick tests by itself, at shop ambient: Not detected in scan; Tested again with busbar setup (not detected in scan)	DRD	BAD	L0	W10	20211213
				Labeled as bad (and we can use the cable); Cable cut off for W10 Sensor Rack		BAD, Cut Off	L	-	20211213
				O1-11	DRD IMG WS				20211213
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O11
OneWires: O11	A					T_11: DS18B20 Digital Temperature Sensor

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD	L	-
2015	Sep	11					O6-11	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914
2021	Dec	13					O1-11	DRD IMG WS				20211213
		14	Tu	~	19:16	~	19:33	Tested by itself on Sensor Rack at ~20⁰C	DRD	OK	L0	W10	20211214
				Removed				-	20211214
				~	23:17	~	23:51	Tested at or above shop ambient on Sensor Rack with O4, O5, O7 and O8 (at or above shop ambient) ...; O4-5 O7-8 O11	DRD SSC IMG			W10	20211214
		15	We	~	11:35			O4-5 O7-8 O11	DRD SSC	OK?			20211215
				DRD				20211215
		16	Th	~	04:30					20211216
				~	06:42				DRD SSC				20211216
				~	08:32				DRD				20211216
				~	09:00	~	09:07					20211216
				~	09:07	~	11:50					20211216
				~	11:50	~	13:52		DRD SSC				20211216
				~	13:56	~	22:30		DRD	Bad?			20211216
				~	22:30	~	22:54		DRD SSC				20211216
				~	23:05				DRD TM21F				20211216
		20	Mo					TM21F			-	20211220
2022	Feb	17	Th	~	08:42	~	13:05		DRD			W10	20220217
				~	13:05					20220217
				~	13:33	~	13:37					20220217
				~	14:05	~	14:20					20220217
				~	14:20	~	14:49					20220217
				20220217
				O4-5 O7-8 O11: O11 Drops out below ~18⁰C	DRD SSC	BAD			20220217
		18	Fr	~	09:30			O11 has been OK all night, but temperature low was 18.6⁰C, above where it dropped out yesterday ...; O4-5 O7-8 O11	DRD		L	-	20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O12
OneWires: O12	A					T_12: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD?	L	-
2021	Dec	15					[O12-18] These are listed on SparkFun.com at $9.95 (but they may charge sales tax and I don't trust them to ship quickly like I trust DigiKey) / Ordered DigiKey at $11.95; 20211215 DigiKey Invoice O12 to O18 (T_12 to T_18) Scan.jpg	EML DRD DKE LIB	On Order			20211215
		18					[O12-18] Received	DRD	Available	L		20211218
2022	Feb	18					[O12-18] Downloads to Library\SparkFun Electronics: 20220218.0 Datasheet SparkFun SEN-11050 (DS18B20).pdf; 20220218.1 Datasheet Dallas Semiconductor DS18B20.pdf / I also created 20180422 Datasheet Maxim DS18B20 (from Wattmon).pdf by copy/rename from Library\Wattmon (India)	LIB				20220218
		19	Sa					By itself on Sensor Rack, shop ambient, pullup resistor 2.7K; Intermittent temperature reporting in the first 10~15m then zeroes; Pullup resistor changed to 4.7K, not reporting; Disabled; Unsoldered (yet on rack)	DRD	BAD?	L0	W10	20220219
		20	Su					[O12-14] Further troubleshooting of T-sensors stopped by ONWT Emergency	DRD TM22				20220220
	May	26	Th					[O12-14] T-Sensor Rack removed and set aside; O12-O13 physically attached but not soldered; O14 soldered (it was the last OW I tested before having to move on to other priorities)	T48S		L	-	20220526
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O13
OneWires: O13	A					T_13: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD?	L	-
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
		19	Sa					By itself on Sensor Rack, shop ambient, pullup resistor 4.7K; Not detected in scan (4x); Unsoldered (yet on rack)	DRD	BAD?	L0	W10	20220219
		20	Su					O12-14	DRD TM22				20220220
	May	26	Th					T48S		L	-	20220526
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O14
OneWires: O14	A					T_14: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				BAD?	L	-
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
		19	Sa					By itself on Sensor Rack, shop ambient, pullup resistor 4.7K; Not detected in scan (4x); Left it soldered to rack	DRD	BAD?	L0	W10	20220219
		20	Su					O12-14	DRD TM22				20220220
	May	26	Th					T48S		L	-	20220526
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O15
OneWires: O15	A					T_15: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O16
OneWires: O16	A					T_16: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O17
OneWires: O17	A					T_17: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## O18
OneWires: O18	A					T_18: SEN-11050 SparkFun Temperature Sensor (DS18B20)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Dec	15					O12-18	EML DRD DKE LIB	On Order			20211215
		18					DRD	Available	L		20211218
2022	Feb	18					LIB				20220218
2023	Jan	20	Fr					O1-18	T48-4 W10				20230120

## P1
Panels: P1	A					P_1: Fennel PWP-100W 100W 12V Polycrystalline

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Apr	22					Ordered from eBay.com; Slated for RW	EML TSP	On Order		20150422
		28					Received	TSP	Available	L	20150428
		29					Modified: Removed connectors and installed Speaker Wire (blue, #12 pair); Testing W side of shop	IMG		L0	20150429
		30					Installed at RW; Initial installation with Mark Webb and Keith Jones		Applied	L1	20150430
	Sep	3					[P1-2] Onsite at RW with Juliya				20150903
2016	Jun	16					[P1-3] Onsite at RW				20160616
		29					[P1-3] These records caught up (sticker printed to be applied upon next trip to RW)				20160629
	Dec	16					[P1-3] Stickers applied; Dimensions	IMG			20161216
		22					[P1-3] Onsite at RW: Photos of 3 panels and new battery box installed 12/16/16				20161222
2018	Aug	13	Mo					[P1-2] Onsite at RW 09:15; AC OK; Photos (before); Removed solar panels P_1 and P_2; Photos (after)		Available	L	20180813

## P2
Panels: P2	A					P_2: Fennel PWP-100W 100W 12V Polycrystalline

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Jul	8					Ordered from eBay.com; Slated for RW	EML TSP	On Order		20150708
		15					Received	TSP	Available	L	20150715
		?					Modified: Removed connectors and installed Speaker Wire (blue, #12 pair)				201507?
		17					Approximate date of installation at RW: [P_2] above [P_1]		Applied	L1	20150717
	Sep	3					P1-2	IMG			20150903
2016	Jun	16					P1-3				20160616
		29					20160629
	Dec	16					IMG			20161216
		22					20161222
2018	Aug	13	Mo					P1-2		Available	L	20180813

## P3
Panels: P3	A					P_3: SunPower PowerFree AFP-100W-Mono 100W 12V Monocrystalline Semi-Flexible

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Aug	19					Ordered from AFP Power	EML TSP	On Order		20150819
		20					Received; Slated for SAPS; [Th6/16/16 installed at RW]	TSP	Available	L	20150820
2016	Jun	16	Th					P1-3; Installed P_3 underneath P_1	IMG	Applied	L1	20160616
		29					P1-3				20160629
	Dec	16					IMG			20161216
		22					20161222
2018	Jul	20					Removed from RW (stored on W side); Slated for SAPS	MA2	Available	L	20180720
2023	Jan	20					4-1/2 years later: SAPS probably isn't going to use it (slated for anything that needs it)	T48-4			20230120

## P4
Panels: P4	A					P_4: Renogy RNG-100D 100W 12V Monocrystalline

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L2
2015	Sep	10					[P4-5] Ordered from eBay.com; Slated for RN	EML TSP	On Order		20150910
		15					[P4-5] Received	TSP	Available	L	20150915
		?					[P4-5] Modified: Removed connectors and installed Speaker Wire (blue, #12 pair)				201509?
		19					[P4-5] Approximate date of installation at RN: [P_4] underneath [P_5]; Photos of tower/panels	IMG	Applied	L2	20150919
2016	Jun	29					[P4-5] These records caught up (sticker printed to be applied upon next trip to RN)				20160629
	Jul	16	Sa					[P4-5] Onsite at RN: Stickers applied; Photographs	IMG	Sold		20160716
2019	Jan	22	Tu					[P4-5] Onsite at RN: Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)				20190122
2020	Aug	11	Tu	~	12:05	~	13:45	[P4-5] Onsite at RN with Keith; Photos TurboNet Onsite @ Swafford Tower; Keith Jones			L2	20200811

## P5
Panels: P5	A					P_5: Renogy RNG-100D 100W 12V Monocrystalline

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L2
2015	Sep	10					P4-5	EML TSP	On Order		20150910
		15					TSP	Available	L	20150915
		?					201509?
		19					IMG	Applied	L2	20150919
2016	Jun	29					20160629
	Jul	16	Sa					IMG	Sold		20160716
2019	Jan	22	Tu					20190122
2020	Aug	11	Tu	~	12:05	~	13:45				L2	20200811

## R1
WebRelays: R1	A					R_1: Xytronix Research & Design X-WR-1R12-1I5-I

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	192.168.1.50	-
2016	Feb	23					[R1-2] Ordered from Zytronix	EML WCA	On Order				20160223
				[R1-2] From Keith Jones "Ip's for Jeff Klute": 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay), both are 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML AED					20160223
		24					[R1-2] To Keith Jones "Re: Ip's for Jeff Klute" which summarizes static IPs: / 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay)	EML CPSN AED					20160224
		26					[R1-2] Received	WCA	Available	L			20160226
	Mar	11					Initial test	AED	Testing	L0	192.168.1.50		20160311
				Configured and left under test …			12.133.21.143		W3	20160311
		16					Installed at RN	AED IMG	Applied	L2			20160316
	Jul	16	Sa		08:08		09:22	Wattmon_3 r/w Wattmon_7	AED				W7	20160716
				Spare fuse silver taped to cord for power to WebRelay and Wattmon (2 Amp fast)	AED IMG					20160716
		23	Sa					[R1-2] I started paying attention to potential WebRelay reboots of the Wattmons; For a while I will try to remember to record here any RCON=3 incidents (cold power starts) that I know I didn't initiate					20160723
		24	Su		12:52			RCON=3					20160724
		25	Mo		00:33		11:52	RCON=3 …; RCON3					20160725
				11:58			RCON=3					20160725
		26	Tu		11:08			RCON=3					20160726
		28	Th		05:44		06:26	RCON=3 …; RCON3					20160728
				09:45		10:06	RCON=3 (email was rec'd 09:50, delayed by email servers) …; RCON3					20160728
				10:31		13:02	RCON=3 …; RCON3					20160728
				16:40		21:37					20160728
		29	Fr		02:09		06:44					20160729
				06:55		08:54	RCON=3 …; RCON3 (email was rec'd 09:03, delayed)					20160729
				10:53		10:53	RCON=40 …; followed immediately by RCON=3; I was watching the WebRelay when it did it, and Wattmon WAS accessible by HTTP, and had not stopped logging / The RCON=40 would have fixed it if the WebRelay was not so aggressive					20160729
				11:22			RCON=3					20160729
				~	17:05			[R1-2] Main Header Text modified (--> "L#2, Swafford N" and "L#1, Water Tower"); Failed Pings Before Reboot modified (10-->100, or about 17 mins) / For a while I will try to remember to record here any RCON=3 incidents (cold power starts) that I know I didn't initiate					20160729
				17:30		22:36	RCON=3. I watched the WebRelay do it. Wattmon WAS accessible by HTTP, ping attempts went to 100, the the WebRelay rebooted. I have no clue now as to why the pings stopped working …; RCON=3					20160729
		30	Sa		02:54			RCON=3					20160730
				04:55			[R1-2] OK, enough: I will not record RCON=3 incidents any more now; If interested, search the Wattmon System Log					20160730
2017	Jan	31	Tu	~	08:45			[R1-2] Disabled Automatic Reboot: Will watch and see if everything goes OK without ping rebooting / Many of the reboots have been unneccessary (I've watched the web relays reboot due to failed pings many times, while the Wattmon is perfectly accessible) / I've also been having difficulties working with DailyBackup.cgi, where I think some of the reboots are due to the web relays having lost pingbacks		Sold				20170131
2019	Jan	22	Tu					Onsite at RN: Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)		Available	L			20190122
2020	Feb	7	Fr					[R1-2] VM from Keith Jones, inquiring about web relays	TW4-5					20200207
		10	Mo					[R1-2] Call to Keith, LMVM: Willing to sell (2) Web Relays for <$80 each					20200210
2021	Nov	20					Selected for ONWT Remote Monitoring project	DORM	ONWT Prep	L0		W6	20211120
2022	Oct	23					ONWT Remote Monitoring project abandoned		Available	L		-	20221023

## R2
WebRelays: R2	A					R_2: Xytronix Research & Design X-WR-1R12-1I5-I

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	192.168.1.50
2016	Feb	23					R1-2	EML WCA	On Order				20160223
				EML AED					20160223
		24					EML CPSN AED					20160224
		26					WCA	Available	L			20160226
	Mar	16					On Bench …	AED	Configuring	L0	192.168.1.50		20160316
				Configured			12.133.21.157		W2	20160316
				Installed at RW	AED IMG	Applied	L1			20160316
	Jun	1					Wattmon_2 and C252_2 removed and replaced with Wattmon_6 and C252_1	AED				W6	20160601
		16	Th	>	11:10			Wattmon_6 removed and Wattmon_8 installed at RW	AED IMG				W8	20160616
	Jul	23	Sa					R1-2					20160723
				20:50			RCON=3					20160723
		24	Su		15:35			RCON=10 (software initiated) immediately followed by RCON=3 (within 2 minutes)					20160724
		25	Mo		05:32		16:40	RCON=3 …; RCON=3					20160725
		26	Tu		04:13			RCON=3					20160726
		27	We		13:40					20160727
		28	Th		19:26					20160728
		29	Fr		06:57		11:06	RCON=3 …; RCON=3					20160729
				~	16:53			R1-2					20160729
		30	Sa		02:29		04:21	RCON=3 …; RCON=3					20160730
				04:55			R1-2					20160730
	Dec	16					Onsite at RW	IMG					20161216
2017	Jan	19					Onsite at RW to install 3rd Genasun					20170119
		31	Tu	~	08:45			R1-2					20170131
2018	Jan	15	Mo	~	12:00			Removed from RW	AED	Available	L			20180115
2020	Feb	7	Fr					R1-2	TW4-5					20200207
		10	Mo					20200210

## S1
Supplies: S1	A					HZ_1: Heathkit IP-2718

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Needs R&R	L
1976					Approximate year of manufacture (copyright dates on my dad's printed manual and assembly instructions, and also on the manual downloaded 5/11/18); My dad probably bought it and assembled it within a year or so	LIB	Ft. Collins, CO		#N/A
1997	Nov					Data Vision Services opened up in Ft. Collins: Sometime before DVs moved to Missouri in the year 2000 my Dad gave me the Heathkit to use for monitor repair work		Available		#N/A
2008	Oct	15					The main shop: Heathkit shown	IMG		L	20081015
2015	Apr	16					The main shop: Heathkit shown being used to charge a battery		Applied		20150416
	May	31					Photos		Available		20150531
	Apr	14					Powering Wattmon_10 on bench, on and off		Applied	L0	20150414
	Jun	24					Removed from powering Wattmon_10		Available	L	20150624
		26	Tu					Wattmon_10		Applied	L0	20150626
2018	Mar	15	Th					[S1-2 S4] Photos 'W100 Testing' (Trace used as CW load, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)	IMG			20180315
	Jul	19		~	06:00	~	06:45	RSDM tested with BK (5v Vdd) and Heathkit (INHI, 0-20vdc)	MA2			20180719
2019	Mar	28			21:30			Wattmon_10 powered OFF (I haven't been able to work on the SAPS for more than 7 months)		Available	L	20190328
		31		~	13:05			Powering Wattmon_9 (and charging old 7AH battery)		Applied		20190331
	May	15					[S1-2] This history sheet reviewed and entries caught up to date				20190515
		22	We					Powering Wattmon_9 and float charging 6 pack of old batteries (A30, TL3_6, + battery I was using before); Adjusted to 13.7vdc Fluke; Note that Heathkit is NOT on UPS, so it dies if power is lost				20190522
	?	?					Also powering Wattmon_10 and when DR Test Setup is being used the DC fans for the APC and load switch				2019MM?
	Jun	28					[S1-2 S6-7] W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1 (charging 6-pack and powering W9 and W10)	IMG			20190628
	Jul	8					[S1-2 S6-7] W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1				20190708
		14					[S1-2 S7] W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)				20190714
		17					[S1/7] W100 DR Test Setup: APC_1 (A32), WP5, C2, S7, A10, 6-pack (Heathkit)				20190717
	Aug	4					W100 DR Test Setup, CC with Ballast (BK_1, 6-pack/Heathkit, B54)				20190804
	Sep	15		~	14:00			Wattmon_9 Battery Status Graph shows we lost connection from Heathkit to 6-pack (probably loose clip lead on Heathkit); 6-pack begins to discharge	W9			20190915
		18		~	04:10			Wattmon_9 and Wattmon_10 Battery Status Graph shows that both Wattmons stopped logging when 6-pack dropped to 6.2-6.4v (as per W9)	W9 W10			20190918
		22			07:55	~	08:20	I discovered that 6-pack was not being charged, totally dead, and Wattmon_9 and Wattmon_10 were not operating; Restored connection to Heathkit but charge current is of course only about 0.5 Amps / Attached BK_1 (13.8v/4.2a), now charging at about 3.5 amps ...; Decided to reduce current limit on BK to 2.1 Amps (in case one of the batteries is soaking up more than the others) / Now charging CC (Heathkit OFF, W9 and W10 attached and running)	W9 W10 S2			20190922
		25	We	~	05:15			6-pack charge current has finally dropped down to where the Heathkit may be able to handle it (560 mA, 13.8v, Fluke 13.65v); 6-pack on Heathkit	S2			20190925
		26	Th					6-pack charge current has exceeded what Heathkit can handle since yesterday (now 12.62v); The warmest battery is JC3#13 battery #20, disconnected from 6-pack; voltage is rising				20190926
2020	May	31	Su					5-pack sent to salvage	A30	Available		20200531
	Jun	13	Sa					Supply B is inoperative; Moved to shelf above DR Test Setup; Applied to Old Honda Battery on the bench		B0		20200613
2021	Jan	16	Sa					[S1-2 S15-16] Seen in videos and photos of TurboNet/RHS bench testing	IMG			20210116
	Oct	24	Su					Video sent to Pavel via Viber				20211024
	Nov	13	Sa					[S1-2] Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup				20211113
		14	Su	~	00:13	~	00:22	[S1-2] Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)				20211114
2022	Feb	24	Th					B0 is failing (high no-load charge current); Meter and regulation is flaky, must use Extech and separate voltmeter; Don't completely trust the meter or regulation for Amps or Volts / Heathkit needs to be disassembled, pots and connections checked/cleaned/tightened/repaired, supply B fixed, calibrated against ITECH	DRD B0	Needs R&R		20220224
	Mar	1	Tu					BO charge current 0.56aE (maximum Heathkit can do); Weird shifts in output voltage, ~12.5vM, Added load W10 and >13vM, later ~12.5vM / Why is the voltage shooting all over the place? Is it because I'm running S1 at maximum current all of the time?; Heathkit case 100⁰F (Fluke IRT MAX)				20220301
	May	26	Th	~	10:00	~	19:15	[S1-2] (Preparing Schauer BC7); Heathkit is not charging; Added BK in parallel, set 13.6v/5.1a; Heathkit OFF ...; Heathkit disconnected from B0 (now using BK direct to #12 AWG Red/Blk)	T48S B0 S2			20220526
	Jun	11	Sa					[S1-2] BC7 BTS test setup broken down: Heathkit on B0, T2 UPS, No load ~13v ~320mA (with circulating fans ~480mA); Lowered setting to ~12.7v (no load ~10mA)	T48S BC7 B0			20220611
	Sep	17	Sa					[S1-2 S13] Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917

## S2
Supplies: S2	A					BK_1: BK Precision 9110

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Aug	3					Ordered from Amazon.com ($248.89 + 17.97 S&H - 35.81 Rewards Points)	EML WMBS	On Order		20150803
		4					Datasheet and Manual downloaded	LIB			20150804
		6					Received; Placed in service (calibrating Wattmons, charging batteries, etc.)	WMBS	Applied	L0	20150806
2015	Sep	8					Used to calibrate Wattmon_2 and C252_2	AED			20150908
		18					Used to calibrate Wattmon_2 and both loops of C252_2 (M2): A1/Vin calibrated against BK Precision, 6.00 to 18.00 volts, 1.00 volt steps; C252_2 zero offsets; 5.000 Amps in 4 loops				20150918
		19					Used to calibrate Wattmon_3 and C252_2 onsite at RN				20150919
2016	Feb	10					Used to attempt battery rejuvenation of batteries for TrippLite TL6_6_B … until 2/13/16	A24			20160210
		13					Used to attempt battery rejuvenation of batteries for TrippLite TL6_4_B … until 2/20/16	A18			20160213
2016	Jun	6					Bench calibration of Wattmon_8 using BK_1	IMG AED			20160606
2016	Oct	25					Used to attempt battery rejuvenation of batteries for TrippLite TL6_5_B	A21			20161025
		31					Used to attempt battery rejuvenation of batteries for TrippLite TL3_1 … until 11/1/16	A25			20161031
2016	Nov	1					Used to float batteries for TrippLite TL6_4_B; Used to charge batteries for TL3_5; Used to charge batteries for TL3_6 … until 11/22/16	A18 A29 A30			20161101
2017	Feb	24					Used to float batteries for TrippLite TL3_6 … until 2/28/17	A30			20170224
2018	Feb	25					WISPOWER #2 Testing: / BK being used as "Solar Panel" input to Genasun_3 (via Schottky)	WRD TW2-3 IMG WP2	WP2 Testing		20180225
2018	Mar	2					WP2/W100_1: White sheet notes on testing concluded 3/2/18, Setup and Conclusions: BK 100w power supply as solar input to Genasun, resistive load ~160w, Genasun hunting around but OK	WRD TW2-3 WS			20180302
		3					WP2/W100_1: (4) White sheet notes "Testing continued with new [Delta] Power Supply": Boosting Delta 150W with BK in parallel; Conclusions "Leave it overnight" and "Wattmon needs correction/configuration"				20180303
		5					[S2-3] W100 Testing (boost for Delta 150W, Genasun_3 no cover, fan taped to bench, W9, B1)	IMG	W100 Testing		20180305
		13					[S2/4] W100 Testing (Trace used as CW load, B1, Delta 200W, Genasun mounted under fan, W9, C252, BK)				20180313
		15					S1-2 S4				20180315
		20					[S2/4] W100 Testing, calibration of C252 (WP2, Delta 200W, Genasun mounted under fan, B1, BK, Trace being used as CW load)				20180320
2018	Apr	2		~	15:15			[S2/4] Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): Sent to Akash	IMG EML	DR Testing		20180402
2018	May	7	Mo					Used to test UPS PS700_2, 28v, 5.1amps	A3	Applied		20180507
		12	Sa					Front and rear (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC)	IMG	DR Testing		20180512
2018	Jun	15	Fr	~	04:45			Removed from powering W9 for use in testing PS_3	V6	PS_3 Testing		20180615
		20	We					Inventory Sticker applied				20180620
		23	Sa					Removed from PS_3 Testing; Used to calibrate C752_1 on Wattmon_10 …	AED	C752_1 Calibration		20180623
		24	Su					… C752_1 calibration concluded; Wattmon_10 Vin/A1 calibration started …		W10 Calibration		20180624
		25	Mo					… Wattmon_10 Vin/A1 calibration completed, being used to power Wattmon_10		W10 Power		20180625
		26	Tu					Available	L	20180626
		27	We					Milwaukee NiCad …		Applied	L0	20180627
		28	Th					I8O8_1 testing …	AED			20180628
		29	Fr					… I8O8_1 testing concluded; PS_4 and DI_1 testing; Also used for TEC_1 and TEC_2 testing	I1 Z11 Z3 Z4	Available	L	20180629
2018	Jul	7	Sa	~	03:20	~	19:00	Milwaukee NiCad				20180707
		8	Su					Tested 12v electromechanical buzzer for SAPS dashboard: 40-80 mA @ 9 to 16 vdc (can be driven from DO1-DO4 which are 500 mA capable)	SOW			20180708
		15	Su					Charging Powerex TRUE 9.6V "200" [blue felt tip "2"]: Battery is rated 230mAh; .05C trickle is 10mA (if battery is lukewarm trickle is too high); "Difficult to impossible to slow charge … 0.1C to 0.3C … must use timer, but time varies" / Charge eff 100% to 70% SoC and remains cool / "Best Fast Charged" and "if lukewarm it is full" (90-110°F, can use 1995 T Monitor to alarm when reaches desired temperature, I found a sharp rise past 100°F to indicate fast charge should stop)		Nimh	L0	20180715
				04:30		05:30	Started with C=200mA (15v limit) … after 1 hr 14.7v and >100°F (sharp jump in last 15 mins)				20180715
				05:30		05:56	Reduced to trickle 10mA … 11.91v, 81°F		Available	L	20180715
		19		~	06:00	~	06:45	SAPS RSDM tested with BK (5v Vdd) and Heathkit (INHI, 0-20vdc)	MA2	Applied		20180719
2018	Aug	13					Onsite at RW, used briefly				20180813
		15					Used to calibrate and power Wattmon_8	AED		L0	20180815
		29	We	~	08:30			Temperature sensor on W9 used to log temperature of NiCad being charged by BK (and BK is powering Wattmon_9)	W9 O1			20180829
		30	Th	~	02:30			Notes on charging Milwaukee NiCad: I applied a C/14 charge current (~160mA, BK was set for 260mA as Wattmon draws ~100mA); 80mm AC fan blowing in on side of battery / The T sensor was placed underneath the battery pinned to the formica countertop; There was a strange jump in voltage @ ~5 hrs into charge (14.1 to 15.4v in < 5 mins) / Peak 15.9v @ 12.5 hrs into charge, declining to 15.5v @ 18 hrs into charge (when terminated) / Battery temperature rose slowly starting at about 8 hrs into charge, but came up more sharply at peak voltage (12.5 hrs into charge) and continued to rise past that (nominal 24⁰C ending 26⁰C) / Temperature rise would probably be easier to detect if there was no fan; Temperature rise would be the easiest to use to detect end of charge, as voltage peak is very broad, but temperature just goes up and doesn't come down / IDEAL setup for charging Milwaukee NiCad: Power Wattmon separately (A1/Vin), T sensor taped to top of battery (no fan), set 240 mA (C/10), use relay on Wattmon to terminate charge when temperature comes up more than 2⁰C		Available	L	20180830
2018	Nov	2	Fr	~	07:10			Installed to charge old battery and power Wattmon_9 (13.6v)	W9	Applied		20181102
2019	Mar	31	Su	~	12:10			Removed from powering Wattmon; Used to attempt equalization of B4-B7 on CP_1	A1 B4-B7		L0	20190331
2019	Apr	1	Mo				08:53	Notes on Absorption/Equalization charging of (4) T-105s in series (B4-B7) using BK_1: Best to do this after a power failure, or twice per year; There's probably not enough power to reach Equalization of 32.40vdc / OVP will not shut it off (it only keeps you from setting a higher voltage); Set Equalization 32.40vdc/3.086amps with a solid connection; Once it reaches 29.64vdc (Absorption) hold for 2 hours		Available	L	20190401
		27	Sa	~	13:00			BK_1 used to charge Milwaukee Nicad (20.00v, 0.160a, Preset A) for <=24 hours …	W9 O1	Applied		20190427
		28	Su				08:30	19 hrs 40 mins was enough (battery is warming itself)		Available		20190428
				08:42	~	14:20	Absorption/Equalize on (4) T-105s (B4-B7) …; CP_1 shut itself off, which shut off BK_1 also (and entire network), I suspect due to overvoltage / New notes on Absorption/Equalization charging of (4) T-105s in series (B4-7) using BK_1 while on CP_1: Can't go over ~30vdc or CP_1 will shut down due to battery overvoltage / Trojan recommends 32.40vdc, Genasun does 30.00vdc; Set Absorption/Equalization 30.00vdc/3.333amps (Preset B), once it reaches 29.64vdc (Absorption) hold for 2 hours	A1 B4-B7	Applied		20190428
				15:10		15:18	Absorption/Equalize on (4) T-105s (B4-B7) (on CP_1), 27.2vdc …; 30vdc, and since we Equalized for 1hr20mins already I shut it off		Available		20190428
2019	May	15	We		09:44		15:10	Bulk/Absorption/Equalize on (4) T-105s (B4-B7) (on CP_1), started at 25.5vdc …; 29.7vdc (planning on continuing for 2 hrs) …		Applied		20190515
				S1-2				20190515
				17:12			… 29.9vdc; BK OFF	A1 B4-B7	Available		20190515
		17	Fr		08:30	~	08:53	Started experiment in charging Milwaukee Nicads with Tsensor on Wattmon_9 to detect full charge; 20.00vdc/0.160amp …; Readjusted Tsensor position to right side of battery (battery terminals up and front) / Also see notes from 8/30/18	W9 O1	Applied		20190517
				~	16:30			Accidently killed the power to BK_1 (I failed to notice that I had plugged it in the same switched T1 circuit as the Ott-Lite at the main station)				20190517
		18	Sa		02:50		18:54	Reapplied power to continue charging …; Charging stopped (~24 hours total charge)		Available		20190518
				Conclusions for Charging Milwaukee Nicads using Tsensor to Detect Full Charge: I wasn't able to detect an obvious increase in temperature at full charge / The temperature reached a plateau at about 31.5⁰C which continued to the 24 hour point (lab temperature about 23.5⁰C); I suggest a slightly higher charge rate of C/10 (240mA) to make full charge point more obvious (limit to 16 hrs) / Higher charge rate will increase the plateau temperature; Also suggest having the Wattmon log the battery voltage, but A1/Vin cannot be used for this due to the parasitic power needs of the Wattmon (try using A2 0-300vdc, it would not need to be calibrated, we are just trying to see where the peak voltage is in time and use that to help determine an algorithm based on Temperature) / Could also manually record battery voltage at 30 min intervals, especially near peak voltage (this might be the easiest method, considering that using A2 would require some Wattmon setup)				20190518
		19	Su	~	12:10			TL3_6 batteries all (6) in parallel charging on BK_1 @ float of 13.60 vdc	A30 IMG	Applied		20190519
		22	We					Removed 6 pack of old batteries (TL3_6, + battery I was using before) and placed them on Heathkit (adjusted to 13.7vdc Fluke) powering Wattmon_9	A30 S1 W9	Available		20190522
		25	Sa		06:39			Charging JC12#10 Battery #08 from salvage pile; 13.70v/0.350a (C/20) …		Applied		20190525
		27	Mo		07:10		07:15	… JC12#10 Battery #08 not recoverable, returned to salvage pile …; JC12#10 Battery #14 from salvage pile; 13.70v/0.350a (C/20) …				20190527
				07:55		07:56	… JC12#10 Battery #14 returned to salvage pile; Unknown BB BP7-12 from a 6-pack from salvage pile; 13.70/0.350a (C/20) …; CC for less than a minute; 13.7v/340mA dropping …				20190527
		28	Tu	~	18:30			… Unknown BB BP7-12 from a 6-pack: CV 13.70/57mA dropping; 78°F (this is a good battery for the 6-pack I want to keep on the bench); Removed to "marry" to bench 6-pack	A30	Available		20190528
2019	Jun	4	Tu	~	11:45		12:40	Charging Milwaukee Nicad: 12.88v (on BK w/o charge); Wattmon_9 to monitor temperature, sensor is on right side; Nicad was allowed to cool down (I put it in the freezer for 5 mins) until stabilized at room temperature ~23⁰C … / 12.91v (on BK w/o charge); 20.00v/240mA, and I will limit this to 16 hours; CC 13.5v climbing	W9 O1 IMG	Applied		20190604
		5	We	~	00:50			Charging Milwaukee Nicad: 16.88v dropping slowly, 33.5⁰C rising; removed from BK charge (12 hrs 10 mins total); Temperature was flat until ~19:50, when it began to rise in almost a straight line passing 30⁰C at 23:00 / Charging algorithm s/b 240mA (C/10) until temperature rises beyond 30⁰C (in this case ~11 hours), for safety time out at 16 hours; 20190605 010735 Screenshot.jpg	W9 O1 SSC	Available		20190605
		16	Su	~	10:10	~	20:30	Charging Milwaukee Nicad A: Some cool down (I put it in the freezer for 3 mins) to ~27⁰C but it had not yet stabilized at room temperature ~23⁰C; 8.44v (on BK w/o charge); Wattmon_9 to monitor temperature, sensor is on right side, charge current goes through RL1/2, Actions modified to Switch Off RL1/2 when T>30⁰C (I will limit this to 16 hrs); 20.00v/240mA, CC 8.9v climbing ...; Relay shut it off @ 10 Hrs 20 Mins	W9 O1	Applied		20190616
		17	Mo	~	01:15		01:35	Temperature Graph, NiCad charge: 20190617 011553 Screenshot.jpg …; Charging Milwaukee Nicad B: No cool down needed, battery is ~22⁰C; 15.45v on BK w/o charge / Wattmon_9 to monitor temperature, sensor is on right side, charge current goes through RL1/2, Action 'T>30'; 20.00v/240mA, CC 15.6v climbing ...	SSC W9 O1			20190617
				~	08:33	~	09:55	17.59v highest voltage seen (but not sure it was the peak)...; Relay shut it off at 8 Hrs 20 Mins; The peak voltage was somewhere between 06:37 and 08:45, and temperature began to rise at ~07:00 / Recommend using 28⁰C for the cutoff (or about 5⁰F above ambient temperature); 20190617 101017 Screenshot.jpg; Action modified and renamed 'T>30' to 'T>28'		Available		20190617
		25	Tu					Calibration of C252_1 and C252_2 on Wattmon_10	AED WCX	Applied	L0	20190625
		26	We					Calibration of A10_1 on Wattmon_10		Available	L	20190626
		28	Fr					Quick check of calibration of C252_1 Current 2 on Wattmon_10				20190628
				~	11:35			Powering a cooling fan for W100 Test Setup (old starter switch for load connection to Trace)	WRD	W100 Test	L0	20190628
				S1-2 S6-7	IMG			20190628
		29	Sa					Calibration of Wattmon_10 A1/Vin	AED WCX			20190629
		30	Su					Calibration of Wattmon_10 A1/Vin completed		Available	L	20190630
2019	Jul	6	Sa		11:02		13:02	2 Hr Equalization of B54 and B1 with BK_1 … / Equalization ended; BK_1 being used to monitor Load cable voltage	WRD WP4 WP5	W100 Test	L0	20190706
		8	Mo		06:10		06:40	30 Min Equalization of B54 and B1 with BK_1 …; Equalization ended; BK_1 being used to monitor Load cable voltage	WRD			20190708
				S1-2 S6-7	IMG			20190708
		9	Tu					Series test setup disassembled but BK_1 yet a part of it (not used for a couple of days)	WRD	Available	L	20190709
		11	Th					BK_1 being used to monitor Load cable voltage in W100 test setup	WRD WP5	W100 Test	L0	20190711
		14	Su		05:23		06:23	1 Hr Equalization of B54 with BK_1; Continued use to monitor Load cable voltage	WRD			20190714
				S1-2 S7	IMG			20190714
		17	We					Used to recalibrate C252_2; Continued use to monitor Load cable voltage	AED WCX			20190717
		28	Su		15:00		17:00	Equalization of B54 with BK_1; Continued use to monitor Load cable voltage (or to modify the voltage that Genasun and/or battery sees)	WRD			20190728
2019	Aug	4	Su	~	03:45	~	10:00	Set up BK_1 to provide a CC load of 5.100 Amps on 27TMX (B54); I was a little afraid to do this, as I don't know what the BK's Reverse Polarity specifications are / Contact request on website to BK Technical Support, case ID 35180 "What is the reverse polarity rating of the output when output is turned OFF?" and "For example, can the 9110 be used without being damaged to discharge a 12v battery at 5 amps Constant Current, by connecting the battery + to the negative - output and the battery - to the positive + output?" (EML response) / Tussled with schematic and determined the safest way to do this is (1) BK s/b ON before attaching (so it never sees reversed battery voltage), (2) use a power ballast resistor >3 ohms in series so that BK is regulating the current when the BK voltage is positive (for all possible values of battery, 10-15v) and (3) use a blocking diode capable of 5a / Set up ~3.25 ohm ballast (capable of ~85w, photos, parts of upper resistors reach ~300°F); All in series, Load Cable +, BK -, BK +, then ballast resistor back to Load Cable - / Discovered that a blocking diode is probably not needed to protect the BK, but the BK dissipates a lot of power when it is regulating current at or below 0v, and turning the BK OFF does NOT stop the current (neither would a diode) / "BK OFF" simply means no regulation, but current can still be flowing / We may not need the ballast resistor, but I can see from first principles that if the BK is regulating 5.1a with a positive voltage that I can't be hurting it (I'll wait for response from tech. support before I decide that issue) / BK does regulate at or below 0v, but I'm not sure how long and how hard I can push this before it might be damaged / Left it running while I went to rest; SSC scan of preliminary notes "CC DR Testing Equipment" from 8/2/19 (20190804 173325 Scan.jpg) / SSC scan of rough sketch schematic "DR Test #13 (5.100 Amps CC to 10.5v as per man'f specs.)" 8/4/19 (20190804 173745 Scan.jpg); WRD for more details	EML IMG SSC TW4-5 WRD			20190804
		5	Mo		11:10			Response from BK: 'Unfortunately this is not going to work with the 9110 or really any of our power supplies. The power supply can only push power out, not absorb power. Reversing the leads will connect some internal diodes across the terminals and they will not be long for this earth in that mode' followed with a sales pitch for their load units	EML			20190805
		6	Tu		20:46			Further questions for BK: 'Yes, I know about your load units. But you need to answer the first question I asked, which you've done only by saying "... some internal diodes across the terminals ... will not be long for this earth ..."' / 'What is the reverse polarity rating of the output?'; 'What size are these "internal diodes" and how much current, voltage or power will they tolerate before "giving up the ghost"?'				20190806
		8	Th		17:06			Response from BK: 'Unfortunately I cannot specify more than what is in the specifications. The DC Power Supply cannot be used in reverse and will fail if tried. My colleague pointed out another point, beyond the diodes there are electrolytic capacitors across the output that may explode if reverse biased. There are devices that can do what you want I think. Keithley makes an excellent unit I have used in the past that works in both sourcing and sinking capacities. https://www.tek.com/keithley-source-measure-units/keithley-smu-2400-series-sourcemeter'				20190808
		21	We		05:00		13:55	Charging Milwaukee Nicad A: No cool down needed, battery is ~22.5⁰C; 11.78v on BK w/o charge; Wattmon_9 to monitor temperature, sensor is on right side, charge current goes through RL1/2, Action 'T>28'; 20.00v/240mA, CC 12.4v climbing …; Exec T>28 but relay did not open (we need to implement double-taps); 8 Hrs 55 mins to when it should have shut off	W9	Applied		20190821
				14:16			T ~28.6⁰C; I manually switched off the charging (W9 Control Widget); 9 Hrs 16 Mins Charge; Modified Action 'T>28' for double-tap (2000ms delay between)		Available	L	20190821
2019	Sep	4	We		08:46		17:43	Charging Milwaukee Nicad B: No cool down needed, battery is ~22.4⁰C; 13.28v on BK w/o charge; Wattmon_9 to monitor temperature, sensor is on right side, charge current goes through RL1/2, Action 'T>28' / 20.00v/240mA, CC 13.7v climbing …; Exec T>28 (8 Hrs 57 Mins under charge)		Available		20190904
		5	Th	~	10:00	~	12:30	27 TMX (B54) removed from W100 Test Setup for delivery to RW: BK_1 used to show Genasun 13.2v battery …; Now being used to monitor W100 Load (and/or Equalize)	WP5	W100 Test	L0	20190905
		22	Su		07:55	~	08:20	I discovered that 6-pack was not being charged, totally dead, and Wattmon_9 and Wattmon_10 were not operating; Restored connection to Heathkit but charge current is of course only about 0.5 Amps; Attached BK_1 (13.8v/4.2a), now charging at about 3.5 amps ...; Decided to reduce current limit on BK to 2.1 Amps (in case one of the batteries is soaking up more than the others); Now charging CC (Heathkit OFF, W9 and W10 attached and running)	S1 W9 W10	6-Pack Charge		20190922
		25	We	~	05:15			6-pack charge current has finally dropped down to where the Heathkit may be able to handle it (560 mA, 13.8v, Fluke 13.65v); 6-pack on Heathkit	S1	Available	L	20190925
				05:30	~	14:15	Charging Milwaukee Nicad B (as above) …; Exec T>28 (8 Hrs 45 Mins under charge)	W9	Available		20190925
2019	Oct	5	Sa	~	08:52	~	10:52	Equalization B4-B7: BK 27.48 vdc; Equalization, 30.00/3.333; Liebert (T1) beep, silenced …; Equalization 2 Hours				20191005
2020	Mar	11	We		02:18			Charging Milwaukee Nicad A without W9 temperature sensing; Nicad sitting up on a tuna can; 20v/0.171amps (C/14); Running phone Timer for 20 hours …		Nicad A		20200311
		12	Th				02:50	24+ Hrs; 86°F max seen with IR T probe; 13.84v dropping slowly; Terminated charge		Available		20200312
				07:57			Charging Milwaukee Nicad B without W9 temperature sensing; Nicad sitting up on a tuna can; 20v/0.171amps (C/14); Running phone Timer for 20 hours …		Nicad B		20200312
		13	Fr				04:40	~21 Hrs; 84°F max seen with IR T probe; 16.62v dropping slowly; Terminated charge		Available		20200313
	May	22	Fr	~	04:30			27TMX initial charge	B57	Applied		20200522
		23	Sa			~	08:00	Removed from 27TMX		Available		20200523
				11:18			Charging Milwaukee Nicad A without W9 temperature sensing; Nicad sitting up on a tuna can; 20v/0.171amps (C/14); Running phone Timer for 20 hours …	WP5	Nicad A		20200523
		25	Mo				05:00	Nicad A removed from charge (88°F, ~41 hrs, I was gone camping with Marcus and Sharon); Charging Milwaukee Nicad B w/o W9 temperature sensing; Nicad sitting up on a tuna can; 20v/0.171amps (C/14); Phone Timer 20 hours …	WP5	Nicad B		20200525
		26	Tu				02:05	Nicad B removed from charge (~21 hrs)		Available		20200526
	Jun	11	Th	~	11:42			Started 27TMX initial charge	B58 WP7	Applied		20200611
		13	Sa	~	04:30	~	14:00	Removed from 27TMX, applied to Old Honda Battery …; Removed from B0	B0	Available		20200613
	Jul	7	Tu		04:08		23:43	Charging Milwaukee Nicad A as before …; Frozen	WP9	Applied		20200707
		8	We	~	23:50		14:06	Charging Milwaukee Nicad B as before …; Frozen		Available		20200708
	Nov	21	Sa					Equalization B4-B7: 30.00/3.333; 2 Hours	B4-B7			20201121
	Dec	17	Th	~	04:45			Initial individual charges of (6) 27TMX for RHS ...	B62-B67	Applied		20201217
		19	Sa					... parallel finishing charges of (6) ...	L5 IMG			20201219
		20	Su					... parallel Equalization charge of (6); Float ...				20201220
2021	Jan	4	Mo					Removed from floating B62-B67; Used with MW_1 to float (6) in series (81.0v total)...	S13 B62-B67			20210104
		5	Tu	~	04:00	~	05:30	Attempted to reach Equalization (16.2x6=97.2v) by raising BK_1 (S2) voltage but after 1.5 hours made it only to 95.9-96.0v total; Returned to Float (MW_1 set 48.6v, BK_1 set 32.4v)	L5 B62-B67 S13			20210105
		8	Fr	~	07:50			Removed from floating B62-B67 (in series with MW_1)	L5 IMG	Available		20210108
		12	Tu					Equalization B4-B7: 30.00/3.333; 2 Hours; NOTE Use 29.8v next time, as there was a Liebert A3 Error for overvoltage / Photos of PC_1, PS700_2, BK_1 and B4-B7; Photos also include TurboNet/RHS project with B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	B4-B7 IMG			20210112
		16	Sa					S1-2 S15-16	IMG			20210116
	Jun	26	Sa					Equalization B4-B7: 29.80/3.355, clip leads; 2 Hours	B4-B7			20210626
	Nov	13	Sa					S1-2	IMG			20211113
		14	Su	~	00:13	~	00:22					20211114
	Dec	25	Sa					Equalization B4-B7 (2h): 30.50/3.278 (BK Preset A, clip leads); NOTE Bypass A3 and A4 and turn them off for slightly more charge current	B4-B7 A3/4			20211225
				Equalization B8/B11 (2h): 17.10/5.100 (BK Preset B, clip leads); NOTE Trace must be unplugged and inverter turned off	B8/B11 BC1			20211225
2022	May	26	Th	~	10:00	~	19:15	S1-2	T48S S1 B0	Applied		20220526
		27	Fr					B0 is warm, ~33⁰C, right side ~40⁰C (Fluke IRT); BK output ~2.2a; B0 has a shorted cell, to prolong life set BK 13.40v	T48S B0			20220527
	Jun	11	Sa					S1-2: BK removed from B0; Applied to jump start BC8 Schauer for BTS testing, set 12.00v/5.100a, T1 UPS	T48S B0 BC7 BC8			20220611
		16	Th					Proof of Principle tests of Traco and ~54v power supply on output: BK as "Battery" set 20.00v/5.00a (100w maximum) / But BK doesn't have enough current to kick Traco into operation with 85w load, so removed from test setup (Traco input replaced with T-105s on floor); 20220616 1714 IMG_2597 PSE.jpg	T48-3 IMG L17	Available		20220616
		29	We					B58 Float maintenance (while in Colorado and after return): Solid #12 connection, set 13.50v/5.100a	TM22 B58	Applied		20220629
	Aug	1	Mo	~	13:42	~	15:42	Equalization B4-B7 (2h): 29.2v/3.424a (solid #12 Red/Blk connection, A3 and A4 bypassed and off)	B4-B7 A3/4			20220801
		2	Tu	~	20:00			B58 Float maintenance: Solid #12 connection, set 13.57v/5.1a (B58 on bench ~22-23⁰C)	B58			20220802
	Sep	17	Sa					S1-2 S13	T48-3 IMG	Available		20220917
	Oct	5	We					[S2/17] W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 IMG WP11			20221005
2023	Jan	13	Fr					R&D TODO: Voltage Reference Calibrations; W150 Full Environmental Testing (WP13)	DWP WP13			20230113
	Feb	6	Mo					Completed ITECH/Fluke/BK/Micronta Cross Calibration Checks: 20230205 ITECH-Fluke-BK-Micronta Cross Calibration Checks.ods sheet 20230206 Analysis / Labels applied to Fluke, BK and Micronta; Micronta graph printed for field meter case	DRD DBD LBX SSC Z17			20230206

## S3
Supplies: S3	A					DE_1: Delta Electronics PMT-24V150W1AA

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer or UPS
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2018	Feb	27					Ordered from Mouser Electronics	TW2-3 MOU EML	On Order			20180227
	Mar	2					Received	MOU TW2-3	Available	L		20180302
		5					S2-3	IMG	Applied	L0	WP2	20180305
		11					W100 Testing concluded (replaced with 200W Delta)	WRD	Available	L	-	20180311
	May	12	Sa					Man'f label (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC); Downloads 20180512 Datasheet_pmt-24v150w1aa-774709.pdf, 20180512 Manual_pmt-24v150w1aa.pdf; Inventory sticker applied	IMG LIB				20180512
2019	May	16	Th					Corrected inventory sticker applied (name changed D_1 --> DE_1); "CAUTION! 120VAC" [yellow] sticker applied / Adjusted output no load 27.0 vdc Fluke; Installed to help float charge B4-B7 on CP_1 (network UPS, which floats at ~27.2vdc)	B4-B7	Applied		A1	20190516
				UPS CP_1 (A1) removed and discarded (too damaged to fix); Batteries are floating on DE_1 (S3)				-	20190516
				~	23:45			UPS PC_1 (A4) in parallel, which has a float of 27.3 to 27.4vdc (therefore Delta is idle when batteries are fully charged)				A4	20190516
		17	Fr	~	05:00			In parallel with PS700_2 (A3) and PC_1 (A4): both the Liebert and the PowerCom have a slightly higher float voltage, therefore Delta is idle when batteries are fully charged				A3 & A4	20190517
				06:10		06:40	Simulated power failure test with near maximum loads on Liebert and PowerCom (T400s/T450s, monitors, emergency lights, Trace/SAPS in Subaru, anything I could easily set up, kept it going) / Tried to turn on JAK2, but PowerCom cannot handle JAK2 starting up with everything else on / Turned off some unessential stuff to try starting JAK2 again, but PowerCom cannot handle JAK2 startup (it probably would handle JAK2 except for the inrush power, which is greater than the ~155 watts I see when it is up and running)... / At 30 minutes 24.5vdc, Liebert says ~75% battery remains (3 bars out of 4, but it said this a few minutes after starting the test), very slight "hot" smell but probably just dust/dirt on the heat sinks / Estimated <5% of battery capacity used; Power restored					20190517
		18	Sa					[S3-5] Reviewed this history sheet and entries are up to date					20190518
		23					Network UPSs on high shelf in rear room: PowerCom, Liebert, Delta, Trojan T-105s	IMG				20190523
2021	Jan	12	Tu					Removed from batteries for network UPSs --> stock	B4-B7	Available		-	20210112

## S4
Supplies: S4	A					DE_2: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L	WP2
2018	Feb	27					Downloads 20180227 Datasheet_pmt-24v200w1am-774744.pdf, 20180227 news_delta-pmt-panel-mount-power-supply-series-is-now-available-in-12v-350w.pdf	LIB				20180227
	Mar	5					Ordered from Mouser Electronics / Download 20180305 Datasheet_pmt-24v200w1am.pdf	EML MOU LIB	On Order			20180305
		7	We					FedEx tracking says "delivered" but it isn't here yet; Contacted FedEx	MOU EML	Lost Shipment			20180307
		8	Th					Called Mouser and explained the problem	MOU				20180308
		9	Fr					Mouser ordered another one at no charge (DE_3, S5)	MOU EML S5				20180309
		11	Su					Received; Photos of FedEx lost box	MOU IMG	Available	L0		20180311
		13					S2/4	IMG	W100 Testing		WP2	20180313
		15					S1-2 S4					20180315
		20					S2/4					20180320
	Apr	2		~	15:15				IMG WRD EML	DR Testing			20180402
	May	8					Finished product photos (L0, W100_1, DE_2, Genasun_3) / Photos and video at WWT (W100_1, DE_2, Genasun_3, 20160421_2/4, 20160421_3/4)		Sold	L6		20180508
2019	May	18					S3-5					20190518
2022	Jun	28	Tu	~	15:15	~	16:30	Onsite at WWT: WP2 (W100_1) removed to take to shop	TM22		Subaru	WP2	20220628
		30	Th					W100_1 boxed, labeled and on North bench			L		20220630

## S5
Supplies: S5	A					DE_3: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L1	WP3
2018	Mar	9	Fr					Mouser ordered another one at no charge to replace "Lost Shipment" / See DE_2	MOU EML S4	On Order			20180309
		13					Received	MOU	Available	L		20180313
	May	7					W100_2 ordered by TurboNet; Slated for W100_2	TW2-3			WP3	20180507
		12	Sa					Man'f label (Bench, BK_1, TS_1, DE_1, DE_3, BTJ_1, ENC)	IMG				20180512
	Jul	27	Fr					Inventory sticker					20180727
	Aug	5	Su					Assembled into W100_2 (WP3)		Applied	L0		20180805
		13	Mo					Finished product photos; Installed at RW	IMG	Sold	L1		20180813
2019	May	18					S3-5

## S6
Supplies: S6	A					DE_4: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L7	WP4
2019	Jun	12	We					[S6-7] DigiKey order	EML TW4-5	On Order		WP4	20190612
		14	Fr					[S6-7] Received	TW4-5	Assembly	L0		20190614
		18	Tu					[S6-7] 2 partially assembled W100 units side by side	IMG	Applied			20190618
		28	Fr					S1-2 S6-7					20190628
	Jul	8					20190708
		9			12:45	~	17:25	Installed at Odessa		Sold	L7		20190709

## S7
Supplies: S7	A					DE_5: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L10	WP5
2019	Jun	12	We					S6-7	EML TW4-5	On Order		WP5	20190612
		14	Fr					TW4-5	Assembly	L0		20190614
		18	Tu					IMG	Applied			20190618
		28	Fr					S1-2 S6-7					20190628
	Jul	8					20190708
		14					S1-2 S7					20190714
		17					S1/7					20190717
2020	May	8	Fr		10:00		13:45	Travel, onsite in Lexington, AB and USB deposits; Plans are to install W100/B56 at LWT next week (kept in Subaru for now); Rec'd $690 payment	WP5	Sold	Subaru		20200508
		22	Fr	~	14:00			Installed at LWT	TW4-5		L10	WP5	20200522

## S8
Supplies: S8	A					DE_6: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L11	WP6
2020	May	26	Tu					[S8-12] Ordered	EML	On Order			20200526
		29	Fr					[S8-12] Received	TW6-10	Available	L0		20200529
	Jun	5	Fr					[S8-12] WISPer		Assembly…		WP6	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP6				20200612
		15	Mo					[S8-12] Assembly completed	WP6-10A	Float	L		20200615
		16	Tu	~	10:30	~	11:00	Onsite at RWWT with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix); Rec’d $1450 TurboNet check	TW6-10	Sold	L11	WP6	20200616

## S9
Supplies: S9	A					DE_7: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L3	WP7
2020	May	26	Tu					S8-12	EML	On Order			20200526
		29	Fr					TW6-10	Available	L0		20200529
	Jun	5	Fr					Assembly…		WP7	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP7				20200612
		15	Mo					S8-12	WP6-10A	Float	L		20200615
		16	Tu	~	11:10	~	11:30	Onsite at RHST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L12	WP7	20200616
2021	Dec	16	Th	~	16:25	~	16:45	Onsite at RHST: Met Mark in parking lot and 27TMX to Subaru ...; Finished pulling W100 from RHST; B58 and WP7 to be installed at RCWT	TM21F SMS		Subaru		20211216
				~	17:20	~	19:15	Onsite at RCWT: Installed (see L3 for details)			L3	WP7	20211216

## S10
Supplies: S10	A					DE_8: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L13	WP8
2020	May	26	Tu					S8-12	EML	On Order			20200526
		29	Fr					TW6-10	Available	L0		20200529
	Jun	5	Fr					Assembly…		WP8	20200605
		12	Fr					Invoiced for delivery w/o Mo6/15	WP8				20200612
		15	Mo					S8-12	WP6-10A	Float	L		20200615
		16	Tu	~	11:50	~	12:35	Onsite at ST with Keith Jones: Installed W100 and battery; No load (Keith will return later to install and configure DC Netonix)	TW6-10	Sold	L13	WP8	20200616

## S11
Supplies: S11	A					DE_9: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L14	WP9
2020	May	26	Tu					S8-12	EML	On Order			20200526
		29	Fr					TW6-10	Available	L0		20200529
	Jun	5	Fr					Assembly…		WP9	20200605

		15	Mo					S8-12	WP6-10A	Float	L		20200615
	Jul	6	Mo	~	12:00			Installed at Odessa North Water Tower (ONWT) / Photos and videos TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb	TW6-10 IMG	Sold	L14	WP9	20200706

## S12
Supplies: S12	A					DE_10: Delta Electronics PMT-24V200W1AM

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L15	WP10
2020	May	26	Tu					S8-12	EML	On Order			20200526
		29	Fr					TW6-10	Available	L0		20200529
	Jun	5	Fr					Assembly…		WP10	20200605

		15	Mo					S8-12	WP6-10A	Float	L		20200615
	Aug	14	Fr	~	10:15	~	17:10	Onsite at New Tower [OT] 2x; Installed box, electrical service, WP10 and B61; Photos	IMG	Sold	L15	WP10	20200814

## S13
Supplies: S13	A					MW_1: Mean Well LRS-150F-48

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2020	Dec	29					[S13-14] Ordered from Mouser	EML MOU	On Order		20201229
2021	Jan	1					[S13-14] Received	MOU L5	Available	L0	20210101
		4		~	18:51	~	19:35	[S13-14] Tested on batteries for RHS: MW_2 and MW_3 in series, each set to 48.6v; Hiccups and very slowly rising voltage; After 44 mins stuck at ~87v (14.5v each); Supplies cannot be used to reach Equalization / MW_1 used with BK to float (6) in series	TA2 B62-B67 S2			20210104
		5	Tu	~	04:00	~	05:30	Attempted to reach Equalization (16.2x6=97.2v) by raising BK_1 (S2) voltage but after 1.5 hours made it only to 95.9-96.0v total; Returned to Float (MW_1 set 48.6v, BK_1 set 32.4v)	L5 B62-B67 S2			20210105
		8	Fr	~	07:50			Removed from floating B62-B67 (in series with BK_1)	L5	Available	L	20210108
2022	Feb	21	Mo					Preparations to go onsite for ONWT Emergency; MW_1 loaded into Subaru (unopened in box); Also brought cheater cord and hook up wire; Not needed/used at ONWT	TM22 L14			20220221
	Jun	16	Th					Proof of Principle tests of Traco and ~54v power supply on output: Cheater cord on L/N; Output connected with #18 solid to Traco output (~52.8v in parallel) / Although MW_1 specs say output maximum ~52.8v it can be adjusted above that; Set ~54.1v (TECH 85w); Seems to be plenty of adjustment room above that if desired; 20220616 1714 IMG_2597 PSE.jpg / Saw MW_1 output 180w but it won't start into that high a load, in fact, anything above 10w while the Traco is not up and MW_1 just hiccups; [Not a fair test, see notes added Mo6/20 to FTR and L17] / CONCLUSIONS: Either one of these two power supplies S13 and S14 may be more than adequate to cover the load range that the Traco can output (if Traco is up when they are powered up), and probably more than enough for LSWT (which is projected to be about 50w load on battery) / But it would be better to get 200w CC mode overload versions now for robustness and the future (to cover the entire Traco output range and start reliably in all situations up to 165w load with capacitance) / [See notes added Mo6/20 to FTR and L17, 200w may be needed but hiccup startup is OK into MikroTik/Mimosa loads which are mostly resistive at initial startup]	T48-3 IMG L17	Applied	L0	20220616
		20	Su					Experiments with ITECH Von and S13: S13 will start into ITECH 165w load if Von=10v, but not if Von=5v / S13 may be useable for LSWT and the future, ITECH 165w is 54.1vI @ 3.05aI which is not above the S13 current spec (3.3a) but slightly above the S13 power spec (158.4w) / 123degC Fluke IRT MAX after ~45m @ 165w; This is very hot and so S13 not suitable for a site that could go to 165w load, but AOK for LSWT; Removed load (idle on bench)	T48-3 L17			20220620
		28	Tu					Dismantled Proof of Principle test setup (MW_1 idled at various power levels since Th6/16)	T48-3 L17		L	20220628
	Aug	18	Th					[S13-14] Prep of Supplies/Chargers For LSWT and Spares: Fabricated L/N/G AC Plugs for BC9, S13 (LSWT) and (2) longer utility plugs for bench use, Load Supply - Wire Label 0.5 in.lbx / Adjusted for target 54.000vI, S13 achieved 53.995vI (ITECH Sense on output screws, CC 100mA, shop ambient); 54V Load Supply.lbx printed (to be applied to Wiegmann back plate) / S13 to be mounted on Wiegmann back plate for LSWT	T48-3 LBX L17	Sold	L0	20220818
		20	Sa					Dual Supply Bench Testing Setup Assembled: Wiegmann Back Panel on bench, S13 mounted with heat sink compound	T48-3 L17 IMG		L	20220820
		22	Mo					[S13-14] During bench testing, as an experiment: Output adjusted to 52.904vI (about 0.1v above 52.8v target for Tracos) / BUT Test of Dual Supply with Isolation at Traco Output fails; Back to R&D; New Design "Isolation at INPUT of Traco"; S13/14 48v supplies will not be used for LSWT and Dual Supply design	T48-3 L17	Available		20220822
		24	We					Tested Traco Maximum Power Limits in range 169-187w: During testing I adjusted S13 for target 54v with 100mA CC load (bench ambient), achieved 54.014vI	T48-3 L17			20220824
	Sep	3	Sa					Modified test setup to measure SCP-75-12 load regulation 0~105w: S13 unplugged; Continues slated to be returned to stock	T48-3 WP11			20220903
		17	Sa					S1-2 S13	T48-3 IMG			20220917
		18	Su					Disassembled Bench Test Setup and Wiegmann Backplate: Removed S13 and cleaned thermal grease; Returned to stock (boxed on N bench)	T48-3 PLN WP11			20220918

## S14
Supplies: S14	A					MW_2: Mean Well LRS-150F-48

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2020	Dec	29					S13-14	EML MOU	On Order		20201229
2021	Jan	1					MOU L5	Available	L0	20210101
		4		~	18:51	~	19:35		TA2 B62-B67 S2			20210104
		5	Tu					Boxed (will not be used for RHS)			L	20210105
2022	Aug	18	Th					S13-14; S14 adjustment achieved 54.002vI / S14 is slated for Spare for LSWT; Boxed on N bench	T48-3 LBX L17	Sold	L	20220818
		22	Mo					S13-14	T48-3 L17	Available		20220822

## S15
Supplies: S15	A					MW_3: Mean Well HRP-150N-48

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L5
2021	Jan	5					[S15-16] Ordered	EML MOU	On Order		20210105
		7					[S15-16] Received	MOU L5	Available	L0	20210107
		8	Fr	~	08:20	~	08:35	[S15-16] Tested on batteries for RHS: MW_3 and MW_4 in series, each set to 48.6v; Failed to reach Equalization (supplies are fighting each other)	L5 B62-B67	Testing		20210108
				~	09:07	~	09:38	[S15-16] Tested on batteries for RHS: MW_3 and MW_4 in series/parallel (middle of string tied between power supplies), each set to 48.6v; Failed to reach Equalization, ~89v maximum seen				20210108
				~	09:52	~	09:54	[S15-16] MW_3 and MW_4 set to 45.0v each (15.0x6=45.0x2=90.0), reached maximum 89.9v before quit				20210108
				~	10:01	~	10:06	[S15-16] 14.5x6=43.5x2=87.0 is OK, power supplies stop buzzing within a few seconds and it holds				20210108
				[S15-16] Tested turning them on while TrippLite is Float charging; 83.0->87.0v (causes no problems with TrippLite)	IMG			20210108
		11	Mo					[S15-16] Experimented with Equalization boost chargers on RHS batteries and TL3_7 TrippLite; See RHS L5 for details/conclusions	L5			20210111
		12	Tu					[S15-16] Photos of B62-B67, MW_3 and MW_4 in background of photos of network UPS setup in rear room	IMG			20210112
		16	Sa					S1-2 S15-16				20210116
2021	Feb	7	Su					[S15-16] Finished and attached the boost charger box assembly and tested Boost/Absorption for 3 hours to see how warm it gets / Highest temperature seen on front center of box ~102°F	L5 B62-B67 IMG	Applied	L	20210207
		24	We	~	12:15	~	17:00	[S15-16] Travel and onsite at RHS: Boost charger mounted to RHS fabricated battery box, which looks great; Photos	IMG TA2	Sold	L5	20210224
		25	Th	~	04:30	~	07:15	[S15-16] Onsite at RHS again to switch loads over to top UPS; Boost voltage is set too high, the bottom UPS went into OVP bypass beep and error / Adjusted boost down using Fluke, was 43.75v each supply, now 43.25 each supply (14.425 equivalent), 86.3v on Murata (battery bank sticker is wrong); Photos				20210225

## S16
Supplies: S16	A					MW_4: Mean Well HRP-150N-48

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L5
2021	Jan	5					S15-16	EML MOU	On Order		20210105
		7					MOU L5	Available	L0	20210107
		8	Fr	~	08:20	~	08:35		L5 B62-B67	Testing		20210108
				~	09:07	~	09:38					20210108
				~	09:52	~	09:54					20210108
				~	10:01	~	10:06					20210108
				IMG			20210108
		11	Mo					L5			20210111
		12	Tu					IMG			20210112
		16	Sa					S1-2 S15-16				20210116
2021	Feb	7	Su					S15-16	L5 B62-B67 IMG	Applied	L	20210207
		24	We	~	12:15	~	17:00		IMG TA2	Sold	L5	20210224
		25	Th	~	04:30	~	07:15					20210225

## S17
Supplies: S17	A					MW_5: Mean Well RSP-200-13.5

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L17	WP11
2022	Aug	22	Mo					Began research for the new design Dual Supply with Isolation at Traco INPUT for LSWT: In initial availability research for the Load Power Supply I looked briefly at the Mean Well RSP-200-13.5 $54.39 (5 in stock at DKE)	T48-3 L17	R&D			20220822
		25	Th					After firming up the desired specifications for the new design I looked again for a supply that could be set at about 13.5 to 14.7v and was brought back to the RSP-200-13.5 / DKE has 5 in stock, MOU is "Non-Stocked"; SPSE shows 5 in stock, and meanwell.com shows that it is not a discontinued product / I planned to order it and set it at 14.5v [Sa10/1 Design changed to 13.8v; Tu10/4 adjusted to 13.7v], it will be diode isolated from the Battery/Charger SCP-75-12, which at highest Float is 14.46v at -15⁰C/122⁰F	T48-3 L17	Selected			20220825
		27	Sa					Ordered from DigiKey along with diodes / Also ordered diode suppression relay from Mouser	T48-3 EML DKE MOU LIB L17	On Order			20220827
		30	Tu					"W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; This supply is slated for LSWT on WP11	T48-3 L17			WP11	20220830
		31	We					DigiKey and Mouser orders received (but not opened): / Load Supply, (2) diodes and a diode suppression relay	T48-3 DKE MOU SSC LIB	Available	L		20220831
	Sep	1	Th					Summary sheet entry completed, during which I discovered, saved and studied a Test Report for the new Load Supplies: Library > Mean Well > 20220901 RSP-200-13.5 Test Report.pdf / Very interesting report and helpful information for the new design; Labels applied Inventory Sticker 0.47.lbx; Also labeled diodes package (pen) and applied TurboNet Relay for Diode Suppression.lbx	T48-3 LIB LBX DKE MOU				20220901
		7	We					We have stock on metric screws for blind mounting of supplies: For the RSP-200-13.5 they should be M4x3 and we have many M4x6 bought for W100s, can use with washer(s)	T48-3			WP11	20220907
		19	Mo					Cardboard template made for visualization / brainstorming on backplate layout: Photo shows layout of BC9, S17, V11 and other components (mostly considered, will finalize later)	T48-3 IMG			WP11	20220919
		30	Fr					Parts Assembled Onto Backplate: Photos		Testing	L0	WP11	20220930
	Oct	1	Sa					TFTP RSP Load Supply s/b set 13.8v: Not 15.0v as planned earlier (I didn't take into account the diode drop); [RSP Load Supply set to 13.70vF on Tu10/4 when in testing at -15degC]	T48-3				20221001
		2	Su					Bench Testing Started (+25⁰C): As from factory 13.57vF with 150wI Traco load (AOK, spec is 13.5v ±1%); Output Setting Experiments, notes on diode bias for various settings; Adjusted to 13.80vF with 150wI Traco load	T48-3 PLN				20221002
		3	Mo					Bench Testing (-15⁰C): BC9 Tcomp estimate (during cooldown) -20.7mV/degC (it's looking like we can lower S17 set to 13.7v or 13.6v) / Burn-In Test Passed: W150_1 on bench, no fan, photo, 175wI Traco load, >15h, Z20 T1 48.2⁰C (between supplies above contactor, silver tape), T2 51.0⁰C (1/4"-20 foot bolt near label area, 5/16" lug)	T48-3 PLN IMG				20221003
		4	Tu					Bench Testing (stable at -15⁰C): Adjusted to 13.70vF, stable throughout range 0-150wI Traco load: Diode +0.608vM (BC9 float 14.30vF, no significant conduction seen with Extech)	T48-3 PLN	Sold	L		20221004
		5	We					S2/17	T48-3 IMG				20221005
		7	Fr					W150_1 Final Assembly and Invoice Date: Labels applied; [Invoice emailed to Keith and Mark Fr10/21]	T48-3 LBX			WP11	20221007
		8	Sa					Photos of W150_1: Product line and orthogonal photos	T48-3 IMG				20221008
		11	Tu					Loaded Subaru for onsite installation at LSWT	T48-3		Subaru		20221011
		21	Fr					Onsite at LSWT: Windy but warm; Photos; Installed B58 and WP11; Power levels measured, Traco Input 32.6w, Output 27.5w	T48-3 IMG		L17	WP11	20221021

## S18
Supplies: S18	A					MW_6: Mean Well RSP-200-13.5

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	WP12
2022	Nov	25	Fr					[S18-19] Production Run #1 Orders Completed: Ordered (2) Load Supplies for WP12-13; Also ordered a Diode and other parts needed for the run	T48-4 EML DKE	On Order		WP12	20221125
		29	Tu					[S18-19] Received (delivered by Fedex)	T48-4 DKE	Available	L0	WP12	20221129
	Dec	1	Th					[S18-19] Applied Inventory Sticker 0.47.lbx; Library scan Mean Well and Vishay > 20221125 DigiKey Invoice, Annotated; (2) Load Supplies, Diode, +; T48-4 (CFS) WP12-13 S18-19 (MW_6-7); 20221201 Scan_2pages.pdf	T48-4 LBX SSC LIB DKE		L	WP12	20221201
		13	Tu					WP12 Load Supply Configuration and Burn-In: As per WP12-13A; Target 13.700vI, achieved 13.712vI; Started 180wI (Traco output) Burn-In (hot smell, this is the 1st time these devices have seen full power since the factory)	T48-4 PLN	Burn-In		WP12	20221213
		14	We					WP12, as per WP12-13A: Configuration and Testing finished; Labels finished; Ready to be installed at CFS		Install	Subaru		20221214
		28	We		12:00		14:00	Onsite at CFS: Installed W150_2, vertical on left side of enclosure (side panel is removeable); Photos	T48-4 IMG	Applied	L18	WP12	20221228
2023	Jan	30	Mo					1st Production Run Completed: (WP13 Completed); WP12-13 Invoice Date	T48-4 WP13	Sold		WP12	20230130

## S19
Supplies: S19	A					MW_7: Mean Well RSP-200-13.5

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L	WP13
2022	Nov	25	Fr					S18-19	T48-4 EML DKE	On Order		WP13	20221125
		29	Tu					T48-4 DKE	Available	L0	WP13	20221129
	Dec	1	Th					T48-4 LBX SSC LIB DKE		L	WP13	20221201
2023	Jan	8	Su					As per WP12-13A Configuration and Testing: S19 Configured, achieved 13.729vI; Started 180wI Burn-In ...	T48-4 PLN	Testing	L0	WP13	20230108
		9	Mo					As per WP12-13A Configuration and Testing: S19/V13 Burn-In completed (16.2h)		Assembly	L		20230109
		30	Mo					1st Production Run Completed: WP13 Completed; WP12-13 Invoice Date	T48-4 LBX SSC	Sold		WP13	20230130
		31	Tu					Photo of WP13	T48-4 IMG				20230131

## S20
Supplies: S20	A					MW_8: Mean Well RSP-200-13.5

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	L	WP14
2023	Mar	8	We					[S20-21] Ordered; Supplier SPSE chosen because preferred suppliers DKE and MOU are out of stock	DWP SPSE	On Order		WP14	20230308
		10	Fr					[S20-21] Received		Available	L0	WP14	20230310
		11	Sa					[S20-21] Created and filled out Summary entries and History sheets; W150 Inventory Sticker 0.47.lbx / 20230308 Sager Invoice, Annotated; DWP WP14-15; (2) Load Supplies S20-21; 20230311 Scan.jpg	DWP LBX SSC LIB SPSE	Assembly	L		20230311

## S21
Supplies: S21	A					MW_9: Mean Well RSP-200-13.5

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	L	WP15
2023	Mar	8	We					S20-21	DWP SPSE	On Order		WP15	20230308
		10	Fr					Available	L0	WP15	20230310
		11	Sa					DWP LBX SSC LIB SPSE	Assembly	L		20230311

## U1
USBs: U1	A					USB_1: Huawei E303s-65 (3G Modem)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Jul	11					Ordered from eBay.com: advertised as "unlocked"	EML WCA	On Order			20150711
		23					Received: branded as "tigo"	WCA	Available	L		20150723
		24					Testing on T400s: SIM card from Samsung phone (Consumer Cellular); Installed Internet Movil Tigo (from E303); "The SIM card has not been detected or is invalid; Inconclusive results (more testing needed)	AED				20150724

## U2
USBs: U2	A					USB_2: Huawei E303F (3G Modem)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	-
2015	Sep	11					[U2-3] Ordered	EML WCA	On Order			20150911
		14					[U2-3] Received	WCA	Available	L		20150914
2017	Apr	1	Sa					Installed CC (Consumer Cellular) card, tested in T400s, CC card evidently not compatible	AED	Testing	L0		20170401
		2	Su					Tested in Wattmon_9 and then removed; Probably not working due to CC SIM card (removed), otherwise fine				W9	20170402
		7	Fr					Placed back in stock. There are cellular service providers that can provide a SIM, notably Ting, T-Mobile and AT&T (see AED 4/2/17 for research into 7 different carriers with data-only plans)		Available	L	-	20170407

## U3
USBs: U3	A					USB_3: Huawei E303F (3G Modem)

Date/Time CST/CDT					Description	Other Sources	Status	Location	Wattmon
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Sep	11					U2-3	EML WCA	On Order			20150911
		14					WCA	Available	L		20150914

## V1
Converters: V1	A					EPE_1: EDACPOWER ELEC. ED1075

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Apr	22					Ordered from PowerStream.com	EML	On Order		20150422
		24					Received; Slated for RW	TSP	Available	L	20150424
		?					Modified: Removed input connector, spliced input fuse and red (tinned) and black (ring connector) battery connections; Replaced output connector with one from the Ubiquiti switch (load)			L0	201504?
		30					Installed at RW; Photos of initial installation with Mark Webb and Keith Jones	IMG	Applied	L1	20150430
	?	?					Removed from RW (records are incomplete), needed repair (internal fuse)		Needs repair	L	2015MM?
	Jul	9					Repaired (Internal Fuse Removed) / Sticker applied		Spare	TurboNet Toolbag	20150709
2016	Jun	28					These records caught up		Spare for RN		20160628
2019	Jan	22	Tu					Onsite at RN: Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)	IMG			20190122
		29	Tu		13:15		14:30	Again onsite at RN: Prepped and left to meet Reason @ 13:30; Replaced converter, but old one was 24.6v and new one 24.5v …; Returned to shop		Sold	L2	20190129
2020	Aug	11	Tu	~	12:05	~	13:45	Onsite at RN with Keith; Ubiquiti Tough Switch removed and replaced with DC Netonix; Converter brought back to shop [technically it belongs to Swafford, but I don't think they care]	L2	Available	L	20200811

## V2
Converters: V2	A					EPE_2: EDACPOWER ELEC. ED1075

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Input Cut	L
2015	May	4					Ordered from PowerStream.com	EML	On Order		20150504
		6					Received; Slated as Spare for RW	TSP	Available	L	20150506
		31					Modified: Removed input connector, spliced input fuse and red (tinned) and black (ring connector) battery connections; Photo on bench	IMG		L0	20150531
	Jul	6					Installed at RW [records are incomplete, but sometime before July 9th, when unit #1 was at the shop and was repaired]		Applied	L1	20150706
	Sep	3					Onsite at RW with Juliya				20150903
		16					Onsite at RW with Juliya (Sasha's iPhone)				20150916
2016	Mar	16					Onsite at RW (to install web relay)				20160316
	Apr	19					Removed from RW (negative input lead cut off)		Input Cut	L	20160419
	Jun	29					These records caught up				20160629

## V3
Converters: V3	A					PS_1: PowerStream SR700-24

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Returned	-
2015	May	16					Ordered from PowerStream.com: $159.00 + $16.20 S&H	EML	On Order		20150516
		23					Received (estimated date)	TSP	Available	L0	20150523
		31					RMA requested	EML		L	20150531
	Jun	16					Returned (USPS, $12.62), refund pending		Returned	-	20150616
	Jul	22					Refund settled ($135.15 total credit)	EML			20150722

## V4
Converters: V4	A					PS_2: PowerStream NBPSU150

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Returned	-
2015	May	22					Ordered from PowerStream.com: $49.00 + $64.00 S&H	EML	On Order		20150522
		29					Received (estimated date)	TSP	Available	L0	20150529
	Jul	13					RMA Requested	EML		L	20150713
		25					Returned (USPS, $7.68), refund pending		Returned	-	20150725
	Aug	19					Refund settled ($41.99 total credit)	EML			20150819

## V5
Converters: V5	A					SPS_1: SuperPowerSupply.com Car Charger

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	SAPS Box
2015	Aug	16					Ordered from eBay ($6.39)	EML	On Order		20150816
		20					Received		Available	L0	20150820
				Not happy, complained, $6.39 credit received	EML		L	20150820
2018	Jun	9					This sheet completed			SAPS Box	20180609

## V6
Converters: V6	A					PS_3: PowerStream DC2012

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	30					Ordered from PowerStream: $89.00 + $6.15 S&H	EML	On Order		20150830
	Sep	4					Received		Available	L0	20150904
2018	Jun	9					This sheet created; Was located in SAPS Box, brought to bench for consideration of use in Mini SAPS	MA2	Mini SAPS?		20180609
		15	Fr					Downloads 20180615 PowerStream DC2012.pdf; 20180615 Vicor (PowerStream DC2012) designguide-vi.pdf; 20180615 PowerStream Vicor VI-J01-CY.pdf	LIB	Testing		20180615
				Bench testing: 12v input; Quescient current is 8mA (0.1 watts); With output powered off 4mA (0.05 watts) / PowerStream says it is Over Temperature Protected; ~36 watt load (~72% of max) temperature of plate is 86°F (after 1-2 hrs) (but body is much hotter than this, 120°F maybe) / Conclusion: suitable for use in Mini SAPS, don't need a kill switch, don't need a heatsink (although if run close to maximum it can get quite warm)	MA2	Available		20180615
		29	Fr					Bench testing I8O8_1 power and TEC_1/2 latching relays		Assembly	MA2	20180629
2020	May	30					Bench cleaned and parts for assembly boxed with labels “MA2”	MA2			20200530

## V8
Converters: V8	A					EPE_3: EDACPOWER ELEC. ED1075

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Parts	L
2015	Sep	10					Ordered from PowerStream.com	EML	On Order		20150910
		14					Received; Slated for RN	TSP	Available	L	20150914
		?					Modified: Removed input connector, spliced input fuse and red (tinned) and black (ring connector) battery connections				201509?
		19					Approximate date of installation at RN		Applied	L2	20150919
2016	Mar	16					Onsite at RN (to install web relay)	IMG			20160316
	Jun	29					These records caught up				20160629
	Jul	16	Sa					Spare fuse silver taped to cord (2 Amp fast)	IMG	Sold		20160716
2019	Jan	22	Tu					Onsite at RN: Replaced Ubiquiti switch with spare; Converter assumed to be OK				20190122
		29	Tu		13:15		14:30	Prepped and left to meet Reason @ 13:30; Replaced converter, but old one was 24.6v and new one 24.5v …; Returned to shop		Defective?	L0	20190129
				14:30		15:00	Converter bench tested and proved to be defective (1A load causes it to shut off); See white paper notes	TSP	Defective		20190129
	Mar	28	Th					Converter opened and examined for defects: I couldn't spot anything, no burnt Rs, electrolytics tested as OK using Cap Wizard; Labeled and saved for parts		Parts	L	20190328

## V9
Converters: V9	A					TP_1: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L14
2021	Aug	18					I discovered the Traco Power line of DC-DC converters during research for the MikroTik project (48v Systems for TurboNet); At first I looked at the TEP 100CM Series, but I could not find a supplier with stock	T48P LIB	Research			20210818
		19					I called Traco Power North America 408-916-4570: No distributors anywhere have stock on the TEP 100-1218-CM or -CMF	T48P				20210819
		20					I found stock at Mouser on 3 other suitable units for the TurboNet MikroTik application: TEP 75-2418WI-CM $171.70 (2 in stock); TEQ 100-2418WIR $367.30 (1 in stock); TEP 150-2418WI $218.30 (13 in stock); Downloaded datasheets for the 75w units	T48P LIB				20210820
		21					Datasheet, Overview and Application Notes for the TEP 150WI series					20210821
	Sep	22					Lexington meeting with Keith and Mark; Discussed "Tower Power Considerations" drawing where I introduced the idea of running just fiber and a power cable for ~48v to the top of the tower / Rec'd $2600 advance on pilot project; TP_1 is slated for ONWT	T48P TPC1 TEDS TOI				20210922
		23					Quote sent to TurboNet: The 150-2418WI Traco is listed as $365 (also see Listed Items Price Calculator.ods)	DBT				20210923
	Oct	7					White sheet notes "Traco TEP 150-xx18WI Output Voltage Adjustment (thought about using 10-turn pot but settled on using discrete resistor); TP_1 ordered from DigiKey, with fuses and in-line fuse holders	T48P DKE WS	On Order			20211007
		11					DigiKey order received: 20211007 DigiKey Invoice V9 (TP_1) Scan.jpg	DKE LIB	Available	L0		20211011
	Nov	8					Inventory sticker; Input cabling fabricated, #14 AWG stranded 24" black, 14.25" red + 9.75" #12 (25a inline fuse, butt splice), 5/16" ring connectors made for #10-12 / Estimated <0.235v drop for 48" of #14 @ 22.6a (typical Under Voltage Lockout is 8.2v, #14 is 2.6mohm/ft) / I could improve the bottom end performance slightly by parallel connections of 2x#14 for both positive and negative: / But this would increase the assembly time and I don't think it is necessary because if we're running a 150w load the battery capacity is mostly limited by the battery's internal resistance, and this small extra drop will make only a very short run-time difference, probably minutes, because when we get down to 9vdc the battery resistance is shooting up rapidly / Output cabling fabricated, 7" of the #16 stranded Red/Black Bonded Zip Cord that I had bought for the W50 project (Powerwerx Wire-RB-16-25), tinned ends on Traco end, but not on the wire nut end (where the Power Cable and MikroTik adapter cutoff are to be attached) / The yellow Ideal #30-451J wire nuts should be fine for at the bottom of the tower, but they may be too big for the top of the tower (depends on MikroTik adapter cable AWG, and they haven't given me one yet, and whether or not they use more than one PowerBox Pro)	T48P	Assembly			20211108
		9					Fabricated trim resistor to boost output +10% to ~52.8v: 1/4w metal film resistors, 15.0 Kohm + 220 ohm = 15.22 Kohm					20211109
				BK for input, no trim resistor: With no fuse the inline fuse holder indicator works great (very bright at 24v, dims slightly at 9v); 9.00vB, 0.120aB, 47.9vF (1.1w); 13.50vB, 0.111aB, 47.9vF (1.5w) / 24.00vB, 0.113aB, 47.9vF (2.7w); Under Voltage Lockout <8.1v and restores >8.6v; All according to specifications		Testing			20211109
				BK for input, with trim resistor: 13.50vB, 0.112aB: 52.7vF, 52.8vM					20211109
				BK for input, set 13.50v, 5.1a max, 250w bulb as load on Traco: 8.57vB, 5.100aB (~44w): 33.6vM; BK can't put up enough input current; Traco is probably oscillating at Under Voltage Lockout					20211109
				~	10:51	T-105s for input, 250w bulb as load on Traco: Input 13.48vF, 6.00aW (81wW); Output 52.8vM, 1.38aE (72.9w, 49% of rated power); 90% efficiency (specifications Efficiency vs. Output Current chart agrees) ... / 46⁰C (Fluke IRT MAX)					20211109
				Sticker applied for set point: "11/9/21 Output set: 52.8v (+10%, 15.22 KΩ)"; Slated for ONWT	T48P IMG	Ready			20211109
		10				~	06:03	49⁰C (Fluke IRT MAX); Removed from test	T48P				20211110
		13	Sa					Detail photos of assembly	IMG				20211113
				Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup					20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)					20211114
		20	Sa	~	03:30			Removed from test bench for mounting to backplate of Mier enclosure	TOI		L		20211120
		23	Tu	~	12:20	~	15:40	Onsite at ONWT with Mark, Keith, Dakota and ?; Installed Mier enclosure with Schauer, T-105s, Traco and Dinico fan control system; WP9 and B60 are still Active; Keith saw 52.4v on 2 of 3 PBPs at the top		Sold	L14		20211123
2022	Feb	19	Sa					Mimosas stopped working; Keith onsite; He did not have a meter and so he didn't know if the Traco was working	TM22 SMS		L14		20220219
		21	Mo	~	09:45	~	11:10	Onsite at ONWT with Keith and Dakota: Traco output 52.9vM (~52.8vF), ~1.42aE (~75w) with MikroTik, ~1.07aE (~56w to top of tower) with MikroTik unplugged / Power cable disconnected/reconnected and PBPs came online, reporting 50.0-49.9-50.0v; I briefly showed Dakota and Keith how to use their meter (reads slightly low, 52.5v=52.9vM)	TM22		L14		20220221
				~	11:10	~	14:00	Onsite at ONWT Alone (after Keith departed): Power Level Measurements and Estimates, Traco efficiency loss measured is in good agreement with specifications (88.2% measured, spec is 86% at full load); Many photos	TM22 IMG				20220221
		22	Tu	~	12:55	~	13:40	Call to Keith 45m, discussing his onsite visit Sa2/19: Agreed again we need a web relay (and switch) on the Traco output	TM22		L14		20220222
				~	18:53	~	18:59	Mark called 6m: ONWT is down again					20220222
		23	We	~	09:37	~	09:41	Mark called 4m: Last night Mark was on onsite, he cycled the Traco output power (wire nuts) and this did not bring the Mimosas back up					20220223
				~	12:46	~	12:48	Angry call from Keith: "Guys are at Odessa now, all the wire nuts are off, Schauer is off, and I'm still seeing power to the PBPs" / I asked if they have any ethernet or other cables running to the PBPs, "NO, just the fiber from the Netonix to the PBP"; I asked what the PBPs are seeing for voltage and he got angry, cussed at me and hung up					20220223
		25	Fr	~	10:04	~	10:18	Called Mark: ... "They tried to undo the power to them, which is weird because they wouldn't go off"; Take all information from Mark "with a grain of salt"					20220225

## V10
Converters: V10	A					TP_2: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L10
2021	Nov	11	Th					[V10-11] Keith was here to plan the ONWT Power Cable Assembly / During "show and tell" we discussed concerns that we have no emergency spares for the Schauer and Traco units being prepared for ONWT; Verbal order for (2) each Schauers and Tracos	T48S	Sales			20211111
		15	Mo					[V10-11] 20211115 Quote - Spare Parts for ONWT and Future.pdf emailed to Mark, Keith and Brad; Quoted Schauers, Tracos, Dinicos and reversing relays (fan control system) / Mark promised $1720 check ASAP	T48S DBT EML SMS	Quoted			20211115
		16	Tu					[V10-11] Received $1,720 Check	TM48S	Advanced			20211116
		17	We					[V10-11] Ordered from DigiKey; Shipped / 20211117 DigiKey Invoice V10 V11 (TP_2 TP_3) Scan.jpg	TM48S EML LIB DKE	Shipped			20211117
		19	We					[V10-11] Received	TM48S	Prep	L		20211119
	Dec	10	Fr					[V10-11] (Schauer chargers and Schauer invoice received); All the spares have been received; TurboNet Invoice Date (although spares have not been prepared yet)					20211210
2022	Jan	2	Su					[V10-11] 20211210 Invoice - Spare Parts for ONWT and Future.pdf; 20220102 Email to Mark, Keith & Brad 'Invoice - Spare Parts for ON & Future (MikroTik 48v Systems)'.pdf	TM48S DBT EML				20220102
	Feb	21	Mo					[V10-11] Preparations to go onsite for ONWT Emergency; TP_2 and TP_3 loaded into Subaru (unopened in box); Also brought 25a fuses; Not needed/used at ONWT	TM22 L14				20220221
	Mar	6	Su					[V10-11] Inventory Sticker 0.47.lbx applied; Invoice fully notated 20211117 DigiKey Invoice V10 V11 (TP_2 TP_3) Scan.jpg	T48S LBX LIB				20220306
	Apr	14	Th					Tracos V10 and V11 Stock Fabrication COMPLETED as per LIPC: Fabricated trimming resistor assemblies; Verified outputs (~30m burn-in, 85w, 52.627vI), 20220414 0640 IMG_2491.JPG / Stickers applied for set points Traco (date) Output Set.lbx; V10 will be assembled immediately for LWT (input/output cabling)	T48s LIPC IMG LBX Z17	Sold	L0		20220414
				Cabling battery to Traco: #14 stranded 36" black, 26.25" red + 9.75" inline fuse at battery end; Did NOT tin the ends; 5/16" ring connectors, shrink; Zip tie near Traco; Fuse installed, spare fuse applied w/silver tape / Cabling for output to MikroTik and Belden Power Cable: #16 stranded red/black zip cord, 12"; Tin Traco end only; Zip tie near Traco; Yellow wire nuts for field application of MikroTik adapter and Belden Power Cable / MikroTik adapter plug cut long (delivered by TurboNet We3/23): Tip is positive (+); Stripped/tinned and polarity indicated by red zip tie; ~7' long / Tested w/BK and ITECH (see T48S for earlier test w/o cabling for LWT)	T48-2	Assembly			20220414
				Prep to go onsite at LWT: Set aside what is needed to drill and mount Traco to inside of metal cabinet; Subaru loaded	T48-2 L10	Ready	Subaru		20220414
				~	10:55	~	15:25	Onsite with Keith, Dakota and Cole: Discussion with Keith; W100 mounted on left wall under shelf; Traco installed on right wall under shelf; Traco input 0.12aE (idle, output not connected, ~1.8w)	T48-2 IMG	Sold	L10		20220414

## V11
Converters: V11	A					TP_3: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L17	WP11
2021	Nov	11	Th					V10-11	T48S	Sales			20211111
		15	Mo					T48S DBT EML SMS	Quoted			20211115
		16	Tu					TM48S	Advanced			20211116
		17	We					TM48S EML LIB DKE	Shipped			20211117
		19	We					TM48S	Prep	L		20211119
	Dec	10	Fr					20211210
2022	Jan	2	Su					TM48S DBT EML				20220102
	Feb	21	Mo					TM22 L14				20220221
	Mar	6	Su					T48S LBX LIB				20220306
	Apr	14	Th					Tracos V10 and V11 Stock Fabrication COMPLETED as per LIPC: Fabricated trimming resistor assemblies; Verified outputs (~30m burn-in, 85w, 52.742vI), 20220414 0640 IMG_2491.JPG / Stickers applied for set points Traco (date) Output Set.lbx; Resistor removed, in box with 2x fuses labeled as "Prepped 4/14/22" and "Slated for Spare"	T48s LIPC IMG LBX Z17	Sold			20220414
	Jun	16	Th					Proof of Principle tests of Traco and ~54v power supply on output: Removed from box, resistor attached; Output #18 solid to S13 output (parallel) / Input BK (clip leads): Not enough current to kick Traco into operation with 85w load when S13 turned OFF / Next attached Traco input to T-105s on floor (clip leads, double length): T-105s can kick Traco into operation with 85w load, but anything more than that and Traco won't start (high resistance in clip leads) / Traco idle power when S13 is supplying the load: 0.03-0.05aE (0.4~0.7w) (13.5~14.5v ENC Float~Absorption); 20220616 1714 IMG_2597 PSE.jpg	T48-3 IMG L17	R&D	L0		20220616
		28	Tu					Dismantled Proof of Principle test setup (TP_3 idled at various power levels since Th6/16)	T48-3 L17		L		20220628
	Aug	20	Sa					Dual Supply Bench Testing Setup Assembled: Wiegmann Back Panel on bench, V11 mounted with heat sink compound / Fabricated cabling battery to Traco, two attempts, 1st attempt kept for utility use on bench, see FTR for details and IMPORTANT NOTES; Photos of how not to do it and 2nd successful attempt / [2nd attempt was very nice, but it also will be set aside for Mo8/22 new design for isolation at input of Traco]	T48-3 IMG L17	Assembly			20220820
		22	Mo					Bench Testing: Problems discovered immediately; By varying ITECH Von Living settings I was able to determine that the Traco transition from idle (Load Supply) to battery drops the output below 5v (120w load) / Experimented with capacitance on load and setting S13 output closer to V11 output (no improvements); Paradigm shift, back to R&D, new design "Isolation at INPUT of Traco"	T48-3 L17	R&D			20220822
		24	We					Tested Traco Maximum Power Limits in range 169-187w: 175w is a very safe limit close to the Traco specification of "105% of Iout" (3.36a, 52.8v, 177.4w); At 175w we need ~206w at Traco input (observed, measured); / 175wIS: 52.771vI; 3.313aI; 174.82wIR; Battery 12.54vF; Traco Input 16.40aE (205.7w); Various TFTP including "LSWT must use isolation at Traco INPUT and relay/diode design"	T48-3 L17				20220824
		30	Tu					"W150" Product Line is Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; This converter is slated for LSWT on WP11	T48-3 L17			WP11	20220830
	Sep	3	Sa					Modified test setup to measure SCP-75-12 load regulation 0~105w: Disconnected V11 from battery (it has been idling for days)	T48-3			WP11	20220903
		17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG				20220917
		18	Su					Disassembled Bench Test Setup and Wiegmann Backplate: Removed V11 and cleaned thermal grease	T48-3 PLN			WP11	20220918
		19	Mo					Cardboard template made for visualization / brainstorming on backplate layout: Photo shows layout of BC9, S17, V11 and other components (mostly considered, will finalize later)	T48-3 IMG			WP11	20220919
		30	Fr					Parts Assembled Onto Backplate: Photos		Assembly		WP11	20220930
	Oct	2	Su					Point to Point Wiring and Cabling FINISHED; Assembly FINISHED (minus labels): Wiring Details for Assembly Parts List (Traco Outputs) / Bench Testing Started (+25⁰C): Proof of Principle Tests Passed, Transitions OK (150wI and 175wI Traco load, Von Living 0.00v); It works as I had hoped / Started overnight BURN-IN test (175wI load on Traco) ...	T48-3 PLN	R&D		WP11	20221002
		3	Mo					Bench Testing (-15⁰C), Burn-In Test Passed: W150_1 on bench, no fan, photo, 175wI Traco load, >15h, Z20 T1 48.2⁰C (between supplies above contactor, silver tape), T2 51.0⁰C (1/4"-20 foot bolt near label area, 5/16" lug)	T48-3 PLN IMG				20221003
		4	Tu					Bench Testing (stable at -15⁰C): Multiple AC OFF/ON Transition Tests at 180wI Traco load during very deep discharge to Traco low voltage cutout (8.2v) / Recovery while heating to +50⁰C: 180wI Traco output; Highest backplate temperatures seen Z20 T1 61.5⁰C, T2 57.2⁰C	T48-3 PLN				20221004
		5	We					W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 IMG				20221005
		7	Fr					W150_1 Final Assembly and Invoice Date: Labels applied; [Invoice emailed to Keith and Mark Fr10/21]	T48-3 LBX	Ready		WP11	20221007
		8	Sa					Photos of W150_1: Product line and orthogonal photos	T48-3 IMG				20221008
		11	Tu					Loaded Subaru for onsite installation at LSWT	T48-3		Subaru		20221011
		21	Fr					Onsite at LSWT: Windy but warm; Photos; Installed B58 and WP11; Power levels measured, Traco Input 32.6w, Output 27.5w (Traco efficiency 84%)	T48-3 IMG	Sold	L17	WP11	20221021

## V12
Converters: V12	A					TP_4: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	WP12
2022	Oct	14	Fr					[V12-16] / Ordered (5) Tracos from Sager (WP12-16)	T48-4 SPSE SSC EML	On Order		WP12	20221014
		18	Tu					[V12-16] Received (UPS delivery)	T48-4 SPSE	Available	L		20221018
		20	Th					[V12-16] Sager Order Followup: Boxes opened; Examined Tracos; Called Sager (Sue Pouliot); S&H s/b $25.20 not $35.61; Sue will request a credit of $10.41 [Th12/8 credit $10.41 x 2 accepted/applied Su12/25]	T48-4 EML SPSE				20221020
	Nov	3	Th					[V12-16] Tracos Order Followup: Created History sheets	T48-4 SPSE				20221103
		4	Fr					[V12-16] Tracos Order Followup: Updated Converters Summary sheet; Printed and applied Inventory Sticker 0.47.lbx; Annotated 20221014 Sager Invoice V12 to V16 (TP_4 to TP_8) Scan.jpg	T48-4 SPSE LBX SSC LIB			WP12	20221104
	Dec	13	Tu					WP12 Load Supply and Traco Burn-In: As per WP12-13A; 52.870vI (Barrier strip, 0wIS); Started 180wI Burn-In (12h, hot smell, this is the 1st time these devices have seen full power since the factory)	T48-4 PLN	Burn-In		WP12	20221213
		14	We					WP12, as per WP12-13A: Configuration and Testing finished; Labels finished; Ready to be installed at CFS		Ready	Subaru		20221214
		25	Su					[V12-16] As per WP12-13A, Procurement > Orders Followup FINISHED: Sager $10.41 double credit accepted/applied (reduced S&H for C8, Fr10/14 T48-4, WISPers and Converters Summaries)	T48-4 SPSE			WP12	20221225
		28	We		12:00		14:00	Onsite at CFS: Installed W150_2, vertical on left side of enclosure (side panel is removeable); Photos	T48-4 IMG	Applied	L18	WP12	20221228
2023	Jan	30	Mo					1st Production Run Completed: (WP13 Completed); WP12-13 Invoice Date	T48-4 WP13	Sold		WP12	20230130

## V13
Converters: V13	A					TP_5: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L	WP13
2022	Oct	14	Fr					V12-16	T48-4 SPSE SSC EML	On Order		WP13	20221014
		18	Tu					T48-4 SPSE	Available	L		20221018
		20	Th					T48-4 EML SPSE				20221020
	Nov	3	Th					T48-4 SPSE				20221103
		4	Fr					T48-4 SPSE LBX SSC LIB			WP13	20221104
	Dec	25	Su					T48-4 SPSE			WP13	20221225
2023	Jan	8	Su					As per WP12-13A Configuration and Testing: 52.720vI (Barrier strip, 0wIS) [somewhat low result kicked off a 4 day R&D project, this Trim R assembly replaced Tu1/10]; Started 180wI Burn-In ...	T48-4 PLN	Testing	L0	WP13	20230108
		9	Mo					As per WP12-13A Configuration and Testing: S19/V13 Burn-In completed (16.2h) / Started investigations into Traco Trim R assemblies and output results: Observations of Traco output as a function of load, CONCLUSIONS (obvious dependency on Traco temperature) / WP12-13A Procedure Change for measuring Traco output (20wI, stabilize longer); Reviewed and analyzed data on Traco output results for V9-13 (output Vs recorded vary ±0.1v over a 0.2v range) / Created Traco Power > 20230109 Traco Output Voltage Adjustment TEP 150-xx18WI (Trim R Values).ods to plot R as a function of Vout (printouts, interpolations) / Began looking for a Trim R formula or equation for Traco specified output as a function of Trim R (Traco does not provide the equation, just the table values)	T48-4 PLN SSC LIB	R&D			20230109
		10	Tu					[V13-16] Traco Trim R Investigations Continued: / Observations of Traco output when V13 or Trim R are cooled, CONCLUSIONs "It's the Traco that's sensitive to temperature changes, not the Trim Rs" (no need to specify low TC resistors) / WP12-13A Procedure changed again for measuring Traco output (stabilize ~1h to no more than ±0.001v change over a 15m period, stable shop ambient) / Brief considerations for using precision 10-turn pots (abandoned) [considered and abandoned again We1/11] / Fluke 8000A calibration checked and found to be AOK; Trim R Assembly measures 15.14 KΩF (original made Tu12/13/22) and according to graph should produce 52.81 VTS / Modified and applied new Trim R Assembly label design W150 Traco Trim R KΩF VTS 0.35.lbx (photo) / Solitary 15.0K 1% assembly fabricated, measured (14.96 KΩF, 52.84 VTS), labeled, installed, stabilized and recorded result: / 52.765vI (Barrier strip, 20wI, ~1h stabilization, shop ambient HVAC set 70⁰F); Result is about 45mV higher than original / Labels for WP13 onwards: Don't mention "52.8" anywhere, just "Output voltage as per Traco Trim R"; We could put a new label to the left of the Trim R position that explains some things / More printouts, pencil interpolations and analysis of straight line Trim Up chart created yesterday (will play with Calc to see if we can come up with a curve-fit Trim R Formula)	T48-4 LBX IMG SSC LIB				20230110
		11	We					[V13-16] Traco Trim R Investigations Continued: Estimated T dependence of Traco output vs. Shop ambient as ~+3.5mV/⁰C / Produced a curve-fit Trim R Formula: 20230109 Traco Output Voltage Adjustment TEP 150-xx18WI (Trim R Values).ods Sheet 10-20% Trim Up 5th Degree Poly / VTS=52.85 requires KΩF=14.898; Researched availability of 0.1% resistors, would need to assemble (2) Rs to hit 52.89 VTS or (3) Rs to hit 52.85 VTS; 10-turn pots considered and abandoned again / Measured the remaining stock of (3) 15.0K 1% resistors from Kit from www.techam.com and calculated VTS for them (52.83-52.84 VTS) / WP14 onwards should use solitary 15.0K: This is the simplest solution, with easy assembly and low cost; Desired output very slightly low but that doesn't matter as much as KISS / (3) 15.0K 1% in stock are useable, then buy 0.1% 15.0K (52.83 VTS)	T48-4 PLN LIB				20230111
		12	Th					[V13-16] Traco Trim R Investigations Concluded: Printed and annotated sheet 10-20% Trim Up 5th Degree Poly; WP12-13A/P edited to reflect what was learned; TODO for 2nd Production Run onwards	T48-4	Testing	L		20230112
		30	Mo					1st Production Run Completed: WP13 Completed; WP12-13 Invoice Date	T48-4 LBX SSC	Sold		WP13	20230130
		31	Tu					Photo of WP13	T48-4 IMG				20230131
	Feb	12	Su					[Design Changes for 2nd Production Run]: WP13, ITECH and an old switch used to test using the Traco Ctrl pin to shut off the output by grounding to RSP-V (Traco -Vin); Works as expected	DWP			WP13	20230212

## V14
Converters: V14	A					TP_6: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	WP14
2022	Oct	14	Fr					V12-16	T48-4 SPSE SSC EML	On Order		WP14	20221014
		18	Tu					T48-4 SPSE	Available	L		20221018
		20	Th					T48-4 EML SPSE				20221020
	Nov	3	Th					T48-4 SPSE				20221103
		4	Fr					T48-4 SPSE LBX SSC LIB				20221104
	Dec	25	Su					T48-4 SPSE			WP14	20221225
2023	Jan	10	Tu					V13-16	T48-4 LBX IMG SSC LIB			WP14	20230110
		11	We					T48-4 PLN LIB				20230111
		12	Th					T48-4				20230112

## V15
Converters: V15	A					TP_7: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	WP15
2022	Oct	14	Fr					V12-16	T48-4 SPSE SSC EML	On Order		WP15	20221014
		18	Tu					T48-4 SPSE	Available	L		20221018
		20	Th					T48-4 EML SPSE				20221020
	Nov	3	Th					T48-4 SPSE				20221103
		4	Fr					T48-4 SPSE LBX SSC LIB				20221104
	Dec	25	Su					T48-4 SPSE			WP15	20221225
2023	Jan	10	Tu					V13-16	T48-4 LBX IMG SSC LIB			WP15	20230110
		11	We					T48-4 PLN LIB				20230111
		12	Th					T48-4				20230112

## V16
Converters: V16	A					TP_8: Traco Power TEP 150-2418WI

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	WP16
2022	Oct	14	Fr					V12-16	T48-4 SPSE SSC EML	On Order		WP16	20221014
		18	Tu					T48-4 SPSE	Available	L		20221018
		20	Th					T48-4 EML SPSE				20221020
	Nov	3	Th					T48-4 SPSE				20221103
		4	Fr					T48-4 SPSE LBX SSC LIB				20221104
	Dec	25	Su					T48-4 SPSE			WP16	20221225
2023	Jan	10	Tu					V13-16	T48-4 LBX IMG SSC LIB			WP16	20230110
		11	We					T48-4 PLN LIB				20230111
		12	Th					T48-4				20230112

## W1
Wattmons: W1	A					Wattmon_1: D8-80-39-0C-B9-6F

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Returned	-	-	-	1.942	2.10	7/19/15 to SD Card #2	2		20150707_2338 L1W1M1 Config
2015	Jun	18					Ordered	EML WCA	On Order					1			20150618
		24					Received	WCA	Available	L					20150624
2015	Jul	2					From Keith Jones "ip for solar": 12.133.21.146, 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML					20150702
		3					On the bench for initial test & configuration …	AED	Test…	L0	192.168.0.55		1.947	2.10					20150703
		4					A1/Vin calibrated against Fluke 8000A [Note added 6/7/16: This was done the "old way" with constants in /config/battery.ini]				12.133.21.146				7/4/15 to SD Card #1				20150704
				OS upgraded					2.9					20150704
		5					15:17	Configured; Saved .tar					M1					20150705_2017 L0W1M1 Config	20150705
		6					00:27	Recalibrated A1; Saved .tar					7/6/15 to SD Card #1			20150706_0527 L0W1M1 Config	20150706
				00:50	Modified Actions; Saved .tar					20150706_0550 L0W1M1 Config	20150706
				02:45	Modified Widgets; Saved .tar					20150706_0745 L0W1M1 Config	20150706
				03:07	Modified Weather Widget; Saved .tar					20150706_0807 L0W1M1 Config	20150706
				At RW	TSP IMG	Applied	L1					20150706
		7					18:38	Installation at RW finished; Adjusted AH capacity of battery; Saved .tar	AED					20150707_2338 L1W1M1 Config	20150707
		10					Cleaned contacts on SD Card					20150710
		11					Firmware downgraded					1.931					20150711
		12					Disabled all Actions; Changed log interval; Firmware upgraded					1.947					20150712
		13					Firmware upgraded; Actions re-enabled					1.948					20150713
		15					Firmware upgraded					1.949					20150715
		17					Replaced Trojan 27TMX with (2) T-105 batteries; Adjusted battery parameters					20150717
		19					Removed from RW (swapped SD Cards with #2); Set up to monitor for lockups; Battery config changed; C252_2 Device set up / Fuse blew and replaced; Note that Vin calibration is from Wattmon_2		Testing	L0	192.168.0.55	M2		2.10	7/19/15 to SD Card #2	2			20150719
		20					Connection errors; Configured					20150720
		21					Connection errors; Abandoned configuration of SD Card #2; Planning on RMA for Wattmon_1 with SD Card #2					20150721
		24					Restarted testing again (under bench); Firmware downgraded; Connectivity issues (cycled power 3 times)					1.942					20150724
		25					Connectivity issues (cycled power 2 times); Email to Akash ('get me another unit, T & RH?')	AED EML					20150725
		28					C252_2 removed for use on Wattmon_2		Defective	L					20150728
2015	Aug	26					Shipped back to Akash in India	EML WCA AED	Returned	-	-	-					20150826

## W2
Wattmons: W2	A					Wattmon_2: D8-80-39-0C-BB-61

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Returned	-	-	-	1.1010	2.11	9/18/15 to SD Card #1	1	20160601_2033 L1W2S1M2 on site before replacing with #6	20160409_1357 L1W2S1M2 Config
2015	Jul	13					Ordered	EML WCA	On Order					2			20150713
		15					Received	WCA	Available	L					20150715
		19					13:38	A1/Vin calibrated against Fluke 8000A / [Note added 6/7/16: This was done the "old way" with constants in /config/battery.ini]	AED	Calibration	L0	192.168.0.55		1.947	2.10	7/19/15 to SD Card #2		20150719_1838 L0W2 As From India (except ~30mins bench testing)		20150719
				Installed at RW (swapped SD Cards with #1) (C252_1) / Note that Vin calibration is from Wattmon_1		Applied	L1	12.133.21.146	M1		2.9	7/6/15 on SD Card #1	1			20150719
		20					Configuration: Device Name changed to Wattmon #2					20150720
		21					Configuration: Battery & Charge Settings; Disabled Scheduler in Package Manager; Firmware updated to current version					1.949					20150721
		22					Configuration: Battery & Charge Settings; Connectivity issues; Manually cycled power @ tower; Firmware downgraded					1.947					20150722
		23					Connectivity problems; Manually cycled power @ tower; TelNet reboot also					20150723
		24					Connectivity problems; Manually cycled power @ tower; Firmware downgraded					1.942					20150724
		27					Connectivity problems; Sasha reset onsite w/paperclip (which reset the IP address to default)				192.168.0.55					20150727
				Removed from RW (left C252_1 @ RW)		Calibration…	L	12.133.21.146					20150727
		28					Put on Bench; Configured Devices (C252_2); Firmware updated; Actions modified; /config/uphp.ini edited for "relay_mode=1"			L0		M2	1.951					20150728
2015	Sep	16					[W2-3] From Keith Jones "IP Addresses from Keith Jones": 12.133.21.141 (for RN Wattmon), 12.133.21.146 (already received for RW Wattmon)	SMS EML					20150916
		18					A1/Vin calibrated against BK Precision, 6.00 to 18.00 volts, 1.00 volt steps; (Also calibrated C252_2)	AED					9/18/15 to SD Card #1				20150918
		19					Installed at RW with C252_2		Applied	L1					20150919
				[W2-3] To/From Keith Jones "Re: IP Addresses": This is what I have now: / 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon) / Keith responds with "You can use .147 if you need another one"	EML					20150919
		20					[W2-3] Reviewed and completed MASTER CONFIGURATION; Operating System updated; Firmware updated	AED					1.969	2.10.2					20150920
				17:54			[W2-3] Remote Config backup					20150920_2254 L1W2S1M2 Config	20150920
				Not accessible; Manually cycled power @ tower					20150920
		26					[W2-3] Modifed Battery and Charge Settings (Charge Efficiency 90 --> 95%, Charge parameters met time 120 --> 180 minutes)					20150926
2015	Oct	9					Inaccessible; Sasha onsite to reset & reset; Updated firmware					1.971					20151009
		15					[W2-3] Increased "Charge parameters met time" from 180 to 240 minutes					20151015
				~	12:40		12:30	Inaccessible …; Sasha onsite to reset					20151015
		17					Inaccessible …; To Akash	AED EML					20151017
		19					[W2-3] Sasha & Butch onsite to reset; Turned on http logging	AED					20151019
				~	13:40		18:20	Inaccessible …; Sasha onsite to reset					20151019
		20					[W2-3] Changed Admin password from "abigtweezer" to AkashCanFixThis					20151020
				22:50			[W2-3] Akash logged in and disabled SNTP	EML AED					20151020
		24					[W2-3] Tried to change "Charge parameters met time" from 240 to 300, but "error saving changes" (limit to parameter?)	AED					20151024
		25					[W2-3] Akash configured and set up Wattmon Online Portal	EML AED					20151025
2015	Nov	8					Inaccessible …	AED					20151108
		11					Jeff onsite to reset					20151111
		13					[W2-3] Enabled SNTP and set UTC - 6 CST; Firmware updated					1.977					20151113
		14					[W2-3] Firmware updated; Charge efficiency 95% --> 90%					1.982					20151114
		15					[W2-3] Return Amps set to "Not Used" & Battery Full Voltage set to 16 volts					20151115
		16					Inaccessible for ~120s; TelNet reboot					20151116
		17					[W2-3] http server set to use port 7977 (as per Akash email suggestion)	EML AED			12.133.21.146:7977					20151117
		27					Jeff & Sasha onsite to recharge batteries with Subaru	AED					20151127
				Inaccessible; TelNet reboot					20151127
				[W2-3] Disabled http logging					20151127
		30					Batteries swapped out; Battery SoC adjusted to 100%					20151130
2015	Dec	7					Inaccessible; TelNet won't connect; Butch onsite to reset					20151207
		10		~	14:50		17:50	Logging gap …; Butch onsite to reset; Battery SoC corrected					20151210
		11		~	12:30	~	20:55	Logging stopped …; TelNet won't connect (19:34) ...; Onsite to reset ...; Battery SoC corrected					20151211
		16					[W2-3] Firmware updated					1.991					20151216
		17					Batteries swapped out; Battery SoC adjusted to 100%					20151217
		18					Inaccessible; TelNet reboot					20151218
				[W2-3] Firmware downgraded					1.974					20151218
		19					[W2-3] Inaccessible; TelNet reboot					20151219
				~	22:18		15:31	Logging stopped …; Butch & Bryce onsite to reset ...; Battery SoC corrected					20151219
		20					[W2-3] Firmware upgraded					1.991					20151220
		26		~	23:25		00:35	Logging stopped and Battery SoC --> 0% …; Battery SoC corrected					20151226
		27					Batteries swapped out; Battery SoC adjusted to 100%					20151227
		30					Http interface non-responsive; TelNet reboot (most likely caused by problems with Google Chrome due to Windows Updates on T400s)					20151230
		31					[W2-3] Firmware updated					1.996					20151231
2016	Jan	1					Inaccessible; TelNet won't connect; Butch onsite to reset; Battery SoC corrected					20160101
		2					Inaccessible; TelNet reboot					20160102
		3					Charge efficiency 90% --> 85%					20160103
		5					Inaccessible; TelNet reboot					20160105
		18					[W2-3] Firmware updated (Akash request)	EML AED					1.998					20160118
		19					[W2-3] Difficulties loading pages (most likely caused by problems with Google Chrome due to Windows Updates on T400s)	AED					20160119
		20					Changed sun angle of panels to 30 degrees above horizon					20160120
2016	Feb	2					Inaccessible; TelNet reboot					20160202
		4					08:18	Inaccessible; TelNet won't connect …; Jeff, Butch and the water company guy onsite to reset ...; Battery SoC corrected					20160204
		5			14:22			Inaccessible; TelNet reboot					20160205
		6			06:25			Set Maximum Concurrent Scripts = 1					20160206
		10					[W2-3] Firmware updated					1.999					20160210
		20					1.1004					20160220
		24					[W2-3] To Keith Jones "Re: Ip's for Jeff Klute" which summarizes static IPs: 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay)	EML					20160224
		26			12:32			Logging stopped; Inaccessible; TelNet won't connect …	AED					20160226
2016	Mar	16					Onsite; Installed WebRelay #2; Battery SoC not corrected …	AED IMG					20160316
				[W2-3] Set [UTC-5] Eastern Standard Time (Spring "leap forward" recently, clocks now correct)	AED					20160316
		17			16:20			… Battery SoC corrected					20160317
		20					Battery AH 235.449996 --> 235; Emails Settings tested OK / Attempted to Update Operating System from 2.10.2 to 2.11 but failed (was trying to apply FULL version not UPDATE version) / Set Max Concurrent Scripts = 2 / Tried installing OS 2.11 UPDATE but failed [These problems were most likely caused by problems with Google Chrome due to recent Windows Updates on T400s) ...					20160320
				[W2-3] http server port 7977 --> 80 (sometime from 3/20/16 to 3/22/16)				12.133.21.146					20160320
		24					[W2-3] Now using Google Chrome on JAK2 for access (much better, browsing problems are gone)					20160324
				OS Updated					2.11					20160324
				Began setting up a better SoC Actions system: Old Actions deleted; Variables Widget "Visible"; Renamed Role "Relay Output 5" as "Relay" / Other Roles modified to NOT Display on Dashboard …					20160324
		25					… better SoC Actions: Roles entered for variables needed; "Initialize NVRAM" entered; Action "After Reboot"					20160325
		26					… better SoC Actions: Action "After Reboot" modified (delays) …					20160326
				[W2-3] WebRelays #1 & #2 reconfigured					20160326
				… better SoC Actions: Entered and tested Actions SOC+100, SOC-100					20160326
				21:50			Saved remote Config backup					20160327_0250 L1W2S1M2 Config	20160326
				… better SoC Actions: Entered Actions SOC+070 and SOC-070; Modified Action "Initialize NVRAM"					20160326
		27					… better SoC Actions: Entered Actions SOC+060 and SOC-060; SOC+050 and SOC-050 in MASTER CONFIGURATION but not finished, because I got started thinking about how to do this better with uPHP scripting					20160327
				Temporarily increased uPHP Settings Max Execution Time when trying to get a complete Backup of files on the SD card, but after locking up the Wattmon a few times, and having to wait before it sorted it out, I set it back to 10 Secs					20160327
		28					Began setting up a much better uPHP Actions System: Created folder /Jeff/ and ran emailtest.cgi, modifying to see how it works …					20160328
		30			06:06			Saved remote Config backup					20160330_1106 L1W2S1M2 Config	20160330
		31					… uPHP Actions System: Continued initial coding and experiments; Action "Startup" entered (but disabled for now)					20160331
2016	Apr	1					… uPHP Actions System: Continued initial coding and experiments through 4/6/16 …					20160401
		9	Sa					Firmware updated …					1.1009					20160409
				Rebooting every two minutes, at "After Reboot"; Disabled Action "Exec After Reboot"; Firmware downgraded …					1.1008					20160409
				… same problem; Firmware downgraded …					1.1007					20160409
				1.1006					20160409
				1.1005					20160409
				… same problem; Firmware downgraded; Same problem; Left Action "Exec After Reboot" disabled; To Akash ("Send me a Config backup and I'll work on it Monday") …	AED EML					1.1004					20160409
				Logging gap during the time I was updating the firmwares: Battery SoC corrected	AED					20160409
				08:57			Saved remote Config backup (To Akash)	AED EML					20160409_1357 L1W2S1M2 Config	20160409
				[W2-3] Modified logging and portal reporting intervals to 3 minutes (RW & RN)	AED					20160409
		10	Su					… uPHP Actions System: Continued initial coding and experiments …					20160410
		11					… Enabled Action "After Reboot"; Same problem as above; Firmware updated (as per Akash email); Enabled Action "After Reboot" and all is OK / But NVRAM variables SOC040 to SOC100 are all zero (firmware upgrade process on 4/9/16 wiped out the NVRAM variables) / Enabled "Initialize NVRAM"; (R) and disabled; Actions system is functioning correctly now	EML AED					1.1010					20160411
		12					… uPHP Actions System: Continued initial coding and experiments (Startup.cgi) …	AED					20160412
		16			04:08		09:04	Battery SoC 96.9% --> 0% …; Battery SoC corrected to 94%					20160416
		19					Increased power needs: Removed Ubiquiti switch and installed Netonix switch (speeds are up ~10x, but "Oh, My!" what about the power levels!) …					20160419
		20					… Power needs have gone up +58% (was 16.5 W, now ~26 W); Began analysis of needed increase to solar panel and battery capacity …					20160420
		22					Batteries swapped out; Battery SoC adjusted to 100%					20160422
		26					[W2-3] Discussed the "random noise issues" with Akash …					20160426
		27					[W2-5] … I called Akash again and he agreed to RMA (4) Wattmons (he will advance ship)		To Be Returned					20160427
		29					Batteries swapped out; Battery SoC adjusted to 100%	AED					20160429
2016	May	4		~	09:40		11:46	Battery SoC 49.04% --> 0% …; Battery SoC corrected to 53%					20160504
		6					Batteries swapped out; Battery SoC adjusted to 100%					20160506
		13					20160513
		14			07:38		07:55	Battery SoC 88.10% --> 0% …; Battery SoC corrected to 88%					20160514
		23					Batteries swapped out; Battery SoC adjusted to 100%					20160523
2016	Jun	1					20160601
				15:33			OnSite SD Card Copy; Removed from RW (C252_2 also removed)			L					20160601_2033 L1W2S1M2 on site before replacing with #6		20160601
2016	Jul	18	Mo					[W2-5] / Sent back to Akash in India	EML WCA AED	Returned	-	-	-					20160718

## W3
Wattmons: W3	A					Wattmon_3: D8-80-39-00-9D-1A

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Returned	-	-	-	1.1010	2.11	9/19/15 to SD Card #3	3	20160716_1308 L2W3M6 on site before replacing with #7	20160613_0715 L2W3M6 Config
2015	Jul	27					Ordered (RMA replacement for Wattmon_1)	EML WCA	On Order			N/A				3			20150727
		31					Received	WCA	Available	L					20150731
2015	Sep	16					W2-3	SMS EML					20150916
		17					Physically installed at RN (no configuration)	AED	Applied	L2	192.168.0.55	M6					20150917
		19					Finished installation at RN; RL1/RL2 jumpered; Network, Battery, Time settings configured; A1/Vin calibrated onsite with BK Precision / (Also calibrated C252_3)				12.133.21.141		1.951	2.10	9/19/15 to SD Card #3				20150919
				W2-3	EML					20150919
		20					AED					1.969	2.10.2					20150920
				17:49					20150920_2249 L2W3M6 Config	20150920
		26					W2-3					20150926
2015	Oct	1					Inaccessible; Reseated SD card several times and restored power (onsite)					20151001
		2					Inaccessible					20151002
		9					Sasha onsite to reset; Updated firmware					1.971					20151009
		15					W2-3					20151015
		17		~	10:00			Inaccessible …					20151017
		19					W2-3					20151019
		20					W2-3					20151020
				22:53				EML AED					20151020
		21			13:52			Battery SoC corrected	AED					20151021
		24					W2-3					20151024
		25					EML AED					20151025
2015	Nov	13					W2-3	AED					1.977					20151113
				Inaccessible; TelNet reboot; Inaccessible again; TelNet reboot					20151113
		14					W2-3					1.982					20151114
		15					20151115
		16		~	07:00	~	08:30	Inaccessible …; Akash managed to TelNet and reboot	AED EML					20151116
		17		~	05:50	~	12:50	Logging stopped …; Jeff & Butch onsite to reset ...; Battery SoC corrected	AED					20151117
				W2-3	EML AED			12.133.21.141:7977					20151117
		22					Since 11/18/15: 3-4 connection errors and TelNet reboots	AED					20151122
		23					Inaccessible for about 7 minutes; TelNet reboot					20151123
		24		~	14:45	~	14:55	Logging stopped …; It reset itself					20151124
				~	16:00		16:05	Inaccessible …; TelNet reboot					20151124
		27		~	03:50		12:05	Inaccessible …; TelNet won't connect @ ~06:50 …; Jeff & Butch onsite to reset ...; Battery SoC corrected					20151127
				W2-3					20151127
2015	Dec	10					Inaccessible; TelNet reboot					20151210
		11			19:33			Inaccessible; TelNet reboot; Battery SoC corrected					20151211
		14					Inaccessible; TelNet reboot					20151214
		16					W2-3					1.991					20151216
		18					W2-3					1.974					20151218
		19					20151219
		20					Inacessible; It reset itself					20151220
				W2-3					1.991					20151220
		25			17:10			Inaccessible; TelNet reboot; No Battery SoC correction was needed					20151225
		31					W2-3					1.996					20151231
				~	00:50		12:04	Battery SoC mysteriously --> 100% …; Battery SoC corrected					20151231
				Inaccessible; TelNet reboot					20151231
2016	Jan	1					Won't reboot from http access; TelNet reboot OK (most likely caused by problems with Google Chrome due to Windows Updates on T400s)					20160101
				Battery SoC adjusted due to logging gaps 12/31/15					20160101
		3					Inaccessible; TelNet reboot					20160103
				Won't reboot from http access; TelNet reboot OK (most likely caused by problems with Google Chrome due to Windows Updates on T400s)					20160103
		12					Inaccessible; TelNet won't connect; Jeff & Bryce onsite twice to reset; Battery SoC corrected					20160112
				Inaccessible; TelNet reboot					20160112
		18					W2-3					1.998					20160118
				Akash disabled SNTP and rotated the logs	EML AED					20160118
		19					W2-3	AED					20160119
		20					Inaccessible; TelNet won't connect; but it fixed itself somehow					20160120
		23					20160123
		27					Inaccessible; TelNet reboot					20160127
		31					SNTP enabled, then disabled					20160131
2016	Feb	10					W2-3					1.999					20160210
		18		~	19:02		13:30	Inaccessible; TelNet won't connect …; Batteries swapped (reset); Battery SoC adjusted to 100%					20160218
		20					W2-3					1.1004					20160220
		24					20160224
		25					Inaccessible; TelNet reboot					20160225
		26			13:17			Adjusted Battery SoC (Genasun in float @ 23W and SoC was 97.6%)					20160226
2016	Mar	2			21:49			Logging stopped; Inaccessible; TelNet won't connect …					20160302
		16					Onsite; Installed WebRelay #1; Battery SoC corrected; Photos	AED IMG					20160316
				W2-3	AED					20160316
		20					Battery AH 235.449996 --> 235; Emails Settings tested OK / Attempted to Update Operating System from 2.10.2 to 2.11 but failed (was trying to apply FULL version not UPDATE version) / Package Manager won't show Available Package List [These problems were most likely caused by problems with Google Chrome due to recent Windows Updates on T400s) ...					20160320
				W2-3				12.133.21.141					20160320
		21					Correction to Battery SoC from 97% to 100% (Genasun float @ 28 W)					20160321
		24					W2-3					20160324
				~	04:50	OS Updated; This caused a problem with the cache and a logging gap started; Right before midnight Akash fixed it …; Battery SoC corrected	AED EML					2.11					20160324
		26					W2-3	AED					20160326
		28		~	23:40	~	07:56	Battery SoC --> 0% …; Battery SoC corrected					20160328
		29		~	09:50					20160329
		31					Changed Device Name from "Rayville N (Swafford)" to "Rayville Swafford N"					20160331
2016	Apr	6		~	21:55		09:16	Battery SoC 98.79% --> 0% …; Battery SoC corrected to 93.6%					20160406
		9					Firmware updated					1.1009					20160409
				W2-3					20160409
		11					Firmware updated					1.1010					20160411
		17		~	19:30		03:36	Battery SoC 99.83% --> 0% …; Battery SoC corrected to 95.7%					20160417
		18		~	16:05		03:55	Battery SoC 93.20% --> 0% …; Battery SoC corrected to 88.5%					20160418
		23			16:40			Battery SoC corrected to 100% (Genasun float @ 24 W, and two "guestimate" corrections made since fully charged on 4/17/16)					20160423
		25		~	20:20		03:30	Battery SoC 99.61% --> 0% …; Battery SoC corrected to 95.7%					20160425
		26					W2-3					20160426
		27					W2-5		To Be Returned					20160427
		30		~	14:45			Possible Genasun Failure: Charging Watts dropped to zero, Battery Voltage also dropped to zero at about this time / See AED (resolved itself on the next day)	AED					20160430
2016	May	14		~	18:30		11:15	Battery SoC 100% --> 0% …; Battery SoC corrected to 98.3%					20160514
		17		~	18:05		10:20	Battery SoC 97.4% --> 0% …; Battery SoC corrected to 95.3%					20160517
		20		~	07:55	~	13:55	Battery SoC 94.7% --> 0% …; Battery SoC corrected to 99.1%					20160520
2016	Jun	2					Device Name Changed: Rayville Swafford N --> RN					20160602
				~	17:02	~	17:04	Battery SoC 100% --> 0% …; Battery SoC corrected to 100% (Genasun float)					20160602
		10		~	17:50		18:09					20160610
		13			02:15			Remote Config Backup					20160613_0715 L2W3M6 Config	20160613
		18	Sa					Network Settings modified to enable TCP Server Export to Wattmon.com					20160618
		22	We					WebRelay used to reboot ~3-5 times in the past week					20160622
				~	05:10		06:10	Battery SoC 95.97% --> 0% …; Battery SoC corrected to 95.7%					20160622
		23	Th	~	15:50	~	23:40	Battery SoC 100% --> 0% …; Battery SoC corrected to 98.3%					20160623
2016	Jul	9		~	16:10		04:39	Battery SoC 99.8% --> 0% …; Battery SoC corrected to 226 AH (96.2%) [yesterday's value at this time]					20160709
		16	Sa		08:08		09:22	Onsite Shutdown for removal: SD Card copy; Site specific information copied to SD Card #7 / Removed Wattmon_3 and C252_3; Replaced with Wattmon_7 and C252_4	AED		L					20160716_1308 L2W3M6 on site before replacing with #7		20160716
		18	Mo					W2-5	EML WCA AED	Returned	-	-	-					20160718

## W4
Wattmons: W4	A					Wattmon_4: 00-1E-C0-E3-0E-82

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Returned	-					4
2015	Sep	11					[W4-5] Ordered	EML WCA	On Order					4			20150911
		14					[W4-5] Received	WCA	Available	L					20150914
2016	Apr	27					W2-5		Return…					20160427
	Jul	18	Mo					W2-5	EML WCA AED	Returned	-					20160718

## W5
Wattmons: W5	A					Wattmon_5: 00-1E-C0-E3-64-B0

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Returned	-					5
2015	Sep	11					W4-5	EML WCA	On Order					5			20150911
		14					WCA	Available	L					20150914
2016	Apr	27					W2-5		Return…					20160427
	Jul	18	Mo					W2-5	EML WCA AED	Returned	-					20160718

## W6
Wattmons: W6	A					Wattmon_6: D8-80-39-0C-A9-E2

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	WebRelay	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Available	L	12.133.21.146	-	1.1015	9/18/15 from SD Card #1	6/1/16 to SD Card #6	-	6	20211201_1930 L0W6M1 FW 1.1015 OS 2.11.1	20160615_1635 L1W6M1 Config
2016	Apr	27					[W6-9] Ordered (Akash agreed to RMA Wattmons #2, #3, #4 & #5)	EML WCA	On Order					6			20160427
2016	May	5					[W6-9] Received	WCA AED	Available	L					20160505
2016	Jun	1					05:42	[W6-9] SD Card Copy (Virgin, never booted here)	AED		L0					20160601_1042 L0W6 As From India		20160601
				[W6-7] Calibration: Vin/A1 and C252_1		Calibrated		192.168.0.55	M1	1.1015	2.11.1	6/1/16 to SD Card #6					20160601
				16:35	Installed at RW with C252_1; Config and Logs copied onsite from SD Card #1 (Wattmon_2) [Device.ini and battery.ini voltage calibration clobbered]; Configured ModBus Devices (C252_1) using Android onsite; SoC Actions system not working yet; Onsite SD Card Copy		Applied	L1	12.133.21.146			9/18/15 from SD Card #1		R2		20160601_2135 L1W6M1 on site after device configuration & initial test		20160601
		2					Portal change for new device MAC#: Email to Akash ("D8-80-39-0C-BB-61 now should be D8-80-39-0C-A9-E2") / A few minutes later he fixed it, but there is a gap in the portal records since yesterday's unit swap	EML AED					20160602
				08:26			Voltage Calibration values corrected: Calibration Multiplier and Offset entered from MASTER CONFIGURATION (from 6/1/16) / [Working for now, but not effective through a reboot] …	AED					20160602
				SoC NVRAM values and operation of SoC Actions restored and working					20160602
				Device Name Changed: Rayville Water Tower --> RW					20160602
		3			06:50			Voltage Calibration values corrected again: Calibration Multiplier and Offset entered from MASTER CONFIGURATION (from 6/1/16) / Rebooted and values are not there …					20160603
		4					Voltage Calibration values corrected by editing battery.ini; Rebooted and now issue is resolved; [But I'm planning on returning to RW to pull Wattmon_6 and replace with another Wattmon that has been calibrated with the "New Way" where the values are stored in NVRAM]					6/1/16 to SD Card #6					20160604
				01:40			Saved remote Config backup					20160604_0640 L1W6M1 Config	20160604
				Configuration changes experiments: I was on the phone with Akash, and configured Device WMPRO60 (and Roles) / Later I reversed the changes, removed from the Dashboard, and edited /config/roles.ini to remove the added role / [I will correct this unit later when I bring it back to the shop]					20160604
				/config/uphp.ini restored from the As From India [SD Card #6] copy of 6/1/16 to remove the line "relay_mode=1"					20160604
				10:29			Logs rotated; Some logs deleted (2000, 2036, httplog.txt from 11/27/15, and all system log*.txt from before 6/4/16 10:29					20160604
		5			03:30			Saved remote Logs Backup					20160605_0830 L1W6M1 Logs	20160605
				Edited and uploaded log20160604.txt: Deleted all entries before 6/1/16 16:11:33 (when #6 was powered up after onsite copying of /config/ and /logs/ files); Inserted Note; Inserted system log entries from 20160601_1042 W6 As From India					20160605_0412 #6 [RW] [SD Card #6] [C252 #1] System Log - log20160604.txt	20160605
				05:45	Selected /config/ files uploaded/modified from 20160601_1042 W6 As From India: 3g.ini, crontab.txt, onewire.ini, packages.ini, roles.ini, uphp.ini, widget.ini; During this process (when examining roles.ini) I saved a remote Config Backup					20160605_1045 L1W6M1 Config	20160605
				07:15			Saved remote Config Backup					20160605_1215 L1W6M1 Config	20160605
				07:20			Saved remote Logs Backup; Rotated System Log					20160605_1220 L1W6M1 Logs	20160605
		13	Mo		14:05			Batteries swapped (--> 27TMX); Set 70AH capacity and rebooted (MASTER CONFIGURATION not updated)					20160613
		15	We		11:35			Remote Config Backup					20160615_1635 L1W6M1 Config	20160615
		16	Th	~	10:40		11:10	Batteries swapped (--> (4) T-105s); Photos …; Removed from RW; SD Card Copy (onsite)	AED IMG	Available	L					None		20160616_1610 L1W6M1 on site before replacing with #8		20160616
2018	Apr	15	Su					SD Card #6 tested in card reader on T400s (L0W10M8M9M10, 'Quick Test' [sic] of LCD_1) / Should be no problems, but noted in case later there are issues	AED					20180415
2021	Nov	20					Selected for ONWT Remote Monitoring project	DORM	ONWT Prep	L0		M6				R1				20211120
	Dec	1	We	~	13:30			SD Card Copy (WinMerge compare: identical to 6/16/16 copy)					20211201_1930 L0W6M1 FW 1.1015 OS 2.11.1		20211201
		29	We					[W6/10] Wattmon.com EMS Subscription Preserved for W6 or W10					20211229
2022	Oct	23					ONWT Remote Monitoring project abandoned		Available	L		-				-				20221023

## W7
Wattmons: W7	A					Wattmon_7: D8-80-39-0C-A0-34

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	WebRelay	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Available	L	12.133.21.141	M7	1.1025	2.11.1	6/11/16		7	20190329_0200 L2W7M7 As From Swafford	20170308_1224 L2W7M7 Complete
2016	Apr	27					W6-9	EML WCA	On Order					7			20160427
2016	May	5					WCA AED	Available	L					20160505
2016	Jun	1			05:46				AED		L0					20160601_1046 L0W7 As From India		20160601
				W6-7				192.168.0.55	M7	1.1015	2.11.1	6/1/16 to SD Card #7					20160601
		11			12:58			On Pasha T450s with C252_4, stabilizing temperatures in laboratory …		Calibrating					20160611
				18:10	~	19:45	Calibration: Vin/A1 to NVRAM					6/11/16					20160611
		12			11:24			Removed from calibration bench (calibrations are "spot-on")		Slated for RN					20160612
				12:16			On calibration bench with C252_4; Calibrations checked AOK					20160612
		13		~	01:30			Observations of calibration accuracy as a function of temperature					20160613
				02:30			SD Card Copy					20160613_0730 L0W7M7 Before configuration for RN		20160613
				>	02:30			SD Card on T400s: Partially configured for installation at RN (config files reviewed/modified/copied)					20160613
				>	04:52			Test and review of configuration					20160613
				05:50			SD Card Copy					20160613_1050 L0W7M7 Before going on-site at RN		20160613
				05:55			Removed from calibration bench		Install…	L					20160613
2016	Jul	16	Sa		08:08		09:22	Installed at RN: Site specific information copied from Wattmon_3 [SD Card #3]; C252_4 also installed	AED IMG	Sold	L2	12.133.21.141					R1				20160716
				09:46			SD Card copy	AED					20160716_1446 L2W7M7 on site after device configuration & initial test		20160716
				Spare fuse silver taped to cord for power to WebRelay and Wattmon (2 Amp fast)					20160716
		19	Tu		08:15			[W7-8] Modified Peukert Constant, Battery AH Capacity and Charge Efficiency: Details on the analysis and decision (AED); RW set to use the same parameters as RN except for 2x the Battery AH capacity, so an analysis of SoC algorithm should be possible in the next few days or weeks					20160719
		20	We		09:43			[W7-8] Modified battery parameters to use C/20 instead of C/40 and adjusted Battery SoC to compensate for the change					20160720
		21	Th	~	10:18	~	10:28	uPHP Settings, Session Expire Time (secs): 600 --> 1800 (R); APP/backuprun.cgi, line 2, max_execution_time(600)-->(1800) / These changes to match RW previously configured that way					20160721
				12:30			[W7-8] Lowered Peukert Constant 1.15 --> 1.13					20160721
		22	Fr					[W7-8] NVRAMs checked, they are virgin: RW & RN have only the calibration values put there by the system and my bench calibrations / Items 0->11, d1rw0->d1rw11, A1->A3 & DI1->DI3					20160722
				15:19			[W7-8] Lowered Peukert Constant 1.13 --> 1.11					20160722
		23	Sa		04:15			[W7-8] Remote Config backup					20160723_0915 L2W7M7 Config	20160723
				04:20			[W7-8] Remote Logs backup					20160723_0920 L2W7M7 Logs	20160723
				04:35			[W7-8] Rotated System Log					20160723
				<	08:20	Uploaded NVRAM SoC/A1 system files (from RW config); Initial emails rec'd, system is working					20160723
				09:06	Remote Config backup					20160723_1406 L2W7M7 Config	20160723
		24	Su		17:39		17:43	Increased Charge Efficiency 80 --> 85% …; Remote Config backup					20160724_2243 L2W7M7 Config	20160724
		28	Th		15:35		15:36	Increased Peukert Constant 1.11-->1.17; Decreased Charge Efficiency 85-->80% …; Remote Config backup					20160728_2036 L2W7M7 Config	20160728
		29	Fr		13:59			RCON 10, but no email rec'd					20160729
		30	Sa		04:20		04:25	Decreased Charge Efficiency 80-->75% …; Remote Config backup					20160730_0925 L2W7M7 Config	20160730
2016	Aug	2			16:47		16:48	Increased Charge Efficiency 75-->80% …; Remote Config backup					20160802_2148 L2W7M7 Config	20160802
		5	Fr		04:41		04:43	Decreased Charge Efficiency 80-->77% …; Remote Config backup	AED					20160805_0943 L2W7M7 Config	20160805
		10	We		06:48			[W7-8] Remote Logs backup					20160810_1150 L2W7M7 Logs	20160810
		12	Fr	~	04:50			Decreased Charge Efficiency 77-->76%	AED					20160812
				~	04:55			[W7-8] TelNet Disabled: edited network.ini to add line "telnet=0"					20160812
				~	05:00			[W7-8] Firmware updated 1.1015-->1.1025; This clobbered the NVRAM values (Details AED) …					1.1025		As From India					20160812
				~	09:22	… Restored 6/11/16 calibration values					6/11/16					20160812
				13:17			[W7-8] To Akash "Re: Firmware update 1.1015-->1.1025 and NVRAM gets clobbered" …	EML AED					20160812
				13:54			[W7-8] Remote Config backup	AED					20160812_1854 L2W7M7 Config	20160812
		13	Sa	~	03:35	~	04:45	Remote APP backup (http://12.133.21.141/app/backuprun.cgi?folder=/app/) … / Uploaded RW's (Akash modified) /app/firmware.cgi and /app/firmwareman.cgi	AED EML					20160813_0835 L2W7M7 APP	20160813
				~	04:50			Remote APP backup (http://12.133.21.141/app/backuprun.cgi?folder=/app/)	AED					20160813_0950 L2W7M7 APP	20160813
		14	Su	~	03:22		03:54	[W7-8] Remote All Files backup …; Logs Rotated					20160814_0822 L2W7M7 Complete	20160814
2016	Sep	1	Th		06:19	~	11:20					20160901_1119 L2W7M7 Complete	20160901
		22	Th	~	18:30			Decreased charge efficiency 76-->75%					20160922
		30	Fr	~	09:30			Increased charge efficiency 75-->76%					20160930
2016	Oct	1	Sa	~	01:02	~	01:34	[W7-8] Remote All Files backup …; Logs Rotated	AED					20161001_0602 L2W7M7 Complete	20161001
		9	Su		12:48			Increased charge efficiency 76-->78%					20161009
		25	Tu	~	08:25			Increased charge efficiency 78-->79%					20161025
2016	Nov	3	Fr	~	06:17	~	07:55	Remote All Files backup …; Logs Rotated; [12/3/16: .tar file is corrupt, won't open] / [1/2/17: Recovered from SD Card Copy "20170101_1945 L2W7M7 on site before adding missing logs" "\backup\backup161103.tar"]	AED					20161103_1117 L2W7M7 Complete	20161103
		4	Fr	~	03:10			Decreased charge efficiency 79-->78%					20161104
		13	Su	~	10:35			Increased charge efficiency 78-->79%					20161113
		21	Mo	~	11:20			Increased charge efficiency 79-->80%					20161121
				~	11:30			[W7-8] Adjusted Time and Date Settings [UTC - 5] Eastern Standard Time --> [UTC - 6] Central Standard Time (I forgot to do this when DST ended a short while ago); Also adjusted portal UTC Offset; This caused a glitch in the logged data (an hour got overwritten)					20161121
2016	Dec	2	Fr		12:58		13:12	Remote All Files backup (missing log files) …; Again (missing log files) / Logs before 11/27/16 are missing (will need to tshoot and perhaps upload them or go onsite and put them on the card) …					20161202_1858 L2W7M7 Complete	20161202
		3	Sa					Uploaded missing file in LOGS: log20160723.txt (deleted LOG201~1.TXT which is identical) …					20161203
		16	Fr					For days now I've been having problems accessing it by http; I've discovered some SD card file corruption beyond missing logs / (see TARS\20161216_0345_RN_1001_1202_Compare.WinMerge) / I managed to upload lib/lib.min.js.gz and lib/colorpicker/images/map.png (but not certain of this) / Device is extremely troublesome in http access (long delays, long connection errors, pages won't load completely) / I think it is likely there is something else wrong with it besides file corruption / Am planning on going onsite to replace the Wattmon (but it may be a while before I can get around to doing this) / Logging and portal reporting appears to be OK					20161216
				05:00			Remote All Files backup … but unit rebooted itself while this was running (and I gave up)					20161216
2017	Jan	1	Su		05:42	~	14:45	Corrected SoC +35.73% from 57.61% to 93.33% (connection difficulties) … / Onsite at RN: redid connections, rebooted Ubiquiti / The biggest gain in connection performance seemed to come from reseating the SD card multiple times, / but upon return to the shop I had just as many connection errors	AED					20170101_2045 L2W7M7 on site before adding missing logs		20170101
				14:55	While onsite at RN I also restored missing logs (all but contents of daily_kwh.csv, 2016/2016_0.csv); Increased charge efficiency 80->82% / SD Card copies					20170101_2055 L2W7M7 on site after adding missing logs & editing battery ini		20170101
		2	Mo				06:00	I found that the corrupt remote download was not corrupt in the SD Card copy (see 11/3/16), and so now we have the logs from October, as well as the first few days of November; Assembled everything needed to restore the missing logs (merging summary .csv as needed) / But connection difficulties continue, and I was unable to upload the .tar with the changes					20170102_1200 L2W7M7 Logs Upload	20170102
				06:57			Log file rotated to /logs/log20170102.txt					20170102
		20	Fr					I'm still having connection difficulties: I'm not sure if it is the Wattmon, or if the problem is from TurboNet's equipment / It is intermittent: Sometimes as though there were no problems, at other times, it never finishes loading the page / A couple of weeks ago Mark reported that the Swaffords had internet problems, and it was during this time that the RN Portal logging stopped for long periods of time, until it mysteriously updated / Logging has been fine lately, but I haven't been able to establish an HTTP connection that isn't plagued with long delays, or doesn't finish loading the page altogether / Because Mark would have followed through and fixed problems with Swafford, I must conclude that the problem is with the Wattmon					20170120
		24	Tu		04:43		06:07	Remote Logs backup …; Deleted /logs/20170102_0600 (failed upload attempt, see 1/2/17)	AED					20170124_1043 L2W7M7 Logs	20170124
				08:06	Details on restoring the missing logs / NOTE: I’ve discovered no way to recover the logs from 11/2/16 to 11/27/16 (partially inclusive), we have them on the portal, but the Wattmon's logs are gone for good (it could be possible to transform the portal logs to the same or similar format as the Wattmon logs, and restore them that way, but it probably isn't worth the trouble) / I'm still having intermittent connection difficulties. …; Remote logs backup (WinMerge compared to compiled logs and 100% synced)					20170124_1406 L2W7M7 Logs	20170124
		25	We		14:51		15:08	Remote Complete Backup …; 1472 files, backup170125.tar; (connection difficulties are back, download failed, will try again in the morning) …					20170125
		26	Th				06:46	… Remote Complete Backup download successful					20170125_2051 L2W7M7 Complete	20170126
				09:37		09:54	Remote Complete Backup …; 1473 files, backup170126.tar					20170126_1537 L2W7M7 Complete	20170126
		27	Fr		08:36			Increased Charge Efficiency 82->85%					20170127
2017	Feb	7	Tu		00:05			Akash set up export to ems.wattmon.com (dataexport.ini)	EML AED					20170207
		13	Mo	~	02:40			Increased Charge Efficiency 85->90%					20170213
2017	Mar	7	Tu		15:08			SoC dropped 99.87 -> 0% and solar charge dropped from 37.8 to 0 watts	AED					20170307
		8	We	~	04:45			Corrected SoC 0% -> 95.1%					20170308
			We		06:24		08:09	[W7-8] Remote All Files backup (backup170308.tar) …; Log file rotated to /logs/log20170308.txt					20170308_1224 L2W7M7 Complete	20170308
2017	Apr	10	Mo		05:14			Decreased Charge Efficiency 90-->85%					20170410
2019	Jan	22	Tu					Onsite at RN: Batteries are Deka ProMaster GC10, Man'f 8/18, 5% smaller capacity than T-105s; Replaced Ubiquiti switch with spare / Removed Wattmon, C252 & Web Relay (Reason said I could have them, and they are not interested in paying for monitoring)		Available	L0					20190122
2019	Mar	28	Th	~	20:00			SD Card Copy; Compared with 20170308, there is the typical SD Card corruption issues, but it was logging until 2017/07 when cronmin.cgi 'parse errors' started; Note that if we want to use Wattmon_7 for another application we'll have to start from scratch as the OS is corrupted			L					20190329_0200 L2W7M7 As From Swafford		20190328

## W8
Wattmons: W8	A					Wattmon_8: D8-80-39-0C-A9-A7

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	WebRelay	OneWire(s)	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Available	L	90.0.0.108	M1	1.1114 Akash	2.26 Akash	8/15/18		O2	8	20180819_0520 L0W8O2 OS 2.26 DHCP	20180701_2205 L1W8M1O2 Logs 201806 backup180701
2016	Apr	27					W6-9	EML WCA	On Order					8			20160427
2016	May	5					WCA AED	Available	L					20160505
2016	Jun	1			05:48				AED		L0					20160601_1048 L0W8 As From India		20160601
		5					Observations				192.168.0.55		1.1015	2.11.1					20160605
		6					Voltage Calibration to NVRAM (The "New Way")	AED IMG	Calibrated					6/6/16					20160606
				04:00			SD Card Copy; Put back in stock for future use	AED	Available	L					20160607_0900 L0W8 After A1 Calibration		20160606
		12			11:40		12:12	On calibration bench for tests & experiments with C252_4; Vin calibration quickly checked and looks AOK / Devices configured (C252_4 added, removed, added, removed); … Removed from calibration bench		Slated for RW	L0		M7					20160612
		15	We		11:30			SD Card Copy					None					20160615_1630 L0W8 Before configuration for RW		20160615
				11:40		06:15	SD Card on T400s: Partially configured for installation at RW (config files reviewed/modified/copied)					20160615
		16	Th		06:22		07:00	On Pasha T450s for test and review of configuration … shut down; SD Card Copy		Install…	L					20160616_1200 L0W8 Before going on-site at RW		20160616
				11:10		11:40	Installed at RW; Configured, site-specific information copied, Device C252_1 configured, Corrected Battery SoC to 100% (498 AH), tested onsite; SD Card copy on-site		Applied	L1	12.133.21.146	M1				R2			20160616_1640 L1W8M1 on site after device configuration & initial test		20160616
				>	12:30			Installed 3rd solar panel: Flexible mono-crystalline; Photos (inside box, outside, site)	AED IMG					20160616
				14:28		00:10	Notified Akash of needed MAC address change on portal …; Akash updated portal	EML AED					20160616
		18	Sa					Network Settings modified to enable TCP Server Export to Wattmon.com	AED					20160618
		23	Th	~	09:00			I noticed that there is no Live Energy view on Dashboard (JAK2, Chrome) …					20160623
		25	Sa					Troubleshooting Live Energy view problem: Firmware updated … / [NOTE ADDED 8/12/16: I didn't notice at the time, but this probably clobbered the NVRAM Calibration and set it back to factory]					1.1019		As From India					20160625
				Portal proxy to remote.wattmon.com:7001/index.cgi: / Dashboard Live Energy is working (I think I have a browser problem and will work on installing and testing FireFox on JAK2)…					20160625
		27	Mo	~	06:15			It is obvious from studying the graphs since the 16th that the SoC algorithm needs adjustment / RW is reaching "100%" hours before it has had time to float into a 5% or less Net Charge Watts to AH Capacity / This is due to the recent change to a higher Peukert Constant; Changed Battery Charge Efficiency to 80%					20160627
				08:09			To Akash (& Ruchir)) concerning Live Energy view problem …	EML AED					20160627
2016	Jul	1	Fr	>	08:15			Noticed that problem with Live Energy view also extends to Energy in Watts and Battery Status Graphs: all views are "blank" …	AED					20160701
				Changed Battery Charge Efficiency to 75%					20160701
		8	Fr					Noticed many “Telnet login failed” entries in System Log starting 6/25/16 17:05:19 …					20160708
				11:27			Firmware downgraded					1.1015					20160708
				"Telnet login failed" entries have stopped …					20160708
				11:45			Firmware updated					1.1019					20160708
				"Telnet login failed" entries have started up again …					20160708
				11:58			Firmware downgraded					1.1015					20160708
				"Telnet login failed" entries have stopped …					20160708
				>	12:30			Logs backup attempted … "Max execution time of 600 reached, terminating script"; uPHP Settings modified					20160708
				12:44			Logs backup attempted again but same limit reached; email to Akash …					20160708
				13:12			Logs rotated					20160708
				13:29			Firmware downgraded					1.1014					20160708
				13:32					1.1012					20160708
				13:36					1.1010					20160708
		9	Sa					Akash response to logs backup problem; Edited app/backuprun.cgi, line 2: max_execution_time(600) --> max_execution_time(1800)	EML AED					20160709
				06:51			Logs backup	AED					20160709_1151 L1W8M1 Logs	20160709
				Akash response to "Telnet login failed" / Firmware updated (for now I'd like to leave #8 as the other three Wattmons recently rec'd from India)	EML AED					1.1015					20160709
		19	Tu		08:12			W7-8	AED					20160719
		20	We		09:36					20160720
		21	Th		12:28			W7-8					20160721
		22	Fr					W7-8; [8/12/16: I didn't notice at the time that the firmware updates beginning on 6/25/16 had clobbered the 6/6/16 A1 Calibrations in NVRAM]					20160722
				<	12:15	NVRAM Actions System Completed: Roles & Actions modified (SoC and A1); Graphing glitches caused by my testing by modifying Current Battery AH (10 minutes); Removed "Control" Widget from DashBoard					20160722
				15:14			W7-8					20160722
		23	Sa		03:55					20160723_0855 L1W8M1 Config	20160723
				04:00					20160723_0900 L1W8M1 Logs	20160723
				04:13					20160723
		24	Su		18:30		18:31	Decreased Charge Efficiency 80 --> 75% ...; Remote Config backup					20160724_2331 L1W8M1 Config	20160724
		26	Tu		17:27		17:31	Decreased Charge Efficiency 75-->70% ...; Remote Config backup	AED					20160726_2231 L1W8M1 Config	20160726
		28	Th		15:00		15:05	Increased Peukert Constant 1.11-->1.17; Decrease Charge Efficiency to minimum allowed by Wattmon 70-->60% … / Remote Config backup					20160728_2005 L1W8M1 Config	20160728
		30	Sa		03:45		03:48	Decreased Charge Efficiency 60-->55% (by editing config/battery.ini) …; Remote Config backup					20160730_0848 L1W8M1 Config	20160730
2016	Aug	10	We		06:48			W7-8					20160810_1148 L1W8M1 Logs	20160810
		12	Fr	~	04:57			W7-8	AED					20160812
				~	05:00	~	08:06	W7-8; Restored 6/6/16 calibration values					1.1025		6/6/16					20160812
				13:17			W7-8	EML AED					20160812
				13:54				AED					20160812_1854 L1W8M1 Config	20160812
				20:20		20:24	Akash logged in …; Akash modified /app/firmwareman.cgi and /app/firmware.cgi					20160812
		13	Sa	~	03:35			Remote APP backup (http://12.133.21.146/app/backuprun.cgi?folder=/app/)					20160813_0835 L1W8M1 APP	20160813
		14	Su	~	02:50		03:54	W7-8					20160814_0750 L1W8M1 Complete	20160814
		30			15:37		15:39	Increased Charge Efficiency 55-->70%					20160830
2016	Sep	1	Th		06:19	~	11:20	W7-8					20160901_1119 L1W8M1 Complete	20160901
		6	Tu	~	04:27			Reduced Charge Efficiency 70-->65%					20160906
		30	Fr	~	08:45			Reduced Charge Efficiency 65-->60%					20160930
2016	Oct	1	Sa	~	01:02	~	01:34	W7-8	AED					20161001_0602 L1W8M1 Complete	20161001
		9	Su		19:19			Increased Charge Efficiency from 60-->65%					20161009
2016	Nov	3	Th	~	07:11	~	07:55	Remote All Files backup …; Logs Rotated	AED					20161103_1211 L1W8M1 Complete	20161103
		21	Mo	~	11:40			W7-8					20161121
2016	Dec	2	Fr	~	12:00			Decreased Charge Efficiency 65-->60%					20161202
				12:58		13:33	Remote All Files backup …; Logs Rotated					20161202_1858 L1W8M1 Complete	20161202
		16	Fr		13:50			Onsite at RW: SD card copied; 1 file not copied (invalid filename) lib/colorpicker/i18n/jquery*ui.colorpicker.nl.js@ / [but note that on 12/19/16 @ 06:35 this file no longer exists]	IMG					20161216_1950 L1W8M1 on site after swapping batteries		20161216
2017	Jan	2	Mo		07:00		07:55	Remote All Files backup …; Log file rotated to /logs/log20170102.txt / [NOTE ADDED 2/5/17: Compare with "WinMerge Compiled" (previous SD Card copy) reveals that backup has some filename corruption, \img\ui-bg_highlight-soft_75_cccccc_1x100.png is named UI-BG_~8.PNG (contents are identical) / Backup is missing a file, \lib\ace\theme-tomorrow_night_eighties.js / Backup has a new file with a corrupted name, \lib\colorpicker\i18n\JQUERY~2.JS / Backup has a corrupted file, \lib\lib.min.js.gz (Binary files are different); These changes were not added into Winmerge Compiled]	AED					20170102_1200 L1W8M1 Complete	20170102
		19					Onsite at RW to install 3rd Genasun	IMG					20170119
		21	Sa		03:55			Remote Logs backup	AED					20170121_0955 L1W8M1 Logs	20170121
				04:38			Remote Logs backup (2017 only)					20170121_1038 L1W8M1 2017 Logs	20170121
				06:21					20170121_1221 L1W8M1 2017 Logs	20170121
				08:45			Remote Logs backup					20170121_1445 L1W8M1 Logs	20170121
		25	We		06:24	~	08:51	Remote logs backup …; Details on "Corruption in 1 file corrected" and "Remote logs backup with Max Concurrent Scripts = 3"					20170125_1224 L1W8M1 Logs	20170125
				09:57			Remote complete backup; / [NOTE ADDED 2/5/17: Compare with WinMerge Compiled (20170121_1445 L1W8M1 Logs was the latest update) reveals that backup has corruption / See 1/2/17 "NOTE ADDED 2/5/17", we have the same problems with \img\ and \lib\ files as noted there / But we have a new potential corruption, \logs\2015\12\20151231_0.csv; These changes were not added into WinMerge Compiled]					20170125_1557 L1W8M1 Complete	20170125
		28	Sa	~	08:00			Restored Max Concurrent Scripts = 2					20170128
				09:27		09:31	Tested DailyBackup.cgi (in development): excludes /CACHE and /logs, 20170128_0927_DailyBackup.tar					20170128_1527 L1W8M1 DailyBackup Test	20170128
				Deleted and recreated directory /backup / (my tests of DailyBackup.cgi created a .tar there that has an embedded space, and Wattmon's File Manager could not delete it)					20170128
				11:44		11:49	Tested DailyBackup.cgi (in development): excludes /CACHE and /logs, 20170128_1144_DailyBackup.tar					20170128_1744 L1W8M1 DailyBackup Test	20170128
		29	Su		08:10		08:15	Tested DailyBackup.cgi (in development): Now includes /logs/, 20170129_0810_DailyBackup.tar / [NOTE ADDED 2/5/17 - Compare with WinMerge Compiled (20170125_1557 was the latest update), differences not merged: / \img\ui-bg_highlight-soft_75_cccccc_1x100.png (WinMerge Compiled only), \img\UI-BG_~8.PNG (20170129_1410 only), / \lang\de (WinMerge Compiled only, empty directory that is on the Wattmon), / \lib\ace\theme-tomorrow_night_eighties.js (WinMerge Compiled only), \lib\colorpicker\i18n\JQUERY~2.JS (20170129_1410 only), / \lib\lib.min.js.gz (Binary files are different)]					20170129_1410 L1W8M1 DailyBackup Test	20170129
				08:47		08:53	Tested DailyBackup.cgi (in development): Now includes /logs/, /logs/2017/, /logs/2017/01/ (yesterdays logs) / 20170129_0847_DailyBackup.tar / [NOTE ADDED 2/5/17 - Compare with WinMerge Compiled (20170129_1410 was the latest update), differences not merged: / \img\ui-bg_highlight-soft_75_cccccc_1x100.png (WinMerge Compiled only), \img\UI-BG_~8.PNG (20170129_1447 only), / \lang\de (WinMerge Compiled only, empty directory that is on the Wattmon), / \lib\ace\theme-tomorrow_night_eighties.js (WinMerge Compiled only), \lib\colorpicker\i18n\JQUERY~2.JS (20170129_1447 only), / \lib\lib.min.js.gz (Binary files are different)]					20170129_1447 L1W8M1 DailyBackup Test	20170129
				09:27		09:33	Tested DailyBackup.cgi (in development): / Checked my date math, this test includes /logs/, /logs/2016/, /logs/2016/12/ (30 days ago); 20170129_0927_DailyBackup.tar / [NOTE ADDED 2/5/17 - Compare with WinMerge Compiled (20170129_1447 was the latest update), differences not merged: / \img\ui-bg_highlight-soft_75_cccccc_1x100.png (20170129_1447 only), \img\UI-BG_~8.PNG (20170129_1527 only), / \lang\de (20170129_1447 only, empty directory that is on the Wattmon), / \lib\ace\theme-tomorrow_night_eighties.js (20170129_1447 only), \lib\colorpicker\i18n\JQUERY~2.JS (20170129_1527 only), / \lib\lib.min.js.gz (Binary files are different)]					20170129_1527 L1W8M1 DailyBackup Test	20170129
				15:04		15:10	Tested DailyBackup.cgi (in development): new filename scheme, 20170129_1504z-6_Daily.tar					20170129_2104 L1W8M1 DailyBackup Test	20170129
2017	Feb	1	We		13:35		13:55	Test of Daily Backup System, 20170201_1335u-6_All.tar; Very big file, difficult to download (multiple failures) / It includes one file that does not compare with 20170125_1557 L1W8M1 Complete (/logs/2015/12/20151203_0.csv) / Double checked with remote backup of /logs/2015/12/ (http://12.133.21.146/app/backuprun.cgi?folder=/logs/2015/12/ -> backup170201.tar, 15:24), and the file on the Wattmon compares good with 20170125_1557 L1W8M1 Complete / Either the .tar on the Wattmon is corrupt, or the download is corrupt, and at this point I don't care which, because the file is almost impossible to download (way too big); Downloads deleted (but left originals on Wattmon)					20170201
				18:11		18:17	Test of Daily Backup System, 20170201_1811u-6_1st.tar (searchdir-logs+JanLogs) / [NOTE ADDED 2/5/17 - Compare with WinMerge Compiled (20170129_1527 was the latest update), differences not merged: / \img\ui-bg_highlight-soft_75_cccccc_1x100.png (20170129_1527 only), \img\UI-BG_~8.PNG (20170202_0011 only), / \lang\de (20170129_1527 only, empty directory that is on the Wattmon), / \lib\ace\theme-tomorrow_night_eighties.js (20170129_1527 only), \lib\colorpicker\i18n\JQUERY~2.JS (20170202_0011 only), / \lib\lib.min.js.gz (Binary files are different)]					20170202_0011_1st L1W8M1 DailyBackup Test	20170201
				20:57			Log file rotated to /logs/log20170201.txt					20170201
		2	Th		10:02		10:03	Test of Daily Backup System, 20170202_1002u-6_Feb.tar					20170202_1602_Feb L1W8M1 DailyBackup Test	20170202
				15:13		15:14	Test of Daily Backup System, 20170202_2113_FebLogs.tar					20170202_2113_FebLogs L1W8M1 DailyBackup Test	20170202
		3	Fr		08:30		08:35	Test of Daily Backup System, 20170203_1430_RootFebLogs.tar / [NOTE ADDED 2/5/17 - Compare with WinMerge Compiled (20170202_0011 was the latest update), differences not merged: / \img\ui-bg_highlight-soft_75_cccccc_1x100.png (20170202_0011 only), \img\UI-BG_~8.PNG (20170203_1430 only), / \lang\de (20170202_0011 only, empty directory that is on the Wattmon), / \lib\ace\theme-tomorrow_night_eighties.js (20170202_0011 only), \lib\colorpicker\i18n\JQUERY~2.JS (20170203_1430 only), / \lib\lib.min.js.gz (Binary files are different)]					20170203_1430_RootFebLogs L1W8M1 DailyBackup Test	20170203
2017	Mar	8	We		06:09		08:38	W7-8	AED					20170308_1209 L1W8M1 Complete	20170308
		11	Sa		05:32			Increased Charge Efficiency 60->70%					20170311
	Apr	23	Su	~	12:10			Decreased Charge Efficiency 70->65%					20170423
	Oct	31	Tu					Fixed IP Address changed				207.229.103.165					20171031
2018	Jan	15					Onsite to swap batteries; WebRelay R_2 (R2) removed	AED					20180115
	Apr	11					User Settings, Device Name "L1W8M1"; Devices renamed "Wattmon_8", "C252_1"					20180411
		23	Mo	~	05:30			Noticed that portal data stops on 4/20/18 ~22:30 CST (~23:30 CDT) / Tried some remote troubleshooting but decided it would be best to bring W8 to L0 and fix it here …	AED	Errors Exporting					20180423
		24	Tu	~	09:05	~	09:30	Onsite; Current loop routing (IMG,RW, Wattmon_8, C252_1, Genasun_1, Genasun_2, Genasun_5, a battery); Removed W8 … / SD Card Copy …	IMG AED		L0		None					20180424_1430 L0W8 As Removed from RW		20180424
				~	21:30	Corruption found in (15) files on SD Card (corrected); Modified F:\config\network.ini (dhcp_enabled=1) / Cover removed and interior cleaned (not bad, no bugs, just a little dusty); Booted (ERR002 errors continue); Rotated System Log / FW 1.1025->1.1104; OS 2.11.1->2.11 FULL; Disabled C252_1 (2); Rotated System Log / No ERR002 errors but checked on it about 8 hours later and rebooting every 5 mins; SD Card Copy (corrupted copy, WinMerge failed) / Tried to copy again but SD card is now totally corrupted ...	AED	SD Card Corrupted		90.0.0.144		1.1104	2.11					20180425_0230 L0W8 FW 1.1104 OS 2.11 (corrupted copy)		20180424
				~	22:00			Data Recovery Software (useless); F:\ Windows Error-checking (useless); Format NOT Quick Format with Label "20180424_W8" …					20180425_0300 L0W8 Recovered from corrupted SD card		20180424
		25	We	~	03:45			Mounted SD card on T450s; Formatted again there; Restored files from backups; SD Card Copy; Booted but ERR002 (every min) / Rotated System Log …		Errors Exporting					2.11.1					20180425_0845 L0W8 OS 2.11.1 as restored from backups		20180425
				~	10:00			SD card on T450s; Copied Library 20180403 From Akash - wattmonOS_2.25_FULL_NOCONFIG to SD Card; Deleted all *.cgc (18) / Saved backup (WinMerge compare OK); Physically attached T_2; Booted / Found & corrected corruption in 20180420_0.csv (now exporting); Configured T_2 ...		Configuring					2.25 Akash			O2		20180425_1500 L0W8 OS 2.25 from Akash		20180425
				~	13:00			Installed OS 2.25 UPDATE; SD card on T450s; Copied & Compared OK; Modified Data Export Settings Interval in minutes 3->1 / (temporary, to speed up getting the portal exports finished); ajax_refresh_time=1->0.75 …					2.25					20180425_1800 L0W8O2 OS 2.25		20180425
		26	Th	~	01:30	~	06:00	Rebooting every 3 mins (stopped as soon as I logged in); Portal is completely caught up, set Export Interval 1->3 mins / Portal and Roles configured for Temperature Graph; Installed and configured better Variables Widget; Roles (36)-(43) deleted / Actions edited (emails don't work 'cause Akash deprecated 'mail' function); Calibrated A1 (no changes needed) / Worked on smtp.cgi (from Jeff's Scripts [RW]), uploaded to /config/Jeff; Restored settings for re-installation at RW ... / SD Card copied and compared on T450s		Install…		207.229.103.165				4/26/18				20180426_1100 L0W8O2 Before re-installation at RW		20180426
				06:22			Onsite and finished installing Wattmon_8 and T_2 (O2) …; Live Energy Graph is working (!); ajax_refresh_time 0.75->0.65 (perfect timing now): Changed name L1W8M1 -> L1W8M1O2; Developing SoC emails system (and other configuration) …		Applied	L1		M1					20180426
		27	Fr				10:45	Developing SoC emails system … decided to make it uPHP based and as a Package "SMTP Alerts" (but this may never happen, as ems.wattmon.com might take care of the issues); Issue "Portal Data Stopped on 4/20/18 (Resolved)"; Remote Config backup					20180427_1545 L1W8M1O2 Config backup180427	20180427
				07:34	KwH Log Modified (Temperature1 Function AVERAGE); Energy in Watts Graph Modified (Local and Portal) / Variables Widget cleaned up (removed all SoC stuff); Actions deleted; Control Widget hidden; Remote Config Backup					20180428_0034 L1W8M1O2 Config backup180427	20180427
2018	May	1	Tu			~	13:09	Roles modified (now same as defaults from India), sysvars (added Solar Current/Watts Out), Data Collection (added Solar Watts Out), Portal (Enable w_out3), Graphs (identical to W9), Remote Logs 201804 Backup					20180501_1809 L1W8M1O2 Logs 201804 backup180501	20180501
				~	15:08	Remote Config Backup					20180501_2008 L1W8M1O2 Config backup180501	20180501
2018	Jun	4	Mo	~	04:58					20180604_0958 L1W8M1O2 Config backup180604	20180604
				~	05:03			Remote Logs 201805 Backup					20180604_1004 L1W8M1O2 Logs 201805 backup180604	20180604
2018	Jul	1	Su	~	17:00			Remote Config Backup; WinMerge compare, 100% identical to 6/4/18 backup					20180701_2200 L1W8M1O2 Config backup180701	20180701
				~	17:05			Remote Logs 201806 Backup					20180701_2205 L1W8M1O2 Logs 201806 backup180701	20180701
2018	Aug	2	Th	~	04:30			Accessible but I can't reboot it: Dashboard shows no time or other information; System Log shows it rebooted itself yesterday morning; It's logging and reporting to the portal; I didn't get an email when it went below 75% 7/27/18		System corruption					20180802
		8	We	~	00:30			Not responsive to any commands, there must be software corruption / Although it has rebooted itself since 8/2/18 rebooting evidently isn't helping it; The only way to fix this is to go onsite					20180808
		13	Mo			~	11:35	Onsite at RW 09:15; AC OK; Photos (before); Removed C252_1; Set up for onsite Tshooting of Wattmon_8 corruption issues / SD Card Copy (not checked, decided to Tshoot at shop); Removed Wattmon_8; Photos (after)	IMG		L					20180813_1635 L1W8M1O2 On Site		20180813
		15	We		00:55			SD Card Copy compared (copied onsite 8/13): logs/2018/01/201802_0.csv is different in the copy (SD Card corruption)			L0					20180815
				Compared SD Card with previous SD Card Copy 20180426_1100 L0W8O2 Before re-installation at RW: / (3) corrupted files in /lib/ (angular.min.js.gz, flotr2.min.js.gz, jsmin.js.gz) / (this was later found to be the reason why the system was not responding), copied from 4/26 version / Copied /logs/2018/01/20180102_0.csv from 4/26 version					20180815
				Compared SD Card with 20180501_1809 L1W8M1O2 Logs 201804 backup180501: April's logs are identical and uncorrupted					20180815
				Compared SD Card with 20180604_1004 L1W8M1O2 Logs 201805 backup180604: May's logs are identical and uncorrupted					20180815
				Compared SD Card with 20180701_2205 L1W8M1O2 Logs 201806 backup180701: June's logs are identical and uncorrupted					20180815
				Compared SD Card with 20180701_2200 L1W8M1O2 Config backup180701: Config is identical and uncorrupted					20180815
				02:10	/config/network.ini edited: dhcp_enabled=0->1					20180815
				~	02:15			SD Card Copy					20180815_0715 L0W8M1O2 OS 2.25 DHCP		20180815
				~	04:00			Set up on bench: BK and Fluke on battery ends of new cables for Wattmon power that should work OK at RW (positive Red has switch and fuse with lighter gauge wire that will fit through C252 load loop), C252_1 attached to simulate similar load at RW for calibration; Dashboard and Live Energy all OK (software corruption has been fixed)	AED	Calibrate A1		90.0.0.108					20180815
				Quick calibration check, 10 to 16v all appear to be slightly low maybe 0.05 volts (this is probably the zero offset needed to compensate for drop in longer wires than was used in the 4/26/18 calibration, where connection was "Directly on A1(2) and GND(1)") / Careful calibration (offset changed 1 count, see MASTER CONFIGURATION)		Update FW					8/15/18					20180815
				FW upgraded 1.1104 -> 1.1113 ("Bug fixes and increased memory availability", released 8/9/18)		Update OS				1.1113					20180815
				OS upgraded 2.25 to 2.26 UPDATE ("… bug fixes and minor feature improvements", released 8/6/18) / [this fully implements new Software Watchdog that Akash recently released, timeout is 5 mins]		Configure Devices					2.26					20180815
				~	06:55			Devices: C252_1 deleted; Shutdown and disconnected; Noticed that without the load of the C252 the A1 voltage is slightly high / C252_1 in stock, available	AED	Misc. Configuration					20180815
				~	08:20	Changed Device Name L1W8M1O2 -> L1W8M2O2; Battery and Charge Settings modified for 27TMX and W100_2 (112 AH, 100% Charge Efficiency, Peukert Constant 1, Current Battery AH 112); Description changed on my.wattmon.com to L1W8M2O2		Emails Configuration					20180815
		16	Th	~	04:50			SMTP Notifications: SD Card copy (compares OK); Copied action*.ini from 20180427_1545 L1W8M1O2 Config backup180427 to SD Card /config (all Actions are disabled); Planning TODO for Actions system …					20180816_0950 L0W8O2 OS 2.26 DHCP		20180816
		17	Fr					SMTP Notifications: Wrote and uploaded script nvram_unset.cgi (Jeff's Scripts [RW]) and cleaned NVRAM (unset/cleared DailyBackup, SOC100, NVRAM, A1_OK, SOC000, SOC025, SOC050, SOC075);					20180817
		18	Sa					SMTP Notifications: Edited, uploaded and tested /config/mail.ini and smtp.cgi (problems encountered with NVRAM full errors) / To Akash '"NVRAM full" but it's not!'	EML					20180818
		19	Su	~	12:20			SMTP Notifications: Wrote and uploaded script nvram_backup.cgi (Jeff's Scripts [RW]) / Upon running it returned 0 but appeared to write /nvram.dat (new date/timestamp) / Downloaded by clicking on it in File Manager, but contents are identical to the nvram.dat that was created on 8/15/18 (when firmware was updated) / SD Card Copy; nvram.dat compared (8/15/18 and 8/18/18 versions) and it is completely different / Conclusion: you can't download a file using File Manager and Firefox, it doesn't work, Wattmon appears to serve up an older version of the contents, not sure why					20180819_0520 L0W8O2 OS 2.26 DHCP		20180819
				~	04:00			SMTP Notifications: Global Variables shown in Variables Widget (Ready,Msg,C01,V13,V11,SOC100,SOC050,SOC000) / (Temperature1 is at the top of the list, it is a role, not a global variable)					20180819
				SMTP Notifications: Edited, uploaded and tested /config/mail.ini and smtp.cgi					20180819
		20	Mo	~	01:30	~	06:00	SMTP Notifications: /config/mail.ini; /config/Jeff/smtp.cgi					20180820
				~	22:00			SMTP Notifications: Variables Widget (Run,Msg,Exceptions,Ready,C01,V13,V11,SOC100,SOC050,SOC000); All Actions deleted / /config/mail.ini; /config/Jeff/smtp.cgi					20180820
		21	Tu	~	01:00	~	03:00	SMTP Notifications: Problems with lockups, only when Variables Widget is enabled and trying to display a string variable that doesn't evaluate to a numeric; Modified /scripts/runonce.cgi for testing and restored the original version / To Akash "Bug Report: Variable Widget Package"	EML					20180821
				~	06:30	SMTP Notifications: From Akash "Re: Bug Report: Variable Widget Package" / Uploaded ajaxdata.cgi he provided and tested (that fixed it) / Restored Variables Widget configuration (role=31, vars=Run,Msg,Exceptions,Ready,C01,V13,V11,SOC100,SOC050,SOC000) / smtp.cgi is now working to the die point; Email to Akash "Re: Bug Report: Variable Widget Package"					2.26 Akash					20180821
		22	We					From Akash 'Re: "NVRAM full" but it's not!'; FW patched with file Wattmon_Core.production.hex (1.1113->1.1114) / /scripts/tests/nvram.cgi?defrag=1; NVRAM Free went from -20DEFRAG! to 7996 / Tested nvram functions (using /scripts/tests/nvram.cgi and /config/Jeff/nram_unset.cgi) and FW patch seems to be successful in fixing the NVRAM problems / Email to Akash 'Re: "NVRAM full" but it's not!' (fixed)					1.1114 Akash					20180822
				SMTP Notifications: Coding and testing smtp.cgi, ran into problems again with Variables Widget (fails with empty string, works with space string ' '); To Akash "Bug Report 2: Variable Widget Package"					20180822
		29	We					No time to work on W8 for the next few weeks: powered off (need BK)		OFF					20180829
2019	Apr	28	Su					Priorities have changed: not planning on installing this at RW (we don't really need to monitor WP3/W100_2)		Available	L					20190428

## W9
Wattmons: W9	A					Wattmon_9: D8-80-39-0C-9F-8D

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	A2 Calibration	OneWire(s)	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Available	L	90.0.0.109	M3	1.1112	2.26	3/13/18	4/21/18	O1	9	20200613_1300 L0W9M3O1	20180410 L0W9M2M3 scripts - Bug report for cronmin (JAK)
2016	Apr	27					W6-9	EML WCA	On Order					9			20160427
	May	5					WCA AED	Calibrate…	L					20160505
	Jun	1					AED			192.168.0.55		1.1015	2.11.1					20160601_1051 L0W9 As From India		20160601
2017	Feb	27	Mo				09:30	Set up on bench; Credentials as from India (admin, admin); Network Settings modified for DHCP; "Getting Started" Hidden / Log file rotated to /logs/log20170227.txt; WattmonOS 2.16 UPDATE (latest release 2017-01-12) / Wattmon Firmware 1.1051 (latest release 2017-02-25); Time and Date Settings UTC-6, Sync Time; SD Card Copy		Cynergy Test Unit	L0	90.0.0.126		1.1051	2.16					20170227_0930 L0W9 Latest OS & Firmware		20170227
				Folder /test created (and will be used for uploading test scripts)					20170227
		28	Tu					uPHP Script Setup (uPHP Settings) Session Expire time (secs): 600-->1800					20170228
2017	Mar	1					uPHP Script Setup (uPHP Settings) Session Expire time (secs): 1800->3600					20170301
		6	Mo					Experiments with firmwareupdate(): Firmware downgraded to 1.1015 / [by uploading image.hex from 20160601_1051 W9 As From India and firmwareupdate()] / Tested firmwareupdate() without /image.hex [it didn't reboot, I didn't reboot it, log file entries are incomplete] / Restored firmware 1.1051 by exploding /firmware.tar [OK, new changelog.txt, image.hex, md5.txt] and firmwareupdate() [OK, firmware 1.1051] / Tested firmwareupdate() without /image.hex [it didn't reboot, I rebooted, log file entries are OK, evidently firmwareupdate() does NOT update the firmware if image.hex is missing]					20170306
2017	Apr	2	Su					Tested USB_2 and then reversed settings and removed (probably not working due to CC SIM card, otherwise fine)	AED					20170402
2017	Aug	3	Th					Configuration and calibration for testing WISPOWER; Installed current sensor and configured devices and roles (config files modified network.ini, setup.ini, battery.ini, roles.ini, device.ini); Use as bench test unit is intermittent (not always on)		Test Unit			M2					20170803
		4	Fr					Updated firmware and OS to the latest available; Firmware update normal; OS update partially completed with System Log entry "Fri Aug 04 08:11:22 2017: Error on pacman.cgi line 106 : Unknown identifier: 108" / Rebooted and says we are using OS 2.20; Repeated update and this time no logged error (but Live Energy is not yet working)					1.1066	2.20					20170804
				12:20			SD Card Copy; Deleted all files on SD Card and copied 20160601_1051 L0W9 As From India to it: / Live Energy is now working (Pasha T450s); But on DHCP cannot login until after restarting FireFox (intermittent)					2.11.1					20170804_1720 L0W9M2 Latest OS & Firmware - Live Energy Inop		20170804
				~	15:40	Configured as needed for bench use and updated Master Configuration; SD Card Copy					20170804_2040 L0W9M2 Graphing Works		20170804
				~	16:05	Updated OS (same problem logging in, repeated attempts); Live Energy is working; SD Card Copy					2.20					20170804_2105 L0W9M2 Graphing Works Latest OS & Firmware		20170804
				A1/Vin Calibration checked (no changes needed, factory calibration was just fine for 12v batteries)					8/4/17					20170804
		7					Photos of WISPer#1 bench testing	IMG AED					20170807
		11	Fr					Akash produced new firmware: Before updating, the login problem remains, but the graphs are AOK (nothing missing), this with Firefox having only one tab; Updated firmware ("Bug fixes for LAN, dongles and modbus commands") / No login problem at first (3 attempts); But later the login problem came back (4 tries to get back in)	EML AED					1.1067					20170811
2018	Feb	25					Photos of W9 behind WISPer #2 test setup	IMG WRD					20180225
2018	Mar	4	Su					Configuration corrections for WISPOWER #2 testing, which has been ongoing since about a week ago / Charge efficiency 90->100%; Widget "Control" hidden; Data Collection Log Interval from 15 to 3 minutes / uPHP Script Session Expire from 600 to 1800 secs; Data Export to Wattmon Cloud Interval 5 to 3 mins / Tweaked A1/VIN calibration for about +1% increase in multiplier constant for better agreement with Fluke / (see Master Configuration)	AED	DR Testing (W100)					3/4/18					20180304
		5					W9 behind WISPer #2 test setup (Delta 150W, Genasun_3 no cover, fan taped to bench, BK for boost to Delta, B1)	IMG					20180305
		13	Tu					WISPOWER #2 testing continues; Tweaked A1/VIN calibration for a slight decrease in multiplier constant for better agreement with Fluke (see Master Configuration) / 'W100 Testing' (Trace used as CW load, B1, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK)	AED WRD IMG					3/13/18					20180313
		15					W100 Testing (Trace used as CW load, B1, WP2, Delta 200W, Genasun mounted under fan, W9, C252, BK, Heathkit)	WRD IMG					20180315
		23	Fr		18:45			Some playing around with Roles, saved a backup of roles.ini and edited it (done by copy and paste)	AED WRD					20180323_2345 L0W9M2 Config - Roles.ini - Before & After minor manual editing		20180323
		24	Sa		22:40			Complete SD Card Copy during W100 testing					20180325_0340 L0W9M2 During W100 Testing Setup		20180324
		27	Tu		07:08			Firmware updated 1.1067 --> 1.1101 (Details AED, there are a number of notable changes)					1.1101					20180327
				21:15	WattmonOS 2.24 UPDATE; Complete SD Card Copy (Details AED, there are a number of notable changes)					2.24					20180328_0215 L0W9M2 Latest OS & Firmware		20180327
		28	We	~	13:30	~	14:35	OS Redone, applying all UPDATEs since “As From India” OS 2.11.1 (details AED) …; Complete SD Card Copy					2.24					20180328_1935 L0W9M2 OS Redone 2.11.1 to 2.24 (FW 1.1101)		20180328
2018	Apr	2		~	15:15			Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): To Akash	IMG EML					20180402
		3	Tu	~	23:30			SD Card Copy	AED WRD					20180404_0430 L0W9M2 FW 1.1101 OS 2.24		20180403
		4	We	~	00:12	~	01:25	SD Card: Everything deleted except /config, /JAK and /logs; copied OS 2.25 from Library …; Booted, Rotated System Log	AED					2.25 Akash					20180404_0500 L0W9M2 FW 1.1101 OS 2.25 from Akash		20180404
				~	15:45	~	16:24	SD Card: Copy; (5) /config files r/w "As From India" …; Booted ("Solar Watts" logging problem is still there)					2.25 Akash/JAK					20180404_2045 L0W9M2 Config		20180404
				~	17:00			SD Card: Restored /config to 20180404_2045					20180404
		5	Th					Bug report for cronmin (JAK) - /scripts/cronsec.cgi and /scripts/cronmin.cgi					20180405 L0W9M2 scripts - Bug report for cronmin (JAK)	20180405
		6	Fr					I3O2 Attached, partially configured					M2M3					20180406
		9	Mo					Bug report for cronmin (Akash) - /scripts/cronsec.cgi and /scripts/cronmin.cgi					20180409 L0W9M2M3 scripts - Bug report for cronmin (Akash)	20180409
				Bug report for cronmin (JAK) - /scripts/cronsec.cgi and /scripts/cronmin.cgi					20180409 L0W9M2M3 scripts - Bug report for cronmin (JAK)	20180409
		10	Tu					Bug report for cronmin (Akash) - /scripts/cronsec.cgi and /scripts/cronmin.cgi					20180410 L0W9M2M3 scripts - Bug report for cronmin (Akash)	20180410
				Bug report for cronmin (JAK) - /scripts/cronsec.cgi and /scripts/cronmin.cgi					20180410 L0W9M2M3 scripts - Bug report for cronmin (JAK)	20180410
		11	We					User Settings, Device Name "L0W9M2M3"; I3O2 configured; Roles configured; Actions deleted (Action to switch on relay 5)	AED WRD					20180411
		14	Sa					CradlePoint Router configured to reserve IP 90.0.0.126-->90.0.0.109 (but W9 is still set for DHCP)	CPSN			90.0.0.109			2.25 Akash/JAK DR 1.0b					20180414
		21	Sa					A3 calibration	AED					4/21/18					20180421
		22	Su					T_1 installed ("L0W9M2M3O1")					O1				20180422
		26	Th					Role (31) Name: T_2 -> Temperature1; Configured Portal; Changed name L0W9M2M3 -> L0W9M2M3O1					20180426
		27	Fr			~	21:00	Deleted items from KwH Log that aren't needed; Changed Temperature1 logging to AVG instead of MAX / Added logging for total_watts / Modified local graphs 'Energy in Watts' (colors, total_watts) and 'Temperature' (logged value now 6) / Portal set to log total_watts (graphs were modified there earlier for W9 and are the same for W8) / Logging for ‘total_watts’ Not Averaged ...; SD Card Copy (on T450s)					20180428_0200 L0W9M2M3O1 OS 2.25 from Akash		20180427
		28	Sa	~	06:00	~	06:25	FW 1.1101->1.1105 …; OS '2.25 Akash' -> '2.25'					1.1105	2.25					20180428
				~	06:40			SD Card Copy (T450s); 20180428_1140 L0W9M2M3O1 OS 2.25 selected files.epp					20180428_1140 L0W9M2M3O1 OS 2.25		20180428
				~	08:25			Added Data Collection 'Test Averaging' and disabled export to portal					20180428
		29	Su					Worked on "Logging for ‘total_watts’ Not Averaged": Modified cronmin.cgi, sysvars.ini and cronsec.cgi …	AED WRD					2.25 JAK					20180429
		30	Mo					… Modified sysvars.ini, datalog.ini, roles.ini; Enabled export to portal …					20180430
2018	May	1	Tu	~	07:30			SD Card Copy (T450s); Modified KwH Log and Graphs for 'Solar Watts Out'					20180501_1230 L0W9M2M3O1 OS 2.25 JAK		20180501
		5	Sa	~	07:15	~	07:46	Modified Battery settings (Capacity 248 AH and set 100% SoC) ...; Again (Capacity 245 AH and 100% SoC)	WRD					20180505
				Actions added for 40w DR test of WISPer #2 (W100) for Wellington Water Tower					20180505
2018	Jun	4	Mo	~	06:30			SD Card Copy; Found a spurious folder during WinMerge Compare with 20180501_1230 L0W9M2M3O1 OS 2.25 JAK: / /logs/2018/W5 (empty folder, deleted on W9)					20180604_1130 L0W9M2M3O1 OS 2.25 JAK		20180604
		15	Fr	~	04:45			Being powered by 27TMX and BTJ_1; Battery AH 105 (reset SoC to 100%)	B1 BC2					20180615
		20	We	~	01:50			Changes to my.wattmon.com: Site ID "W9" --> "Bench"; Latitude and Longitude corrected (they were reversed)					20180620
2018	Jul	1	Su	~	17:40			SD Card Copy					20180701_2240 L0W9M2M3O1 OS 2.25 JAK		20180701
2018	Aug	8	We	~	12:45	~	00:55	SD Card Copy; FW 1.1105->1.1112 "Bug fixes for certain memory leaks and implemented software watchdog"					1.1112					20180808_0545 L0W9M2M3O1 OS 2.25 JAK		20180808
				~	01:10	~	01:15	WattmonOS 2.25 to 2.26 UPDATE "… bug fixes and minor feature improvements" / (supposedly has software watchdog system fully implemented) / (note that this clobbered the files I had modified, cronmin.cgi, cronsec.cgi); Rotated System Log; SD Card Copy					2.26					20180808_0615 L0W9M2M3O1 OS 2.26		20180808
		12	Su	~	06:55			Placed on old battery and BTJ_1; C252_2 removed for installation at RW	B0 BC2 WRD	Lab Temp	L		M3					20180812
		29	We	~	08:30			Temperature sensor used to log temperature of NiCad being charged by BK (W9 being powered by BK)	S2	NiCad Temp					20180829
		30	Th	~	02:30			W9 powered by old battery and BTJ_1	B0 BC2	Lab Temp					20180830
2018	Nov	25		~	23:15			Export to portal stops		Not Exporting					20181125
2018	Dec	6			07:55		07:58	Logrotate ...; Logs show error in ip.cgi line 622, every minute					20181206
		31			19:23			Logs show error in ip.cgi 622 stops, but now "Socket open timed out!" every minute					20181231
2019	Jan	14		~	12:58	~	13:03	Logrotate; ip.cgi lines 32 and 385 "Socket open timed out!" errors continue every 30 seconds; SD Card Copy					20190114_1903 L0W9M3O1 OS 2.26		20190114
				Compared previous 20180808_0615 LOW9M2M3O1 OS 2.26 with SD Card: / lib/lib.min.js.gz binary is different, although same date (copied previous to SD Card)					20190114
				~	13:43			Reinstalled SD Card and powered up; Trying to open Data Export Settings, but every time I do so W9 reboots					20190114
		15		~	05:00	~	05:16	Logrotate; ip.cgi lines 32 and 385 "Socket open timed out!" errors continue every 30 seconds / Trying to open Data Export Settings, but every time I do so W9 reboots; Data Export Settings > Reset Export					20190115
				05:27		05:52	Logrotate; Portal New Subscription (balance 2000 INR, used 1000 INR) but couldn't figure out how to apply it to W9 … / Data Export Settings > Export to Wattmon Cloud > Disabled (R)		Lab Temp, No Portal					20190115
2019	May	8	We		13:46			Applied to monitor temperature inside my desiccant regeneration oven (Dad's old camp box, having returned from RW where it was used as a battery box); Desired temperature 118.3⁰C, and the DS18B20 sensors should read to 125⁰C		Desiccant Oven					20190508
				15:08			Logrotate (several)					20190508
				Actions modified to switch Main Relay on/off @ 118⁰C					20190508
		9	Th					Actions modified to start temperature at 25⁰C and raise it slowly to 118⁰C (1⁰C/4 min); Logrotate (several)					20190509
		10	Fr		03:45			Logrotate					20190510
		12	Su					Finished Desiccant Oven operation (all Silica Gel has been regenerated and stored); T Sensor remains inside oven		Lab Temp					20190512
		17	Fr		08:30			Started experiment in charging Milwaukee Nicads with Tsensor to detect full charge	S2	NiCad Temp					20190517
		18	Sa	~	03:00			Modified uPhP Settings > Session expire: 1800-->18000					20190518
				18:54	Ended Milwaukee Nicad charging experiment (details S2); Tsensor on bench	S2	Lab Temp					20190518
		22	We	~	15:10	~	15:20	6 pack of old batteries (TL3_6, + battery I was using before) on Heathkit (adjusted to 13.7vdc Fluke) powering Wattmon_9 … / Heathkit says 14.1 vdc @ 430 mA (dropping); Wattmon says 13.7 vdc	A30 S1					20190522
2019	Jun	4	Tu					Logging temperature for Nicad charge (details S2); Photos show Tsensor taped to Nicad	S2 IMG	NiCad Temp					20190604
		5	We	~	00:50		01:15	Terminated Nicad charge (see BK_1 for details); Temperature was flat until ~19:50, when it began to rise in almost a straight line passing 30⁰C at 23:00; Charging algorithm s/b 240mA (C/10) until temperature rises beyond 30⁰C (in this case ~11 hours), for safety time out at 16 hours; 20190605 010735 Screenshot.jpg ...; Logrotate; SD Card Copy	S2 SSC	Lab Temp					20190605_0615 L0W9M3O1		20190605
		16	Su	~	10:10	~	20:30	Logging temperature for Milwaukee Nicad A charge (details S2); Charge current goes through RL1/2, Actions modified to Switch Off RL1/2 when T>30⁰C ...; Relay shut it off @ 10 Hrs 20 Mins	S2	NiCad Temp					20190616
		17	Mo	~	01:15		01:35	Temperature Graph, NiCad charge: 20190617 011553 Screenshot.jpg … / Charging Milwaukee Nicad B (details S2): Action 'T>30' ...	S2 SSC					20190617
				~	08:33	~	09:55	17.59v highest voltage seen (but not sure it was the peak)...; Relay shut it off at 8 Hrs 20 Mins / The peak voltage was somewhere between 06:37 and 08:45, and temperature began to rise at ~07:00 / Recommend using 28⁰C for the cutoff (or about 5⁰F above ambient temperature); 20190617 101017 Screenshot.jpg / Modified and renamed Action 'T>30' as 'T>28'; Rotated log	SSC	Lab Temp					20190617
		28	Fr					[W9-10] W100 Parallel Test setup: / BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1	IMG					20190628
2019	Jul	8					[W9-10] W100 Series Test setup: WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1					20190708
		14					[W9-10] W100 DR Test Setup: / APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)					20190714
2019	Aug	3	Sa	~	12:05	~	12:25	Reviewed Wattmon_9 Temperature Graphs (it's been logging lab temperature for > 1 year)		W100 Test					20190803
			Su	~	07:30	~	17:00	T probe has been taped to the bench; Began dissipating about 90w from ballast resistors and BK_1 about 18" away on the bench; T graph shows how temperature was affected by this (A/C remains at 70°F nighttime setting) … / Moved T probe, now taped to top of 27TMX	S2 WRD B54					20190803
		21	We		05:00		13:55	Charging Milwaukee Nicad A (details S2) …; Exec T>28 but relay did not open (we need to implement double-taps)	S2	NiCad Temp					20190821
				14:16			I manually switched off the charging (W9 Control Widget); Modified Action 'T>28' for double-tap (2000ms delay between)		Lab Temp					20190821
2019	Sep	4	We		08:46		17:43	Charging Milwaukee Nicad B (details S2) …; Exec T>28					20190904
		15		~	14:00			[W9-10] Wattmon_9 Battery Status Graph shows we lost connection from Heathkit to 6-pack / (probably loose clip lead on Heathkit); 6-pack begins to discharge	S1 W10					20190915
		18		~	04:10			[W9-10] Wattmon_9 and Wattmon_10 Battery Status Graph shows that both Wattmons stopped logging when 6-pack dropped to 6.2-6.4v (as per W9)		Inoperative					20190918
		22			07:55	~	08:20	[W9-10] I discovered that 6-pack was not being charged, totally dead, and Wattmon_9 and Wattmon_10 were not operating / Restored connection to Heathkit but charge current is of course only about 0.5 Amps / Attached BK_1 (13.8v/4.2a), now charging at about 3.5 amps ... / Decided to reduce current limit on BK to 2.1 Amps (in case one of the batteries is soaking up more than the others) / Now charging CC (Heathkit OFF, W9 and W10 attached and running)	S1 W10 S2	Lab Temp					20190922
		25	We		05:30	~	14:15	Charging Milwaukee Nicad B …; Exec T>28 (8 Hrs 45 Mins under charge) / Note that log.txt was corrupted and could not be read, rotated logs	S2	NiCad Temp					20190925
		26					[W9-10] On or after 9/26/19: Powered down (6-pack is so poor could not keep >=6 volts) / [later examination of logs showed it was running until 1/2/20]	W10	Available					20190926
2020	Jun	13	Sa	~	08:00			SD Card Copy: log20190926.txt is corrupted (skipped copy); T450s ChkDsk fixed invalid entries in \logs and recovered many file fragments to \Found.000 which I moved to the backup; WinMerge comparison with 20190605_0615 shows it was running until 1/2/20, and there are a lot of log files missing (due to corruption); Boxed and set aside for now	WP6-WP10					20200613_1300 L0W9M3O1		20200613
		14	Su	~	08:15			AWS is having problems copying 20200613_1300 backup from NAS to T400s: / There’s corruption/problems with files \logs\log20180513.txt and \logs\LOG201~2.TXT; Deleted those files from backup					20200614

## W10
Wattmons: W10	A					Wattmon_10: 54-10-EC-8C-1C-D0

Date/Time CST/CDT					Description	Other Sources	Status	Location	IP Address	Module	Firmware	OS	A1 Calibration	SD Card		Other Backups
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM					#	Copy
				Available	L	DHCP 90.0.0.110	M9 M1	2.1203	3.9	6/30/19	10	20220601_1315 L0W10M1M9 FW 2.1203 OS 3.9	20180623_1053 L0W10M8M9M10 ip_export_custom.cgi from Akash on W10
2018	Feb	19					"Ordered": Date of Akash's agreement to send me a MEGA at no charge as a "sponsor" of the SAPS/VAPS project	EML	On Order					20180219
2018	Apr	10					Shipped			UPS					20180410
		12					Received	WCA	Test…	L0	192.168.0.55					10			20180412
		14		~	13:00	~	13:30	Labeled; SD Card Copied; Newest file is 4/9/18 (the day before he shipped it); System Log shows FW 2.1100 and OS 2.25 / Firmware was updated 4/9/18, the device was tested for a few hours …; Modified /config/network.ini for DHCP (dhcp_enabled=0->1)	AED					2.1100	2.25			20180414_1800 L0W10 As From India		20180414
				~	13:45			Booted; CradlePoint Router configured to reserve IP 90.0.0.121-->90.0.0.110 (but W10 is still set for DHCP) / Initial test is perfect (and faster than the PRO)	AED CPSN	Burn-In		90.0.0.110					20180414
		15					Corrected Time; I8O8_1 Attached for Quick Test; Questions/Conclusions	AED				M8					20180415
				A10_1 Attached for Quick Test; Conclusions					M8M9					20180415
				LCD_1 Attached for Quick Test … but it didn't go well: Temporarily disconnected and disabled I8O8_1 and A10_1; FW 2.1100->2.1102 / Tried restoring "As From India" but SD card now corrupted and unreadable (needs to be formatted, but Windows format fails) / To/From Akash into 4/16/18 AM ...	AED EML	SD Card Corruption			M8 M9 M10	2.1102					20180415
		16					SD Card #10 successfully reformatted (NOT "Quick format"); "As From India" restored; /config/network.ini modified for DHCP; Booted OK / Restored some the missing logs for /logs/log.txt that happened to have been "cached" in Firefox before the incident yesterday	AED	LCD_1 'Quick Test'					20180416
		19	Th					LCD_1 now functioning as it should; I8O8_1 and A10_1 also functioning / L0W10M8M9M10 "4/15/18-4/20/18 ‘Quick Test’ [sic] of LCD_1 (SD Card Corruption)"		Burn-In					20180419
		20	Fr			~	15:07	Clear Cache …; Powered off		Assembly	MA2					20180420
		21	Sa					On for a few minutes to show Stacey					20180421
2018	May	3	Th		05:00			SD Card Copy (T450s)					20180503_1000 L0W10M8M9M10 OS 2.25		20180503
2018	Jun	19	Tu					Attempted to setup my.wattmon.com but "Device does not exist" / To/From Akash "Portals: new MAC addresses please" (1st get it exporting to portal); Powered on / Configured Data Export Settings and Data Collection / my.wattmon.com new device added and logging for all variables enabled (now logging to my.wattmon.com)	AED EML					20180619
		20	We					Configured Data Export Settings for ems.wattmon.com but problems exporting …	AED					20180620
		22	Fr	~	15:05			… Wattmon_10 Custom Export URL ems.wattmon.com/data/setdatacsv (now Actively exporting, but spurious errors in System log) …					20180622
				~	18:00	~	18:30	… exports are caught up, and now new type of ip.cgi system log entry (To Akash) ...	AED EML					20180622
		23	Sa	~	03:00	~	04:00	… ip.cgi and ip_export_custom.cgi from Akash uploaded to W10 but export errors continue (To Akash); From Akash (he'll check it remotely) …	EML AED					20180623_0335 Scripts from Akash (to attempt to fix custom export)	20180623
				~	06:30	~	06:45	… 06:08 From Akash (he logged in and fixed the ems export issue by modifying ip_export_custom.cgi)					20180623_1053 L0W10M8M9M10 ip_export_custom.cgi from Akash on W10	20180623
				C752_1 attached; Device names changed; Configured Current 1/2 roles; Calibrated C752_1 …	AED WCX				M8M9M5M10					20180623
		24	Su					… C752_1 calibration completed; Renamed roles for C752_1; Calibration of Vin/A1 started …					20180624
		25	Mo					… Vin/A1 calibration completed					6/25/18				20180625
		26	Tu	~	05:00			SD Card Copy ...; Roles added for A10; FW 2.1102->2.1108; Configured as per Wattmon_9	AED					2.1108				20180626_1000 L0W10M8M9M5M10 OS 2.25 Akash		20180626
		28	Th			~	15:55	"FireFox prompts to download System Log": Firmware downgraded 2.1108->2.1102; To Akash "System Log will not open in browser on MEGA" … / SD Card Copy; WinMerge compare and uphp.ini corrected (line "relay_mode=1" was in the wrong section, oops!); Problem with FireFox is gone!	AED EML					2.1102				20180628_2055 L0W10M8M9M5M10 OS 2.25 Akash		20180628
				~	16:45			FW 2.1102-> 2.1108; No problem with FireFox and .txt files	AED					2.1108					20180628
		29	Fr					Configured Roles for I8O8_1 (DO1->DO8); Action added for contactor on/off					20180629
2018	Jul	1	Su					Frequent Reboots (and FireFox Prompts Explained) …					20180701
				I302_2 attached but Not Detected (L0W10M8M9M5M10M4 and L0W10M8M9M4M5M10)					20180701
				… Troubleshooting Many Reboots as per Akash: FW 2.1108->2.1105; Disabling Devices one at a time and observing …	EML AED					2.1105					20180701
				~	19:00			SD Card Copy; Spurious file /ÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑÑ 6/29/18 9:47 PM, contents are two System Log entries "Exception at 9D0F3530" and "Task: cronmin.cgi, Memcpy=137" (Frequent Reboots problem, yet troubleshooting); Attempted deletion of spurious file from W10 (File Manager) but "Unable to delete directory %EF%BF%BD%EF%BF%BD%EF%BF%BD%EF%Bdir" / Deleted spurious file on SD Card on T450s; %SoC went to zero, corrected to 100%	AED					20180702_0000 L0W10M8M9M5M10 OS 2.25 Akash		20180701
		3	Tu					… Troubleshooting Frequent Reboots conclusion: The frequent reboots are caused by having the dashboard open on more than one computer (system is stable now with all Devices enabled); FW 2.1105->2.1108					2.1108					20180703
		9	Mo					Action "DO1 Pulse" added (to test)					20180709
2018	Aug	12	Su	~	05:50			SD Card Copy					20180812_1050 L0W10M8M9M5M10 OS 2.25 Akash		20180812
2019	Mar	28			21:30			Powered OFF (I haven't been able to work on the SAPS for more than 7 months)					20190328
2019	Jun	23	Su	~	05:00			Removed from SAPS equipment box; SD Card Copy	AED					20190623_1000 L0W10M8M9M5M10 OS 2.25 Akash		20190623
				~	05:45			Applied to W100 project testing; A1 power from 12v 6-pack; Rotated log; Control Panel settings partially reviewed (Master Configuration) / Firmware updated 2.1108->2.1135 (SSC of all the firmwares skipped over); After firmware update could not connect	AED SSC	W100 Test	L0			2.1135					20190623
				~	07:00			SD Card Copy	AED					20190623_1200 L0W10M8M9M5M10 OS 2.25 Akash FW2.1135 Won't Connect		20190623
				~	07:30	~	08:45	SD Card modified: OS 2.25 As From India with current logs and selected config files; Still can't connect					-					20190623_1230 L0W10 OS 2.25		20190623
				~	08:45	~	09:08	SD Card modified: FW 2.1108 files copied from '20190623_1000 …” to SD card (all are modified 7/3/18) …; Power applied while holding down the reset button (this reapplies the firmware from imagez.hex); Logged in OK; Now FW 2.1108 and OS 2.25; SD Card Copy					2.1108				20190623_1430 L0W10 FW 2.1108 OS 2.25		20190623
				Installed ID 401 "WattmonOS 3.2 FULL No Config (Mega Only)" released 6/19/19; SD Card Copy					3.2			20190623_1500 L0W10 FW 2.1108 OS 3.2		20190623
				~	10:25			FW 2.1108->2.1135 released 5/15/19; His "Firmare Manager" still doesn't quite work right … and can't connect; SD Card Copy					2.1135				20190623_1530 L0W10 FW 2.1135 OS 3.2 Won't Connect		20190623
				~	23:35	~	23:45	Restored FW 2.1108 by copying (5) files from 20190623_1500 L0W10 FW 2.1108 OS 3.2 to SD Card (md5.txt, firmwarez.tar, changelog.txt, imagez.hex, nvram.dat, all modified 7/3/18) and applying power while holding down the reset button / Logged in OK; Rotated log …; FW 2.1108->2.1130 released 4/15/19; Can't connect; Reset boot again; Can't connect; SD Card Copy					2.1130				20190624_0500 L0W10 FW 2.1130 OS 3.2 Won't Connect		20190623
		24	Mo	~	00:10	~	00:17	Again, restored FW 2.1108 as above …; FW 2.1108->2.1123 released 11/22/18; Logged in OK; Rotated log; SD Card Copy					2.1123				20190624_0530 L0W10 FW 2.1123 OS 3.2		20190624
				~	00:35			FW 2.1123->2.1126 released 12/20/18; Logged in OK; SD Card Copy					2.1126				20190624_0545 L0W10 FW 2.1126 OS 3.2		20190624
				~	00:55			FW 2.1126->2.1128 released 1/5/19; Logged in OK; SD Card Copy (this is good one to keep, as it has only the basic configuration, no actions, no devices, no packages)					2.1128				20190624_0605 L0W10 FW 2.1128 OS 3.2		20190624
				~	01:20			FW 2.1128->2.1133 released 5/2/19; Unable to connect; Reset to reload firmware; Unable to connect; SD Card Copy					2.1133				20190624_0640 L0W10 FW 2.1133 OS 3.2 Won't Connect		20190624
				~	01:45		02:12	Restored FW 2.1128 by copying (5) files as above and reset to reload firmware / I can't see it is worth while to try to update the firmware to 2.1129 Beta, and 2.1130 and 2.1135 didn't work ...; To Akash and support team	EML					2.1128					20190624
				~	02:25	~	04:00	Rotated log; Reviewed and modified configuration (Master Configuration) …; Completed review up to Packages (but skipped Widgets) / SD Card Copy	AED					20190624_0900 L0W10 FW 2.1128 OS 3.2		20190624
				~	04:20	~	11:50	Moved previous logs to logs/archive (T450s); SD Card Copy ...; Rotated log					20190624_0925 L0W10 FW 2.1128 OS 3.2		20190624
				~	12:30	~	13:45	Completed review and modification of configuration (Master Configuration) …; SD Card Copy	AED					20190624_1845 L0W10 FW 2.1128 OS 3.2		20190624
		25	Tu			~	23:00	Attached C252_1; Calibration using BK_1 …; Completed calibration	AED WCX S2				M1					20190625
				~	23:15	~	01:15	Attached C252_2; Calibration using BK_1 …; Completed calibration					M1M2					20190625
		26	We	~	01:30	~	03:30	Attached A10_1; Calibration checked with BK_1 …; No changes made; Log rotated; SD Card Copy (Device Name "L0W10" has not been changed yet)					M1M2M9					20190626_0845 L0W10M1M2M9 FW 2.1128 OS 3.2		20190626
		27	Th					Integrated Wattmon_10, C252_1, C252_2 and A10_1 into test setup with Trace inverter; Configuration of Device Name and roles for parallel test …					20190627
				C252_1 Current 2 Divider 200 -> 100 / (using one loop to double range to 30 amps, this should not affect accuracy of calibration, but at this point I don't care if it does)	AED WCX					20190627
		28	Fr					Configured Roles; C252_1 Current 2 Invert 0 -> 1 (this should not affect the calibration, as I'm still using positive upward flow, but group Grid is positive and needs to be negative); ajax_refresh_time 0.65->0.9; Finished review of Config; List of Issues yet to resolve in TODO					20190628
				~	07:30			SD Card Copy					20190628_1230 L0W10M1M2M9 FW 2.1128 OS 3.2		20190628
				~	08:01	~	08:15	FW 2.1128->2.1135; Can't Connect, hard reboot, won't connect; SD Card Copy					2.1135				20190628_1315 L0W10M1M2M9 FW 2.1135 OS 3.2 Won't Connect		20190628
				~	08:30	~	09:00	Restored FW 2.1128 by copying (5) files as above (all modified 6/24/19 00:54-00:55) and reset to reload firmware … / To Akash with 20190628_1348 FW 2.1128 to 2.1135 For Akash.zip which has _1230 and _1315 SD Card copies	EML					2.1128					20190628
				~	09:55		10:30	Battery capacity for 200w DR test calculated (97 AH) and configured …; Began 200w DR test	AED WRD					20190628
				W9-10	IMG					20190628
		29	Sa	~	09:30	~	13:00	Up and running on Series Test setup / Added Data Collection for A10_1_v1 (this is the only way to get individual wattages for the two batteries/W100s, the data must be put into Excel and massaged, as the Live Energy View is based on the total voltage of the battery bank which is nominal 24v) / Added logging for A1 Voltage (because I don't trust Akash's System Variable "Battery Voltage") / C252_1_current2 Divider 100 -> 200 (using calibrated range of 0-15 amps for the Series Test) / Began to calibrate A1/Vin for 24vdc nominal range but could not connect to W10 (I moved it closer to the computer) / Disgusted, went to take a break, will continue this ASAP ...	AED WRD WCX					20190629
		30	Su	~	01:00	~	02:35	… Can't connect; SD Card Copy; log.txt shows system is booting but nothing after runonce loads /package/VariableWidget.cgi / Comparison of 20190628_1230 with 20190630_0615 doesn't reveal any corruption / W10 moved back to W100 test setup (A1/Vin ~24v, Modbus connections as they were); Logged in OK / Changed name of SD Card Copy (was named with "Won't Connect"); Unplugged Modbus, Logged in OK; Rotated log / Moved W10 close enough to BK_1 to calibrate (powered by BK_1), Logged in OK; Attached Fluke directly to A1/Vin and GND and lost connection / Grounded GND via BK, won't connect; Reset NetGear 1Gbps switch, won't connect; Rebooted CradlePoint router, won't connect / Rebooted Network (rear room), won't connect; Noticed no LAN indicator lights (bad cable connection), reseated both ends, Logged in OK / This brings into doubt the results with the firmware upgrade problem, as the symptoms are the same (TODO) / Also could have been the cause of the long delays getting to the Dashboard, if the hardware Ethernet level was getting a lot of errors it would keep retrying over and over again until it finally got through (TODO, will watch for this symptom); Log rotated	S2					20190630_0615 L0W10M1M2M9 FW 2.1128 OS 3.2		20190630
				~	03:45	Calibration of A1/Vin on BK_1 ...; W10 moved back into W100 Test setup	AED WCX S2					6/30/19				20190630
				~	07:00	Dashboard Widgets reordered; Roles modified so that Relay Output 1-4 don't show in Control Widget; (Master Configuration) ...; SD Card Copy	AED					20190630_1200 L0W10M1M2M9 FW 2.1128 OS 3.2		20190630
				I3O2_1 Attached, Roles and Logging configured					M1M2M3M9					20190630
				RL5 wired up to power both WP4 and WP5 from T1 Main (we'll lose charge if we have a power failure, but I don't have enough UPS to keep it up without setting up the Trace on the Subaru batteries); Action 'SoC<50%' created and tested					20190630
				14:00	I3O2_1 out1 and out2 wired to trim resistors (Major and Minor); (2) Actions for Trim created and tested (we won't use the 2nd trim, Role modified to not show it in Control Widget) ...; Began Discharge for 1st Series Test (200w); Details and summary of test …	AED WRD					20190630
2019	Jul	1	Mo		00:52			From Akash, he fixed the "Won't Connect after FW upgrade" problem with FW 2.1138 released 7/1/19	EML					20190701
				13:25	1st Series Test Concluded, details; W10 is logging	WRD					20190701
		2	Tu				11:00	Battery and Charge Settings corrected; Role for I3O2_1_out2 modified to show in Control Widget; Globals LL and LH added to Variable Widget / Actions modified for new trim system; Tested trim system; Dashboard Widgets layout optimized ...; Began Discharge for 2nd Series Test (200w)	AED WRD					20190702
				12:59			2nd Series Test failed due to Watchdog Timeout reboot (Load and logging continued through the night)	WRD					20190702
		3	We		03:54			2nd Series Test Concluded (load killed)					20190703
				~	06:40	Action 'Set Load Limits 198.5/201.5' modified to run whenever LL=0 (this will survive a reboot) …; SD Card Copy	AED WRD					20190703_1140 L0W10M1M2M9 FW 2.1128 OS 3.2		20190703
				~	07:15	~	07:40	SSC available FW versions from 2.1128 to 2.1139 (which was just released today, I'm not going to install it, "FTP and SFTP Support") / FW 2.1128->2.1138 (Akash "Bug fix for DHCP mode") / Also note that in 2.1133 Akash "Added ability to set role variables in devices using mb_set_dev_var" (TODO, if this allows me to improve Variables Widget display, which is limited to Roles and non-array Globals then I need to know about it) / Logged in OK (Akash fix effective) … / To Akash "Re: MEGA OS 3.2 doesn't work with FW 2.1130, 2.1133 or 2.1135" where I also bring up the issue with battery_cur_ah=0 at every reboot	SSC AED WRD					2.1138					20190703
				Then I noticed that now that the FW upgrade was installed it is no longer setting battery_cur_ah=0 at every reboot; Follow up To Akash / Set battery_cur_ah=102, rebooted several times, all is OK	EML					20190703
				08:24	Data Collection for CSV Log 'Disk write interval' 3->1; But this writes to the SD card every 2 minutes (it's buffering 1 minute's data, then on the 2nd minute it writes 2) ...; To Akash 'Data Collection "Disk write interval"'	AED EML					20190703
				09:00			Began Discharge for 3rd Series Test (200w)	WRD					20190703
		4	Th		08:55			3rd Series Test Concluded (Success w/minor problems); SD Card Copy; Rotated Log					20190704_1400 L0W10M1M2M9 FW 2.1138 OS 3.2		20190704
				Calculated and set battery capacity AH; Action modified for 297.75/302.25 (4.5w trims)	AED WRD					20190704
				14:30			Began Discharge for 4th Series Test (300w)	WRD					20190704
		5	Fr	~	17:40	~	18:25	Modified Actions to add double-taps for Sw On/Off; Modified Action 'SoC<50%' for delay 5	AED WRD					20190705
		6	Sa		11:02		13:02	2 Hr Equalization with BK_1 …; Ended, logging continues in Float	WRD S2					20190706
		7	Su	~	03:00			4th Series Test Concluded (Success w/minor problems); SD Card Copy; Log rotated	WRD					20190707_0800 L0W10M1M2M9 FW 2.1138 OS 3.2		20190707
				Battery and Charge settings modified (99 -> 107 AH); Action modified 'Set Load Limits 297.75/302.25' -> 'Set Load Limits 99.5/100.5' …	AED WRD					20190707
				Action modified 'Set Load Limits 99.5/100.5' -> 'Set Load Limits 99.2/100.8' …					20190707
				08:00			Began Discharge for 5th Series Test (100w)	WRD					20190707
		8	Mo	~	06:50			5th Series Test Concluded (Inadequate Trim); Log rotated					20190708
				Actions improved to "repair" Control Widget display of state of RL5 (and improve logging), other improvements	AED WRD					20190708
				10:18			Began Discharge for 6th Series Test (100w)	WRD					20190708
				W9-10	IMG					20190708
		9	Tu		12:00			6th Series Test Concluded; SD Card Copy; Left powered off	WRD					20190709_1700 L0W10M1M2M9 FW 2.1138 OS 3.2		20190709
		11	Th	~	19:05			Up and running, powered by 6-pack (Heathkit), A10, WP5 and APC_1 on 27TMX; C252_1 attached but not being used / C252_2 monitoring WP5 charge and load; Rotated log	S1 WP5 A32 B54 WRD					20190711
				~	21:15	Group Wind NOT visible; Role settings modified, A10_1_v1 Definition 'Voltage', C252_1_current1 and C252_1_current2 'Not Grouped', added role for C252_2_current2 (load); Variables Widget modified; Rotated log; Calibration of C252_2_current2 modified (inverted); Modified Battery settings	AED WCX					20190711
				~	20:45			Setup for 7th Test (100w)	WRD					20190711
		12	Fr		02:00			Began Discharge for 7th DR Test (100w)					20190712
		13	Sa		01:30			7th DR Test Concluded (100w); SD Card Copy					20190713_0650 L0W10M1M2M9 FW 2.1138 OS 3.2		20190713
				/config/battery.ini charge_efficiency=101.7; Setup for 8th Test (50w), LL=49.5, LH=50.5, battery capacity 107 AH	AED WRD					20190713
				03:00			Began Discharge for 8th DR Test (50w)	WRD					20190713
		14	Su	~	06:45			8th DR Test Concluded (50w)					20190714
				Action 'After Reboot' modified for LL=149 & LH=151; Battery capacity changed	AED WRD					20190714
				08:00			Began Discharge for 9th DR Test (150w)	WRD					20190714
				W9-10	IMG					20190714
		15	Mo		00:42			Action ‘After Reboot’ modified 149/151 -> 148.8/151.2 LL/LH	AED WRD					20190715
		16	Tu	~	08:15			9th DR Test Concluded (150w); W10 Continues logging	WRD					20190716
		17	We	~	05:30			C252_2 has been recalibrated; Set Charge Efficiency 100% and battery_cur_ah=99; Now maintaining 100% SoC in Float	AED WCX WRD					20190717
				Action 'After Reboot' modified for LL=49.6 & LH=50.4; Battery capacity changed	AED WRD					20190717
		18	Th					Action(s) added and modified to insure that if battery_cur_ah changes more than it should that it is reset (including changes to Variables Widget) / [Watchdog] …					20190718
		19	Fr					Watchdog Action modified; Charge Efficiency modified (battery.ini)					20190719
		20	Sa					Charge Efficiency modified (battery.ini)					20190720
				Discovered & corrected NVRAM corruption: I was puzzled as to why Action 'After Reboot' was not loading the NVRAM values for AH1 and AHD / /scripts/tests/nvram.cgi showed a lot of unexplained issues / Wattmon_10 device calibration looked good, but I couldn't find the values in NVRAM / (no idea how A1/Vin calibration was working right, but it was) / There were NVRAM entries for AH1 and AHD but none of them were Status=128 (that means that is the active entry, Status=0 is an entry that has been replaced / /scripts/test/nvram.cgi?defrag=1 reduced the entire set of over 1000 items to just Item 0 to Item 7, and some of the A1/Vin calibration entries were gone / Note that Calibrate works with cached values for NVRAM, it does write the new ones, but a reboot is required after defrag to see the actual NVRAM values / Restored Wattmon_10 calibration values OK (SSC) / Now Action 'AH Watchdog Update1 Change' is able to write AH1 and AHD, and 'After Reboot' is restoring them / Note that /changelog.txt mentions NVRAM corruption and defragmentation issues fixed in FW 2.1115, 2.1118 and 2.1129 / Evidently the corruption was introduced during the time before I upgraded to FW 2.1138	AED WRD SSC					20190720
				Watchdog Actions (still working on logic) …	AED WRD					20190720
				After several hours of writing AH1, AH0 and AHD to NVRAM the corruption issues returned …					20190720
		21	Su					… RL5 is Status=128, but AH1, AH0 and AHD do not have a valid entry in NVRAM; defrag; RL5 was removed as well as AH1, AH0 and AHD / Wattmon_10 calibration values are OK; To Akash 'NVRAM Corruption Continues'	EML					20190721
				I'm still working on debugging NVRAM replacement scripts /config/ini_get.cgi and ini_set.cgi; Actions modified	AED WRD					20190721
		22	Mo			~	06:40	From/To Akash 'Re: NVRAM Corruption Continues'; Deleted \nvram.dat / Powered up with reset button (to reload FW 2.1138, and NVRAM will be empty then); Restored previous Wattmon_10 calibration values / NVRAM is clean, no spurious items / Akash wanted me to rerun the tests using NVRAM, but I've decided I'm sick and tired of dealing with restoring calibration values and so I will avoid using NVRAM for the DR Test Setup / /scripts/tests/nvram.cgi?backup=1 (/nvram.dat created) ...; SD Card Copy	EML					20190722_1140 L0W10M1M2M9 FW 2.1138 OS 3.2		20190722
				~	07:05	FW 2.1138->2.1141 [2.1139 'FTP and SFTP Support' 7/3/19; 2.1140 'Fixes for FTP and increased roles per device from 40 to 60' 7/5/19; 2.1141 'Bug fixes that caused watchdog reboots in some sites' 7/20/19] …; SD Card Copy					2.1141				20190722_1205 L0W10M1M2M9 FW 2.1141 OS 3.2		20190722
				OS 3.3 Update installed [414, WattmonOS 3.3 Update (from 3.2) - Mega and M2, Update from WattmonOS 3_2, 7/22/19] / Error during OS Update (SSCs); Live Energy transition from OS 3.2 to 3.3 (SSC, balance is now being rounded/truncated) / To Akash 'Re: OS 3.3 Update errors'; Changes to Data Collection (SSC, logging has been wiped out); Follow up To Akash	SSC WRD EML					3.3?					20190722
				22:41			From Akash 'Re: OS 3.3 Update Errors': "It seems like one of the language files did not get installed. Were you on 2.1140 or 2.1141 when you installed it? … If need be, run the OS3_3 full. I have tested the upgrade here and it seems to work fine on the latest fw."	EML WRD					20190722
		23	Tu		00:34		00:47	To Akash 'Re: OS 3.3 Update Errors': "I had upgraded to FW 2.1141 before installing the OS 3.3 Update." … / From Akash "In that case try the full install…"					20190723
				~	01:40			SD Card Copy; Restored files from 20190722_1205 L0W10M1M2M9 FW 2.1141 OS 3.2 (all except /logs); SSC Live Energy / Installed OS 3.3 FULL "413, WattmonOS 3.3 FULL No Config (Mega and M2), Updates and bug fixes" 7/20/19 … after 45 mins to an hour I refreshed the page / /wattmonos3.3tar exists (4226388 bytes, which is less than 4226924 bytes shown on WattmonOS Manager page); Rotated log; Rebooted / Still OS 3.2; Closed Dashboard; Again, install 413; Uncrompressing ended with same error as before (SSC); To Akash 'Re: OS 3.3 Update errors' / /wattmonos3.3tar is 4226388 bytes, which is less than 4226924 bytes shown on WattmonOS Manager page; Trim system is working / .csv looks good; Reboot, OS is 3.3; File Manager uncompressed /wattmonos3.3.tar; That stops with the same error, but on a different line (SSC) / Reboot; To Akash w/SSC	SSC WRD EML					3.3			20190723_0640 L0W10M1M2M9 FW 2.1141 OS 3.3 corrupted		20190723
				~	04:25			From Akash 'Re: OS 3.3 Update Errors': "The issue seems to be due to a missing file in the lang folder. Can you put this in the root and uncompress it please?" (lang.tar.gz attached); SD Card Copy; To Akash 'I'm working on that,' discrepency in wattmonos3.3tar and 'why doesn't a "Full" OS package include the language files?'; Copied lang.tar.gz to root; From Akash concerning lang files "It does include them. However, apparently the extract failed. I have to look into it."; Rotated log; Uncompress /lang.tar.gz	EML WRD					20190723_0925 L0W10M1M2M9 FW 2.1141 OS 3.3		20190723
				~	04:55			SD Card Copy; WinMerge compare with 0925 shows that no language files were missing / To Akash "I uncompressed /lang.tar.gz but WinMerge comparison shows that there are no differences to the /lang files, i.e., I had all of them already." / Uncompress wattmonos3.3.tar, same error as before / To Akash "After installing your /lang.tar.gz I tried to uncompress wattmonos3.3.tar again, same error as before." / Note that system appears to be working but I don't trust that OS 3.3 is fully installed / From Akash "Hmmm. Can you try and extract it all via your PC and see if that solves it?"					20190723_0955 L0W10M1M2M9 FW 2.1141 OS 3.3		20190723
				~	12:00			SD Card Copy					20190723_1700 L0W10M1M2M9 FW 2.1141 OS 3.3		20190723
				~	12:15			Created another Copy; On Copy, PeaZip used to extract /wattmonos3.3.tar to /wattmonos3.3, renamed as .tar.tar and then extracted that "To Here"; WinMerge compare 1700 to 1715 and there are no files added or changed (they all already existed); Just to be sure I extracted with option "overwrite existing files" (which took a little longer) and WinMerge compare 1700 to 1715 shows again that there were no files missing before PeaZip extraction (i.e., the uncompress on W10 ended with an error, but all files were extracted as they should have been); Renamed Wattmon Backups made recently (they're all not "corrupted"); Deleted Wattmons Backup PeaZip Extract as we don't need it; System is stable, and appears to be functioning correctly; To Akash 'Re: OS 3.3 Update errors'	EML WRD					20190723_1715 L0W10M1M2M9 FW 2.1141 OS 3.3 … DELETED		20190723
				To Akash 'battery_cur_ah & SoC randomly corrupted'	EML					20190723
				99 AH Capacity; LL/LH 148.8/151.2	AED WRD					20190723
		24	We					One last attempt to fix scripts and actions to use DR.ini instead of NVRAM, but I couldn't find something that doesn't trigger an Exception when ini_set.cgi is run from AH Watchdog1 Change / Actions for Watchdog disabled, and After Reboot modified to use NVRAM for RL5; End Discharge disabled					20190724
				03:00			Began Discharge for DR Test #10, 150w to as Low as APC will Go	WRD					20190724
				05:46			From Akash 'Re: battery_cur_ah & SoC randomly corrupted': "I am not really sure how it happens. However, will keep it in mind and see if I can come up with a failsafe, i.e. NVRAM + SD when I get a bit of space."	EML					20190724
		28	Su	~	15:50			Concluded DR Test #10 (150w to as Low as APC will Go); SD Card Copy; Rotated log	WRD					20190728_2050 L0W10M1M2M9 FW 2.1141 OS 3.3		20190728
				Configuration for DR Test #11 (50w to as Low as APC will Go)	AED WRD					20190728
		29	Mo		00:09			From Akash "Can you please update to 2.1143 - I think the NVRAM issue should be resolved. It had (unfortunately) to do with a processor bug that had to do with page writes - after switching to word writes the issue cleared up. Took a while to fix."	EML					20190729
				09:00	Charge Efficiency 100->100.5 ...; Began Discharge, DR Test #11 (50w to as Low as APC will Go)	WRD					20190729
				13:48			To Akash: "I'll update soon and I'll let you know if I have any more NVRAM corruption." / Asked for specs on NVRAM concerning number of writes (because I might be writing 50 bytes every minute or 500,000 times per year)	EML					20190729
		30	Tu		23:17			From Akash: Each byte has 100,000 write cycles minimum (only applies to cell erasures); Details on how to calculate the number of write cycles for two different scenarios; For 50 bytes we have a minimum of 32 million cycles, or 64 years; "More than enough for your application."					20190730
		31	We		01:09			To Akash: "Thank you very much for your insight into whether or not I could use NVRAM in this way (new values every minute)" / Mentioned problems running script ini_set.cgi from an Action; Suggestion to add Action choices to ini_set/get values to/from INI/globals / Offered 3 PROs for 1 MEGA					20190731
				~	08:00			Concluded DR Test #11 (50w to as Low as APC will Go); SD Card Copy; Rotated log	WRD					20190731_1300 L0W10M1M2M9 FW 2.1141 OS 3.3		20190731
				10:00	Configuration for DR Test #12 (100w to 10% WSoC): LL/LH=99.2/100.8; battery_ah_end=battery_ah*0.1; battery_ah=102; CE=100% / Charge Efficiency 102.5 …; Began Discharge, DR Test #12 (100w to 10% WSoC)	AED WRD					20190731
2019	Aug	2	Fr	~	18:55			Concluded DR Test #12 (100w to 10% WSoC, but APC Quit @ 12.8% WSoC); SD Card Copy; Rotated log	WRD					20190803_0000 L0W10M1M2M9 FW 2.1141 OS 3.3		20190802
				~	21:15			Verified version of cronmin.cgi that is being used on W10 (it's writing Data Collection to SD every minute): Winmerge compare of 20190722_0351 cronmin.cgi from Akash with version in 20190803_0000 L0W10M1M2M9 FW 2.1141 OS 3.3 and they are identical / Evidently, between the time when Akash said it wasn't yet in the Full OS 3.3 and when I installed the Full OS 3.3 Akash went and updated cronmin.cgi in that OS package to the version I was emailed direct from Akash					20190802
				~	21:55	~	22:10	FW 2.1141->2.1145; Should resolve any lingering NVRAM issues (see 7/29 emails); Checked calibration values (OK) and nvram.cgi	EML SSC					2.1145					20190802
		4	Su				21:00	Charge Efficiency 102.5->100; battery_ah=105; battery_cur_ah=105; Actions modified; Variables Widget Configured / Roles modified (to remove I302 outputs from Control Widget) …; Began Discharge, DR Test #13 (5.100 Amps CC to 10.5v as per man’f specs.)	AED WRD					20190804
		6	Tu	~	23:00			Concluded DR Test #13 (5.099 Amps CC to 10.5v as per man'f specs.); SD Card Copy; Rotated Log	WRD					20190807_0400 L0W10M1M2M9 FW 2.1145 OS 3.3		20190806
2019	Sep	15		~	14:00			W9-10	S1 W9					20190915
		18		~	04:10					20190918
		22			07:55	~	08:20		S1 W9 S2					20190922
		26					W9-10	W9	Available	L					20190926
2020	Jun	13	Sa	~	09:00			SD Card Copy: Comparison with 20190807 / \daily_kwh.csv is missing information before 6/22/19 and after 7/10/19 clock was set to 1/0/70, then 9/21/19 and 1/3/20; Logrotate 9/5/19 / I see no corruption to system files, only data files / Decided to clean up the SD Card (it has log files created when clock was bad which are obviously erroneous) / Deleted \logs folders 1970, 2021 and 2027; Moved \logs\log.txt to \logs\archive\log20200613.txt; Created \logs\log.txt with 1st line note	WP6-WP10					20200613_1400 L0W10M1M2M9 FW 2.1145 OS 3.3		20200613
				~	15:30			SD Card Copy (after above modifications, before trying to boot it up)					20200613_2030 L0W10M1M2M9 FW 2.1145 OS 3.3		20200613
				Set Charge Efficiency 100% (it was some non-integer value); Peukert Constant is already 1; Actions for trim enabled (but I’m not going to use them)	WP6-WP10					20200613
				~	17:15	~	21:45	Used for quick DR tests of WP6-WP10 (B57-B61) as per WP6-10A Misc	B57-B61	W100 Test					20200613
				~	21:45			Continuing test of WP10/B61 (we have new harness testing to do yet, will keep it running)					20200613
		15	Mo		03:00			Wattmon_10 powered down	WP6-WP10	Available					20200615
2021	Oct	19	Tu					On the bench to use for TurboNet MikroTik project (Schauer 2512, Traco DC-DC) / Configured Roles, C252_1_current1 "Solar" (3, green), C252_1_current2 "Grid" (2, red) / Configured Variable Widget (Package Manager) to show C252_1 currents on dashboard / Configured Data Collection, added Group ID 2 named "0" (because I couldn't get it to take name "Simple"), just A10_1_v1, C252_1_current1 and C252_1_current2; Backup	T48P A32	Applied	L0	DHCP 90.0.0.110	M9 M1					20211019_2030 L0W10M1M9 FW 2.1145 OS 3.3		20211019
		24	Su					Began setting up testing of Schauer JAC2512 (SBC_1)	BC6					20211024
				Video sent to Pavel via Viber	IMG					20211024
		26	Tu					Control Panel > Widgets: Rearranged for order Variables, Charge, Discharge, Control, Battery; Widths reduced (all five widgets "above the fold")					20211026
				Control Panel > Battery: Changed battery capacity 105->225 AH					20211026
		28	Th			~	12:40	Configured to add logging for Battery Cur AH and Battery Percent (Control Panel > Data Collection > Data Points (4) and (5)					20211028
	Nov	1	Mo	~	05:40	~	06:03	Backup ...; Rotated system log					20211101_1040 L0W10M1M9 FW 2.1145 OS 3.3		20211101
		7	Su	~	02:39	~	02:45	Time Settings adjusted for CST (UTC-6); This resulted in a logging discontinuity ...; Rotated system log					20211107
		11	Th	~	06:00	~	10:00	Logging improved, Data Collection Group (2) named "v4ac2wc1ad2wd1b2"; Live Energy improved by editing Groups and Roles / Live Energy legend shows (Green) Charge, (Red) Discharge, (Blue) Balance	T48P					20211111
		13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup	IMG					20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)					20211114
	Dec	1	We	~	12:30	~	12:55	Backup ...; Rotated system log					20211201_1830 L0W10M1M9 FW 2.1145 OS 3.3		20211201
		8	We					One Wire temperature sensors T_6, T_7, T_8 and T_9 attached and all (4) sensors are being detected in scan	DRD O6 O7 O8 O9					20211208
		9	Th					Configuration for (4) T sensors: Roles, Temperature, Package Manager (VariableWidget), Data Collection, Graphs / Also improved Live Energy and Battery Status graphs (they were not working because they were still pointing to the original CSV log) / (4) sensors have intermittent and random problems "reading zeroes" (not communicating properly)	DRD SSC O6 O7 O8 O9					20211209
		10	Fr	~	23:30			Backup ...; Rotated system log					20211211_0530 L0W10M1M9 FW 2.1145 OS 3.3		20211210
		11	Sa	~	00:00			NVRAM examined (SSC); SSC of firmware update page (nothing notable for my present concerns with the T-sensors) / FW 2.1145->2.1203 (12/6/21); T-sensor errrors continue; Examined /changelog.txt (nothing notable for my present concerns) / NVRAM and calibration values look to be the same	DRD SSC O6 O7 O8 O9					2.1203					20211211
				~	00:45	~	01:05	OS Updated: Currently 3.3; Available Package List shows only one that is obviously applicable / {ID 477; WattmonOS 3.9 FULL (Mega MINI2 M2 and MINI3); Latest changes and integration of power control package; Version 3.9; 10/13/20}, / all the other available packages beyond 3.3 do not say "Mega" / Installed 3.9 which crashed after about 10 mins with "Unknown function: lang Error on line 137: Unknown function: lang Error on line 137: Invalid function" (SSC) / I rebooted and header says "WattmonOS 3.9 (WM-MEGA)"; Installed 3.9 again, same error, same place (SSC) / (4) temperature sensors appear to be stable (no zeroes)					3.9?					20211211
				~	01:40			SD Card Copy; Extracted /wattmonos3.9.tar using PeaZip and WinMerge compare with files on SD card (all files were extracted from the .tar on W10); Therefore OS update is good; Also looked at WinMerge differences with OS 3.3 backup (nothing major for my concerns, changes to Time settings page, Configure Graph page is still "fucked up"); Temperature problems may have been fixed by FW & OS updates [problems came back later while I was sleeping], I've seen no zeroes, but will have to observe longer; Sensors placed in meaningful places in setup and still no zeroes	DRD O6 O7 O8 O9					3.9			20211211_0740 L0W10M1M9 FW 2.1203 OS 3.9		20211211
				~	12:05			Awoke and booted T400s/T450s; W10 not responsive (cycled power and regained access); T-sensor problems came back at about 09:10 (SSC) / Tried changing the polling intervals for the 1-Wire sensors 300ms, 1000ms, 60000ms, 700ms (nothing helped) / Added 2.7Kohm resistor between 5V and OW pins (so now the pullup is ~1.35K) and suddenly everything became "golden" / The stronger pullup resistor may have fixed it; Set T datalog points as MIN (so that any data error zeroes will show in log while testing) / Currently everything OK with ~1.35K, 700ms poll intervals and logging MIN	DRD SSC O6 O7 O8 O9					20211211
		12	Su	~	07:15			W10 was on last night, logging; No intermittent/random problems reading the temperatures; There was one data spike on T_8 Battery1 to "-1.0" but other than that there are no zeroes; For now I'm assuming the problems were fixed by the stronger pullup resistor					20211212
				~	08:22	~	08:23	O6-O9: A few zeroes for two minutes, after that all OK	DRD O6 O7 O8 O9					20211212
				~	18:57			Temperatures were reading AOK, then suddenly O6-O9 reading zeroes; Cycled power W10 and scanned OW bus; W10 powered off for ~10m / Nothing helped (all zeroes)					20211212
		13	Mo					Removed O6-O9; Disabled T_6-T_9; Installed O1 (T_1); Scan and Configured Role as T_8 Battery1; Stable	DRD O1					20211213
				Lots of details here, so see FTR: Reinstalled O6-O9 (inop); Cut off O9; O6-O8 inop; Cut of O6; O7-O8 AOK; Individual testing of O9 and O6 (inop); O2 OK; O3 and O10 not detected in scan; O4 OK; CONCLUSIONS I have a lot of bad sensors, they all need to be carefully tested; White sheet design W10 Sensor Rack (to make individual and group testing easier, and will be used on the bench); Changes to configuration for OWs not noted in MASTER CONFIGURATION (will do this once testing is complete); Assembled Sensor Rack (ready for testing sensors); T-Sensor Rack	DRD IMG O2 O3 O4 O6 O7 O8 O9 O10 WS					20211213
		14	Tu					O7 & O8 harness died (pulled, they need to be individually tested)	DRD O7 O8					20211214
				Testing all sensors individually on Sensor Rack (unless they already passed) / Configuration changes for Temperature, Roles and Graphing for each one (not noted in MASTER CONFIGURATION, see OWs for details)	DRD O3 O4 O5 O6 O7 O8 O9 O11					20211214
				~	23:26			O4, O5, O7, O8 and O11 all working ...; Sensors placed in meaningful places (edited Roles and Temperature Graph Titles to add locations)	DRD SSC IMG O4 O5 O7 O8 O11					20211214
		15	We	~	10:55	~	12:15	Booted T400s/T450s and W10 not responsive (I had logged out of it last night); Cycled power; (5) sensors are functioning / Noted data errors seen in Temperature Graph and log (all sensors have at least one isolated error since last night)	DRD SSC O4 O5 O7 O8 O11					20211215
				~	13:18	Data Collection expanded to record MIN, AVG, MAX for all 5 Tsensors; Temperature Graphs edited/added (AVG, MIN, MAX)	DRD					20211215
				~	13:40	~	13:51	SD Card Copy ...; Booted and rotated log					20211215_1940 L0W10M1M9 FW 2.1203 OS 3.9		20211215
				1-Wire polling intervals changed 300ms->6000ms (all 5 T-sensors); This may well reduce the isolated errors, which could have been caused by trying to poll 5 sensors every 300ms; It makes sense not to poll any faster, and the AVG logging will have about 10 samples/min	DRD O4 O5 O7 O8 O11					20211215
				Ordered (7) SparkFun SEN-11050 DS18B20 sensor assemblies, DigiKey, $90.64	DRD O12 O13 O14 O15 O16 O17 O18					20211215
		16	Th	~	05:20			SD Card Copy; Found and removed spikes in logged data (20211215_1.csv, 20211216_1.csv)	DRD					20211216_1120 L0W10M1M9 FW 2.1203 OS 3.9		20211216
				~	06:30	~	06:40	SD Card Copy (with modified files) ...; Booted and rotated log; Temperature AVG Graph SSCs	DRD SSC					20211216_1230 L0W10M1M9 FW 2.1203 OS 3.9		20211216
				I noticed that in the system log that cronsec is occassionally skipping a cycle just past the minute due to cronmin being active / I'm logging a lot of points and pushing the limits					20211216
				I can't say that changing the 1-Wire polling intervals to 6s has reduced the incidence of isolated errors, there were a lot of them from 19:06 yesterday until 04:20 today; But at least I've done everything I can to help reduce this problem	DRD O4 O5 O7 O8 O11					20211216
				Two days in a row now W10 has not responded 1st thing in the morning after booting T400s and has required power cycling to regain access / (but it continues to log, it just won't respond to a login request, even if I logout before shutting down for the night)	DRD					20211216
				Data Collection name changed: v4ac2wc1ad2wd1b2t4 --> v4ac2wc1ad2wd1b2t15					20211216
				Alternative Energy.doc MASTER CONFIGURATION review (for changes since Mo12/13), OTHER CHANGES: Users and Security > Device Settings > Device Name L0W10M1M2M9 -> L0W10M1M9; Email Settings Password JKlute@2014 -> JAKlute@2020; uPHP Script Setup > Debug Level Medium -> Verbose; Roles (minor edits in the process of listing all of the Roles); Actions, all disabled (except for those that are Manually Triggered); Scheduled Tasks /config/crontab.txt line for logrotate restored to "as from India" (30 59 23 * /scripts/logrotate.cgi) so that system log is rotated every night at 23:59:30 (if W10 is running)	DRD AED					20211216
				~	13:40	~	13:47	SD Card Copy ...; Booted (did NOT rotate system log, that should be done by cron every night now)	DRD					20211216_1940 L0W10M1M9 FW 2.1203 OS 3.9		20211216
				~	13:56	~	22:54	Disabled O11 ...; SSC of Temperature AVG Graph, shows 4 Ts oscillating at around 4⁰C ~14:00-~20:00 then all Ts became noise (no discernable pattern); Further t-shooting of T-sensors stopped by RCWT Emergency	DRD SSC O4 O5 O7 O8 O11					20211216
		20	Mo					Disconnected the Sensor Rack from the Wattmon (W10 is needed for the W50 Autopsy Test)	TM21F WP1 O4 O5 O7 O8 O11					20211220
		21	Tu	~	12:25			Configured Battery Capacity = 105 and Current AH = 78 (for W50 Autopsy Recovery Testing)	TM21F WP1 IMG					20211221
				~	18:00			20211221 180017 Screenshot.jpg; Wattmon "Charge in Today" 18,447 PetaWattHours (PWH); LOL	SSC					20211221
		22	We	~	08:30	~	09:50	Edited SSCs from yesterday, printed for wall of memories and emailed to Akash and others in India: / SSC 20211221 182205 Screenshot_ver002.png (modified 12/22/21 09:47:05); EML Wattmon Reports Integration of 18,447 PWH (new record!)	SSC EML					20211222
				~	22:27			Email from Akash "We do have a maxval that can be set in the data collection page, have you had a look at that?"	EML					20211222
		23	Th	~	05:29	~	05:41	20211223 052858 Screenshot.jpg: Data Collection page, MIN MAX boxed; Email to Akash "Is this what you are talking about?"	SSC					20211223
				~	08:11			Email from Akash "Yes... If you enter a non zero value for either of them it will use those values as min max references. Also please note that all functions besides instantaneous seem to have random issues, so I recommend logging with instantaneous values for now. I think that will go a long way in improving your stability"	EML					20211223
				(T400 and T450s were off since last night); W10 not responding (from T450s); Power cycled					20211223
		25	Sa					Setup for W50/B26 D&R 75w @ -15⁰C: Configured VariablesWidget [Roles '32,33,34,36,37,38,43,44' -> '22,36,37'; Variables 'battery_ah,battery_cur_ah' -> 'battery_ah,battery_cur_ah,battery_v_end']; Configured Actions [After Reboot enabled, battery_v_end=10.5; Fix !RL5 enabled; Fix RL5 enabled; End Discharge at Battery V enabled]; Cheater cord (T1 UPS) to RL5 to WP1 (W50)	TM21F Z0					20211225
		26	Su					While in the W50/B26 Discharge 75w @ -15⁰C: Configured Action After Reboot battery_v_end=10.85					20211226
		28	Tu	~	06:15			(T400 and T450s were off last night, and before shutting down I logged out of W10); W10 not responding; Power cycled					20211228
		29	We					W6/10	DORM					20211229
2022	Feb	17	Th	~	08:42	~	20:14	T-Sensor Rack attached and W10 powered up; Modbus devices unplugged (A10, C252, not needed for T-Sensor testing) / O4, O5, O7, O8 and O11 all concluded as BAD (tested individually in Engel, they drop out below ~5 to ~20⁰C)	DRD SSC Z0 O4 O5 O7 O8 O11					20220217
		18	Fr					O11 has been OK all night (temperature low of 18.6⁰C); Disabled O11; O4-O11 removed from Engel and sensor rack, labeled as BAD	DRD O4 O5 O7 O8 O11					20220218
		19	Sa					Deleted One Wires O4,O5,O7,O8,O11; O12 tested individually on sensor rack (Role "T_4 Center", polling interval 6000ms), some intermittent reporting then zeroes; Disabled Modbus Devices C252_1 and A10_1; Edited /config/onewire.ini to leave only the one device / O12 not reporting, disabled; O13 and O14 tested individually (not detected in scan)	DRD O12 O13 O14					20220219
		20	Su					Further troubleshooting of T-sensors stopped by ONWT Emergency	DRD TM22 O12 O13 O14 Z0 Z19					20220220
	Mar	1	Tu	~	10:35	~	11:05	Powered up to update MASTER CONFIGURATION ...; SD Card Copy	DRD		L					20220301_1705 L0W10M1M9 FW 2.1203 OS 3.9		20220301
	May	16	Mo	~	10:37			Powered up to log ENC charge voltage on B70/71 T-105s; A10_1 Enabled	TM22 BC3					20220516
		18	We			~	08:33	Settings > Time Settings > UTC Offset: [UTC - 6] Central Standard Time -> [UTC - 5] Eastern Standard Time (CDT); (R); SYNC; Shut down	TM22					20220518
		24	Tu	~	11:39			(Schauer BC7 Preparation): Powered up to log battery voltage (A10_1 attached to B70/71)	T48S PLN BC7					20220524
		26	Th					Instrumentation set up, T-105s in Engel: Powered down and T-Sensor Rack removed; onewire.ini num_devices=1 and it is disabled / C252_1 enabled; Battery 225 AH	T48S O12 O13 O14 BC7 IMG					20220526
	Jun	1	We	~	08:15			SD Card Copy; W10 has been powered up and logging since Tu5/24	T48S					20220601_1315 L0W10M1M9 FW 2.1203 OS 3.9		20220601
		11	Sa	~	08:30			BC7 BTS test setup broken down: W10 OFF; C252_1 disconnected; (Setting up for BC8 BTS tests and W10 will not be used)	T48S BC7	Available					20220611
	Aug	20	Sa					Dual Supply Bench Testing Setup Assembled: W10 and A10_1 not needed, removed from bench, boxed on N bench	T48-3 L17				M9 M1					20220820
2023	Jan	20	Fr					Cleaned the bench and put all the OneWire T sensors, sensor rack and assembled harnesses in a box	T48-4 O1-18					20230120

## WP1
WISPers: WP1	A					W50 ― 1st Generation Prototype ― WISPOWER#1; Dual 75w PS with Schottky Diode; 100AH SLA, Service					Batteries	Charger (PS1)	Charger (PS2)

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$464.27	231.50	Sold	L18	B26	BC4	BC5
2017	Mar	10					Components Specifications - Initial Thoughts; Quote Verbage for Mark Webb "An off-the-shelf UPS system is not available for this application, I've spent a lot of time looking for one"	WRD		5.00		5.00	Research					20170310
		11					Continuing to mull over the best way to come up with an example UPS for RW (25 W load, 24 hours); Reporting Modules; How to avoid $300+ for ICT power supply/charger			4.00		9.00					20170311
		12					Ignoring the Reporting Module; Two General Solutions; Further Consideration of Options			3.00		12.00					20170312
		13					Began to set up a test bench to test UPSs but abandoned this approach			3.00		15.00					20170313
		14					General Specifications for 'Standby Float Charger for WISP - Sized for RW (12v/25w/24hrs/600WH)' / Was thinking Gel Cell, 50W Switch Mode Power Supply, optional LVC and Reporting Module			6.00		21.00					20170314
		16					Mean Well SCP-50 is the best T compensated power supply I've found in it's class/price range; Tprobe must be made from parts			3.00		24.00				BC4	BC5	20170316
				Spreadsheet 20170316 WISPer DC UPS Parts List (initial draft).xls			1.00		25.00					20170316
		29	We					Preparing quote for Mark; Battery Bank (BatterySharks)	WRD		2.00		27.00					20170329
				Email to Mark Webb "DC UPS quote examples (RW, RN)", after "3 days of internet research and engineering design"	EML WRD TW1		1.00		28.00	Research / Sales					20170329
		30					Notes concerning quote sent to Mark, battery bank considerations; Considered the use of cheap automotive batteries [too many defects for serious consideration] / "I think we need to go with AGM for the flagship" [wrong thinking]	WRD EML		4.00		32.00					20170330
	Jun	27	Tu					To Mark "Re: DC UPS quote examples (RW, RN)": I talked with Mark and Keith while they were at RW to meet AmerenUE.	EML TW1		2.00		34.00					20170627
		28	We					From/To Keith Jones "what the average tower will look like!"	EML		2.00		36.00					20170628
	Jul	5	We					To/From Mark and Keith "RE: what the average tower will look like!" / Competition research SENS Battery Charger with Tcomp - 101233_FC1_w_RTS_RevB.pdf, Short_Form_inverter.pdf	EML TW1 LIB		3.00		39.00					20170705
		6					Power supply research 20170706 enc120.pdf, 20170706 enc180.pdf / Competition research ICT-DC-UPS-Series-2_Data-Sheet_800-146-005.pdf, 855-146-200_dcUPS2_WEB.pdf, gsu-series-dc-ups.pdf, sr-u.pdf	LIB		4.00		43.00					20170706
		10	Mo					To Mark "Re: DC UPS quote examples (RW)": I quoted $500 for a DC UPS at RW, and was looking at a 180 Watt power supply.	EML TW1		4.00		47.00					20170710
		11	Tu					From Mark "Re: Flyers needed": "… can meet you Wednesday and give you some money to start on DR system."	EML		1.00		48.00					20170711
		12	We					We met at McDonald's in Richmond (I had to buy Skype Credit $10 to facilitate communications, and 20 miles @ $0.54) / Mark Webb of Turbonet advanced me $400.00 for "Rayville Battery Back-up DR" (this was to develop WISPower #1 for them) / To/From Mark and Keith "RE: DC UPS stuff (WISPOWER)"; Started design and procurement of parts	TW1 WRD EML	$20.80	7.00	$20.80	55.00	Design / On Order	L0				20170712
		13	Th					Ordered ENC-180-12 from TRC Electronics (problems with verification)	EML TW1	$84.85	3.00	$105.65	58.00				BC3		20170713
		14	Fr					TRC Electronics order being shipped; Ordered SigmasTek 12V 100AH from BatterySharks.com; T Compensation Probes research / Competition research 15.murphy_sentinel150_bulletin.pdf, 1715009.pdf, 1110857.pdf	EML TW1 LIB	$170.39	6.50	$276.04	64.50			B26			20170714
		17	Mo					Email from pjpower.com "Palmer Johnson quote - Murphy charger and sensor" (research)	EML		4.00		68.50					20170717
		18	Tu					Battery Received; "Let There Be WISPOWER" (prayer and inspiration) / Research, Hiccup Mode Power Limiting 1303.pdf; parallel.pdf; Technische_Beschreibung_Parallelschaltung_ENGL.pdf, 20170718 SCP-75.pdf	TW1 LIB WRD		7.00		75.50					20170718
		20	Th					ENC-180-12 received; To Julie Nawrocki @ TRC Electronics "Re: Order#198997 - MISSING NEEDED PART (no connector for thermistor) / To/From Mark and Keith "Re: DC UPS stuff for RW (WISPOWER #1); 20170720 ENC User Manual.pdf	EML IMG LIB		5.00		80.50					20170720
		21	Fr					From Keith "Re: DC UPS stuff for RW (WISPOWER #1)": "… did you have any power supplies shipped here …" / From Julie Nawrocki at TRC Electronics "… the mating housings are not included …" (research into connectors needed) / To Keith "RE: WISPOWER design choices" (Netonix WS-12-250-DC SMTP alert?) / 20170721 ENC-180 Series Desktop Battery Charger.pdf, 20170721 DF11_catalog.pdf (DF11 Connector), 20170721 Notes.txt (concerning problems with ENC_180_12) / Competition research, 6 pdfs; Netonix WS-12-250-DC ws-specsheet.pdf	EML LIB		9.50		90.00					20170721
				Schottky Diode idea for dual power supplies (see concept drawing); Abandoned use of ENC-180-12 (BC3) for WISPer (it will hang in Absorption with >10% load)	TW1 WRD		4.00		94.00					20170721
		23	Su					To/From Keith "RE: WISPOWER design choices"	EML		1.00		95.00					20170723
		27					Competition research, 6 pdfs	LIB		2.00		97.00					20170727
		28	Fr					Ordered (2) Mean Well SCP-75-12 power supplies from Mouser / Further T Compensation Probes research, 2 pdfs	EML MOU LIB	$55.85	4.00	$331.89	101.00				BC4	BC5	20170728
		29	Sa					To meanwellusa.com "NTC Thermistor for SCP-75 Power Supply"; T Compensation Probes research, 2 pdfs	EML LIB		3.00		104.00					20170729
		31	Mo					From meanwellusa.com "RE: NTC Thermistor for SCP-75 Power Supply"	EML		2.00		106.00					20170731
	Aug	1	Tu					Received Mean Well power supplies (approximate date); To service@veteng.com "Temperature sensor for power supply" / Response rec'd 20170801 RE_ NTC Thermistor for SCP-75 Power Supp.pdf	MOU EML LIB		3.00		109.00				BC4	BC5	20170801
		2	We					From service@veteng.com "Temperature sensor for power supply"	EML		2.00		111.00					20170802
		3	Th					To/From Mark "Re: WISPOWER"; Bench testing setup (incomplete); Phone call discussion with Mark; $980 invoice sent "Re: Invoice" (20170803 Invoice.pdf)	EML IMG DBT TW1		6.00		117.00	Testing			BC4	BC5	20170803
		4	Fr					Phone call to Mark; He mailed $300.00 check for "Disaster recovery Box"	WRD		4.00		121.00					20170804
		5	Sa					I wrote "Precautions" sheet for WISPer #1; Competition research, 2 pdfs	TW1 LIB		4.00		125.00					20170805
		6	Su					Battery in service testing WISPer #1: Discharge Test with scrap diode (~70w resistive load) "hot but hopeful" …	TW1 WRD		4.00		129.00					20170806
		7	Mo					Test setup; Discharge Test Conclusions; Received $300.00 check (now $700 total rec'd for WISPer #1)	IMG TW1		4.00		133.00				BC4	BC5	20170807
		8	Tu					WISPOWER 75 Enclosure Search with drawings; 10 pdfs	TW1 LIB		5.00		138.00	Design					20170808
		9	We					Enclosure research and pricing, with drawings, 10 pdfs; Research "Mouser, Schottky Diodes & Rectifiers In Stock" (selected Vishay VS-STPS20L15D-N3) / Printed and studied charts 'Vr - Reverse Voltage (V)' and 'If(av) - Average Forward Current (A)'; 20170809 Vishay ntcle100-222385.pdf (for SCP Series) / Other Schottky Diode research, 5 .pdfs; T Compensation Probes research, pdf	TW1 LIB		9.50		147.50					20170809
		10	Th					Enclosure research, 17 .pdfs / Ordered Hammond Enclosure, Schottky Diodes and NTC Thermistors from Mouser; Researched M3 Button Head Screws	LIB EML MOU	$44.84	8.00	$376.73	155.50	On Order					20170810
		11	Fr					Ordered M3 screws and Allen insert bits from BoltDepot.com; Ordered Red/Black Zip Cord (16 gauge, 25 feet) from BulkWire.com / To Mark and Keith "WISPOWER 75 Status" with photos "proof of principle" testing successful; From Keith "RE: WISPOWER 75 Status" concerning Netonix DC switches / Phone call with Mark; To Mark "AC UPS (our phone conversation); To Mark and Keith "Netonix DC Switch Capabilities"	EML TW1 BDC	$32.46	8.00	$409.19	163.50					20170811
		13	Su					Competition research, 5 pdfs; To info@tyconsystems.com "TP-BC Series Chargers" (the competition: Tcomp charging?) / Remote Monitoring & Control research, TPDIN-Monitor-WEB2 Remote Monitor and Control Spec Sheet.pdf	LIB EML		4.50		168.00					20170813
		14	Mo					Rec'd M3 screws and Allen insert bits from BoltDepot.com; Rec'd Red/Black Zip Cord from BulkWire.com; Rec'd Enclosure, Schottky Diodes and NTC Thermistors from Mouser / From Scott Parsons at Tycon Systems "Re: TP-BC Series Chargers" ("we are working on a model with battery temp compensation")	TW1 MOU EML BDC		5.00		173.00	Assembly					20170814
		16	We					Detailed drawings for Enclosure to show locations of power supply mounting holes	TW1		4.00		177.00					20170816
		17	Th					Detailed drawings for Enclosure to show locations of power supply mounting and other holes; Detailed 'DC Wiring' and 'AC Wiring' drawings / 1st test after assembly (discovered that with thermistor attached to PS1 the voltage needed to be adjusted)			8.00		185.00	Testing					20170817
		18	Fr					Adjusted PS1 with 3w resistor load to simulate fully charged battery, tested Temperature Compensation / Discharge Test with 75-100w resistive load (~7.5 hrs); Recovery Test with 65-90w resistive load (HOT!!!) / 20170818 WISPer #1 Parts List.xlsx (later copied to sheet WP1A and edited); 20170818 WP75D12 User's Manual (WISPer#1 - draft).docx	TW1 WRD		10.00		195.00					20170818
		19	Sa					Removed plastic covering from enclosure; Removed cover; Unit runs cooler but still HOT!!! … somewhat disgusted, but decided it could be placed in service (left it on for a few days) / Redundant power supply research, 2 pdfs	TW1 LIB		4.00		199.00					20170819
		24					Floating at 13.70vdc Fluke; Adjusted down to 13.51 O.C.; This will help PS1 from overheating during full charge	TW1		0.50		199.50					20170824
		31	Th					I drove to Lexington to show Mark and Keith the prototype and to discuss things (42 miles @ $0.54) / To Mark and Keith "WISPOWER Basic Features and Benefits" with WISPOWER Features & Benefits.pdf; 20170831 WISPer Backup Time Chart (rough estimates).xlsx / 20170831 WISPer (WISPOWER #1) Features & Benefits.docx; 20170831 WISPer (WISPOWER #1) Features & Benefits.pdf	TW1 WRD EML	$22.68	8.00	$431.87	207.50	Install…					20170831
	Sep	5					WISPer #1 Ready to Install at RCWT	IMG		2.00		209.50				BC4	BC5	20170905
		6					WISPer #1 and battery installed at RCWT: Photo of water tower; Final payment of $280 rec'd from TurboNet, total rec'd $980; 1 Year Warranty (we didn't discuss it but I'll honor it) / 35 miles @ $0.54 including trip to Odessa tower for further inspiration; From Keith "FW: test email from Rich-City-DC" (he got the Netonix SMTP working) / To Keith "From the chart I gave you, you should have about 14 hours of battery backup for your load of 65 watts"	IMG TW1 EML WRD	$18.90	6.00	$450.77	215.50	Sold	L3				20170906
		8					Final design thoughts for WISPower #2, but they were all based upon improvements to the dual supply with Schottky design	WRD TW1		0.00		215.50					20170908
2018	Feb	9					All development for WISPer has been stopped since 9/8/17; WISPer #2 idea to use Genasun	WRD WP2		0.00		215.50					20180209
	Mar	24					There are quite a few erroneous conclusions/assumptions in the notes I made from ~3/10/17 to 3/30/17, above; Recap of notes missing (that were printed for file)	WRD		2.00		217.50					20180324
	Jul	27	Fr	~	03:45		07:45	Completed assembly sheet	WP1A		4.00		221.50					20180727
		31	Tu	~	04:25	~	06:10	Assembly sheet improved			1.75		223.25					20180731
	Aug	1	We	~	01:00	~	02:15				1.25		224.50					20180801
		2	Th	~	02:15		04:15				2.00		226.50					20180802
2019	Mar	27	We		12:15			From Mark Webb: '… come check out battery back up @ RCWT … DC switch blew up like the beginning of winter … we're going to put in another but "it's not getting enough power to do it" so give me a holler thanks'	SMS TW1		0.25		226.75					20190327
	Apr	1	Mo		09:46		09:56	Spoke with Mark concerning RCWT, Swafford's and RW; RCWT 'Hooked up new DC unit last week, and not enough power'; Scheduled onsite Tu AM	TW1		0.33		227.08					20190401
		2	Tu		07:53		08:02	MMS & SMSs from Keith Jones: Screenshot showing 33.2 watts on AC Netonix @ RCWT; 'Seems to be between 34-45 watts'	SMS TW1		0.25		227.33					20190402
				09:05		10:35	Onsite at RCWT: 48°F, battery 14.1vdc, load 15.2vdc (DC Netonix is running but no loads on it, Schottky is blocking, Tcomp on battery charger is AOK, s/b 14.15vdc battery) / Removed AC, battery 13.9vdc, load 13.6vdc (AOK); AC on, battery 13.8vdc, load 15.2vdc (AOK); Power supplies are both cold; No visible signs of heat damage / Everything is working as it should; Waited ~20 mins for Keith to show up; 'Show and Tell', discussion [Service Call to be billed as 'No Fault Found' and 'Defective DC Netonix']	TW1 SMS	$13.50	2.42	$464.27	229.75					20190402
		3	We	~	05:00	~	05:30	To Mark and Keith "Invoice for Service Call @ RCWT + Offer": $160.00 (4/2/19, added to income for WP1); I offer to work for him on his network or infrastructure in any capacity	DBT EML TW1		0.50		230.25					20190403
				From Mark "We'll have to figure something out.": He complains about not having charged me for internet "for ever"	EML		0.00		230.25					20190403
	May	4	Sa					Invoice revised and To Mark (email & USPS) "Revised Invoices as per our agreement", $160 is "Paid in Full by Service Rendered (Internet before 5/1/19)"	DBT EML TW1		0.25		230.50					20190504
		5	Su					Completed review and update of this sheet for entries in WRD	WRD		0.50		231.00					20190505
		7	Tu					Completed review and update of this sheet for EML and DBT	EML DBT		0.50		231.50					20190507
2021	Mar	12	Fr	~	10:25	~	11:55	Onsite at RCWT for the Backup Power Supply Maintenance Program; See L3 for details	DBT TM21S SMS SSC					L3	B26			20210312
		13	Sa					Email Report to Mark and Keith; ; See L3 for details	EML TM21S					20210313
	Dec	16	Th	~	15:20	~	16:15	Onsite at RCWT: Power and Netonix are OFF; SLA 12.71vM OCV; 15:36 W50 powered by Trace, 12.71vM no charging, Netonix is up (~2.65aE @ 15.05vM = ~40w) / 15:49 Their other stuff powered by Trace (~0.43aE @ ~120vac = ~52w) / 16:07 Call to Mark (4m), I told him the battery is "shot" [I found out later the W50 fuse was open] and the W50 won't handle everything at site (if Keith puts the other stuff on the Netonix ~90w), we agreed to meet @ RHS for him to give me the 27TMX and for me to get the W100 from RHST ...; Departed for RHS	TM21F SMS					L3	B26			20211216
				~	17:20	~	19:15	Onsite at RCWT: AC power is ON; SLA 12.71vM not charging (once again, due to blown fuse, but I thought it was "shot"); Removed SLA and W50 to take to shop					Subaru	-	BC4	BC5	20211216
				Unloaded Subaru	TM21F					L0				20211216
		17	Fr	~	01:25	~	02:35	Cleaned (compressor & wet towels); Discovered and replaced W50 PS1 blown fuse; Charging / CONCLUSIONS Fuse was blown by load short on 8/4/21, battery has been resting and there has been no backup for 4.4 months					B26			20211217
				B26 installed in Engel Battery Enclosure and stabilizing towards 25.0⁰C; Found another fuse and silver taped to W50 top ... / Checked and corrected Float from 13.508vI to 13.635vI (25.0⁰C Dinico, 0.22aE, ~4.5w); Began series of W50 BTS checks (5, 10, 15, 20, 25, 30⁰C) starting with 5.0⁰C ...	TM21F PLN Z0 Z19					B26			20211217
		18	Sa					... Engel W50 BTS Tests: Data for 5, 10, 15 and 20⁰C ...	TM21F PLN					20211218
		19	Su					... Engel W50 BTS Tests Concluded: Data for 25 and 30⁰C [See TM21F 1/28/22 for Analysis and Conclusions] / Library\Mean Well\20211218^19 BTS; Mean Well SCP-75-12 (WP1-W50 PS1), 5^10^15^20^25^30⁰ Float (B26 SLA).ods	TM21F PLN LIB Z0					B26	BC4	BC5	20211219
		20	Mo					W50 Autopsy (why did it blow the fuse?): Examined data sheet on Mean Well SCP-75-12 power supplies (the fuse should not blow when charging a dead battery, but it may hiccup) / Examined and notated historical records for L3, WP1 (BC4, BC5) and B26 (We8/4/21 is when the workers got the equipment wet, Th8/5/21 early AM is when I was onsite and found the destroyed Netonix, and I missed the fact that the W50 had blown a fuse) / Set up W10, Engel and ITECH to repeat the conditions of the August incident (21⁰C, 40w load); Started ITECH battery test 3.33a, stop at 8h or 9.6v ...	TM21F PLN W10 Z0 Z17					20211220
		21	Tu					W50 Autopsy (why did it blow the fuse?): ITECH Battery Test concluded, Calc, CONCLUSIONS (B26); Recovery Started ...; W50 temperatures measured, CONCLUSIONS (BC4 and BC5)	TM21F PLN Z0 Z17 W10 IMG					B26	BC4	BC5	20211221
		22	We			~	06:45	Recovery completed [Analysis and Conclusions 1/29-30/22, Edited 2/8/22] / Library\Mean Well\20211221^22 Recovery; Mean Well SCP-75-12 (WP1-W50 PS1), 27 AH, 0w, 21º (B26 SLA); Wattmon Data & Graphs.ods	TM21F LIB					20211222
				~	08:04	~	11:58	ITECH: Adjusted PS2 output down slightly 15.132v -> 15.01v (no load, shop ambient); Chart of PS2 Load Output Voltage vs. Load Wattage, 0 to 100w / CC load tested at 10a (130w), no problems except drooping voltage (both supplies working together, temperatures measured) / At CC load 10a the W50 is OK if AC power is turned OFF and ON (does not blow fuse or hiccup, SSCs of Live Energy in transitions) / Determined the highest possible short-term load wattage as ~250w (battery must be fully charged, at this wattage it is discharging and fuse will blow within minutes) / PS1 fuse blew within a few minutes after setting ITECH CC 30a (~266w); Video showing the fuse melt, track time 04:30-04:47, just before 11:46 as per Wattmon log / Political Thoughts for Invoicing (over an hour thinking on the porch); I will reverse/eliminate all charges for RCWT 8/5/21 to date	Z17 TM21F SSC IMG L3					20211222
		23	Th					Closeup photo of melted fuse metal that dripped onto the wire yesterday (also some on LF100); Replaced PS1 FS2; Powered up (SSC); Tried to clean PS1 LF100; Powered up again (SSC)	TM21F IMG SSC					20211223
		25	Sa	~	09:45			W50 OFF during set up of Engel for D&R at -15⁰C (+5⁰F) ...; By the end of the day W50 ON connected by cheater cord to W10 RL5	TM21F Z0					20211225
		26	Su	~	10:15	~	17:43	W50 OFF by W10 control for Discharge (75w ITECH load on load cables); Schottky and cable drop ~1.16v @ ~6.9a (~8w) / Predicted drop will be 1.26v when battery is ~11v (modified W10 Action After Reboot for battery_v_end=10.85 so that Discharge will end when load sees ~9.6v) / Engel is not maintaining -15⁰C (the discharge is warming the battery) ...; Recovery started by W10 control (while I was sleeping)					B26			20211226
		27	Mo	~	02:40	~	19:00	During recovery the battery probably warmed up to -8⁰C (Engel maximum cool); ITECH 75w load removed from PS2 / Decided to finish recovery at +25⁰C, battery warmed up as rapidly as possible (Engel maximum heat) ...; Recovery completed					20211227
				[See TM21F 2/8/22 for Recovery Analysis and CONCLUSION] / Library\Mean Well\20211226^27 Recovery; Mean Well SCP-75-12 (WP1-W50 PS1), 54 AH, 0w, ~-12 to +25⁰ (B26 SLA); Wattmon Data & Graphs.ods	TM21F LIB					B26	BC4	BC5	20211227
		28	Tu					20211228 Credit - Richmond City.pdf; Recommendations for Further Discussion (W50/SLA should go to WWT, T-105s from WWT should go to RCWT)	TM21F DBT L3 Z19					20211228
2022	Jan	3	Mo					20220103 Email to Mark, Keith & Brad 'Account Credit - Richmond City Water Tower'.pdf	TM21F DBT EML L3					20220103
		28	Fr					Calc analysis of W50 BTS tests (data from 12/18-19/21) Conclusions: Compensation average -25.2 mV/⁰C (-4.2 mV/cell/⁰C) / I've set the wrong Float voltage on the W50 (PS1), now 13.65v but s/b 13.5v @ 25.0⁰C (see notated SSC printout from SigmasTek\20180503 SP12-100(NB).pdf)	TM21F LIB SSC					B26	BC4	BC5	20220128
		30	Su					Calc analysis of W50/SLA Recovery (data from 12/21-22/21) Conclusions: Graphs clearly show that in Bulk the MeanWell charger operates in CC at about 7.1-7.4a (but it also looks like CW at about 95w); For conditions as they were at RCWT (~40 Watts Load) an 8 hour power loss will require about 9 hours to recover the discharge volume lost	TM21F LIB					20220130
	Feb	8	Tu					Calc analysis of Recovery (data from 12/26-27/21) CONCLUSIONs: In hindsight WP1 could have been a LOT SIMPLER					20220208
		17	Th	~	11:30			WP1 removed from bench, B26 removed from Engel (placed under bench on maintenance charge)	DRD Z0					L	B26	BC4	BC5	20220217
	Jun	28	Tu					Prepared W50/B26 for installation at WWT: W50 cleaned (compressor); BTS bundled in conduit pipe with Dinico T2 / Checked PS2 Load Output at shop ambient ~23⁰C, 15.00v (14.995vI; 0.100aIS) / Set PS1 to Target 13.50v Float at BTS 25.0⁰C and load 100mA, without battery, 13.507vI (See Fr1/28/22 TM21F "Calc, W50 BTS Tests" Conclusions) / Labels printed and applied to W50: Inventory Sticker 0.5 WP1 (W50).lbx; W50 Battery Float 0.7.lbx; W50 Output & Load Rating 0.47.lbx; W50 Fuses 1.0 Yellow.lbx / W50 Warning! Shock Hazard! 120 VAC! 1.0 Yellow.lbx; W50 Warning! Hot! 1.0 Yellow.lbx	TM22 Z0 LBX					L0				20220628
				~	14:20	~	14:55	Onsite at TLNB: Keith stated his intentions that WWT would eventually be AC only (3 customers) and that he'd pull the W50/B26 (yet to be installed there today) for use at Carrollton	TM22 L16					Subaru	-			20220628
				~	15:15	~	16:30	Onsite at WWT: WP1 (W50) installed to replace WP2 (W100_1) / W50 AC power connected, initial charge >7aE; BTS silver-taped to top of battery ~35⁰C (~95⁰C); 13.34vM (13.27vF equivalent, good Float V for current battery T); Float ~0.030aE	TM22					L6	B26	BC4	BC5	20220628
	Jul	19	Tu					Call from Keith: Ordered new site CFS; He removed the W50/SLA from WWT to take to CFS (sometime while I was in CO in the past two weeks); Partially and temporarily installed at CFS	T48-4					L18				20220719
		21	Th	~	11:05	~	11:35	With Keith at shop to discuss Power Cable Assembly for CFS: I saw B26 (from WWT) in the back of his vehicle (HOT!) and he confirmed again that the W50 is partially installed at CFS / He plans to be onsite at CFS Mo7/25 to install cables and hookup the W50/B26/Netonix/antenna					20220721
	Aug	25	Th					Call from Mark and Keith: CFS is up and running on W50/B26 / Keith saw ~78w (MikroTik and Mimosa interfaces), I wouldn't be surprised if it was actually higher than that, as he's not seeing the total battery load / He knew that WP1 is rated 75w, so he took some stuff off and dropped it down	T48-3					L18				20220825
	Sep	15	Th					W50 mentioned in Report (discussed move to CFS with Keith Tu7/19): / 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 DBT EML					L18				20220915
	Dec	28	We		12:00		14:00	Onsite at CFS: B26 behind T-105s (photo); WP1 is sandwiched behind the enclosure up against the wall, on edge horizontal, powers the DC Netonix / Keith plans to come back "maybe next week" to move all loads to the W150 (some now on AC, some now on WP1/B26) / Keith may move WP1/B26 to CCC (new Location L19) after he gets done with it at CFS	T48-4 IMG					L18	B26			20221228
2023	Jan	10	Tu					TFTP TODO: I gave some erroneous advice to Keith when I was onsite We12/28/22 (how to power the Netonix if he wants to keep it at the site); See L18 for details	T48-4					L18				20230110

## WP2
WISPers: WP2	A					W100_1 ― 2nd Generation Prototype ― Delta PS 24v/200w, Genasun, Fan, (2) T-105 Batteries					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$560.61	448.33	Sold	L	-	S4	C4
2017	Sep	6					Installed WISPer Prototype #1 at RCWT and began thinking about designing WISPer #2, but the initial thoughts were all based upon improvements to the dual supply with Schottky design (WISPOWER #2 Design Thoughts)	WRD TW2-3		4.00		4.00	Design					20170906
		7					"It's going to have to have a fan" and other thoughts for dual supply design (WISPOWER #2 Design Thoughts 9/7/17) / Researched power supplies lrs-150f-spec-752934.pdf, RSP150spec.PDF; Fan and enclosure research, 3 pdfs	WRD LIB		5.00		9.00					20170907
		8					Final thoughts for dual supply design (notes on pink and white sheets) including "How to get a 150 W load at 33vdc?", 2 pdfs / More power supply research, LPP-150-spec-1109460.pdf, power_supply_lrs-150-datasheet-1108963.pdf; More enclosure research, 2 pdfs; More Schottky Diode research, 6 pdfs	TW2-3 LIB WS		6.00		15.00					20170908
				From/To Keith Jones "irma live cams from key west": storms were taking down towers there, much discussion/consideration for sales to Florida	EML BII		1.00		16.00					20170908
		15					More power supply research, 20170915 SCP-75-SPEC-806456.pdf	LIB		2.00		18.00					20170915
				To Mark "48 volt DC UPS for 3 days": they had inquired about a particular installation in Key West, for which (as currently powered) we would need a lot of batteries / I asked for more information	EML BII		1.00		19.00					20170915
		18					More power supply research, SP-320.pdf; Competition research, 6 pdfs; Design development put aside for other priorities, about 5 months	LIB WRD		3.00		22.00					20170918
				From Mark/Keith "Fw: mimosa dc power supply": 'Look at this and call me'; Link to Tycon Power Systems TP-DCDC-4848D-HP (48vdc input 56vdc output 35W 802.3at) / Basically a PoE+ inserter for 56vdc PoE	EML		1.00		23.00					20170918
		27					From Mark "Fw: NEMA Enclosures for Every Application" (considered really nice but pricy weatherproof enclosures)			1.00		24.00					20170927
2018	Feb	9					White sheet "WISPOWER - new idea": Unregulated DC for Genasun solar input	TW2-3 WRD WS		2.00		26.00					20180209
		23					White sheet "WISPOWER - new idea": > 140 W Regulated Power Supply for Genasun solar input (Schottky diode isolation later discarded as not needed) / Started researching specifications on Genasun GV-10-Pb-12V and Mean Well 200 W power supplies / To Mark and Keith "AC at RW?" where I mention a much better design for a DC UPS power supply for RW	TW2-3 EML WS		6.00		32.00					20180223
		24					MPPT Research, Agresta_Mikolajczak_MQP_MPPT_Solar_Charger_1.pdf, C0505015022.pdf, DN06054.PDF, BSE_What_is_MPPT.pdf; More power supply research, SP-200.pdf	LIB		5.00		37.00					20180224
		25					Test setup for validating initial idea with Genasun (very encouraging): / OK with BK_1, Schottky in air, Genasun_3 (cost from 8/6/15 purchase) and 27TMX battery 20150422 (Wattmon_9 and C252_2 used for observation) / Schottky diode destroyed, but Genasun OK without it / Photo To Mark and Keith "Re: AC at RW?" and mentioned "Proof of principle, better DC UPS (WISPOWER) design" and "I think I could sell these initially for about $400 (battery not included)"	TW2-3 WRD IMG EML	$111.53	6.00	$111.53	43.00	Testing	L0	B1	S2	C4	20180225
		26					Lexington TurboNet office: I pitch the idea in person and Mark gives me a check for $400 for WISPOWER #2 for RW (including removal of solar system, not including battery) / Mileage 42 miles @ $0.54 [The $400 was later applied towards WISPer #2 at WWT]	TW2-3 WRD	$22.68	6.00	$134.21	49.00	On Order					20180226
		27					"Shopping / procuring WISPOWER #2 w/Genasun": Researched available power supplies and ordered Delta PMT-24V150W1AA (DE_1) / Downloaded Datasheet for Delta PMT-24V200W1AM (DE_2, S4) / More power supply research, Datasheet-Orion-Tr-DC-DC-converters-isolated-100-250-400W-EN.pdf, REC5-S_DRW_Z-958358.pdf (DC-DC converters) / Competition research, 4 pdfs; TODO (whitesheet)	TW2-3 MOU EML LIB S3 S4	$35.38	7.00	$169.59	56.00					20180227
		28					Improved test setup (heavier wires): C252_2 Calibration (M2)	M2		2.00		58.00	Testing					20180228
2018	Mar	2					White sheet notes on testing concluded 3/2/18, Setup and Conclusions: BK 100w power supply as solar input to Genasun, resistive load ~160w, Genasun hunting around but OK	TW2-3 WRD WS		5.00		63.00					20180302
				Received 150W Delta (DE_1); Testing, see white sheet notes concerning "stiffness" / (hiccup problems, hit on idea of using ~30 inches of 22 AWG wire between Delta and Genasun, but hiccups may have been caused by Delta hiccups beyond 150w)	MOU WS TW2-3 WRD		5.00		68.00				S3		20180302
				White sheet notes "Questions to be answered": / What resistance is needed between [Delta] and Genasun? Can Genasun remain stable for several days at max. power until battery gets recharged?	TW2-3 WS		4.00		72.00					20180302
		3					White sheet notes on testing concluded 3/3/18 with ~30 inches of 22 AWG solid between [Delta] and Genasun input / Conclusions "Genasun self-heating depresses Absorption and Float voltages significantly" and "Remove cover on Genasun and/or fan cool it"	TW2-3 WRD WS		7.00		79.00					20180303
				White sheet notes "Genasun self heats" and "New load configuration" (jumpers for resistive load changes)	TW2-3 WS		3.00		82.00					20180303
				(1) White sheet notes "Testing continued with new [Delta] Power Supply"; Theories on Genasun T compensation (long time constant) / "I think it is imperative that the Genasun have fan cooling (when there is AC)"			3.00		85.00					20180303
				(2) White sheet notes "Testing continued with new [Delta] Power Supply"; Conclusions and Theories, Genasun resets T comp by removing battery power			2.00		87.00					20180303
				(3) White sheet notes "Testing continued with new [Delta] Power Supply": / Genasun cover removed, 120vac fan mounted above Genasun, resistive load jumpers used to manually regulate between 85 to 95 W (90 W target) / Conclusion "I either need a PS that doesn't hiccup on overload, or with a higher rating (200W), because when "cold" the Genasun can draw 180 W"	TW2-3 WRD WS		4.00		91.00					20180303
				(4) White sheet notes "Testing continued with new [Delta] Power Supply": Boosting Delta 150W with BK in parallel / Conclusions "Leave it overnight" and "Wattmon needs correction/configuration"	TW2-3 WS		2.00		93.00					20180303
		4					White sheet notes "Testing continued with new [Delta] Power Supply": Wattmon configuration corrected, tweaked A1/VIN calibration (W9); Conclusions "Need to order 200 W PS"			8.00		101.00					20180304
		5					White sheet notes "Testing continued with new Delta Power Supply": Genasun fan taped to bench / Conclusions "Axially mounted 41 cfm fan is more than enough cooling", "… Genasun can maintain 180-190 W throughout bulk with peaks of 193 W (~90 W load)", / "Maximum recommended load wattage s/b 100 W" / Photos of W100 Testing (Delta 150W, Genasun no cover, fan taped to bench, BK, W9, B1)	TW2-3 IMG WS		4.00		105.00					20180305
				Ordered 200W Delta power supply from Mouser (DE_2, S4)	EML MOU	$43.87	2.00	$213.46	107.00	On Order					20180305
		6					White sheet notes "Testing continued with Delta Power Supply": >150w load; Hiccups / Conclusions "At 176 W load the Genasun can reach Absorption, but it would probably not be able to reach Equalize …", / "At these high loads voltages are depressed by as much as 0.2v", / "At no load, voltages are above spec. by about 0.1v", / "A good way to state the specifications: 100 W Continuous (constant wattage load), up to 150 W overload (long term consequences to battery life ..."	TW2-3 WS		5.00		112.00	Testing					20180306
		7	We					FedEx tracking says 200W PS "delivered" but it isn't here yet; Contacted FedEx	MOU EML		1.00		113.00					20180307
		8	Th					Called Mouser and explained the problem with the Lost Shipment (DE_2, S4)	MOU		1.00		114.00					20180308
		9	Fr					Called Mouser and they ordered another 200W PS at no charge (DE_3, S5)	MOU EML		1.00		115.00					20180309
				White sheet notes "WISPOWER #2 & SAPS - How did I manage to read 190 W with +- 12.5 Amp current loop?": Answer is "Because range is much more than Akash states"	TW2-3 WS		3.00		118.00					20180309
		11	Su					"Lost" 200W PS received: Photos of lost and found Fedex shipment box	MOU IMG		1.00		119.00					20180311
				White sheet notes "Delta 200W supply was received and setup for testing today": 12 guage solid Delta/Genasun connection / Conclusions "No hiccups", "I think we should mount the Genasun and the fan on top of the power supply", "We might be able to raise the stated upper power limit ..."	TW2-3 WRD WS		4.00		123.00				S4		20180311
		12	Mo					White sheet notes "Parts list - Genasun & fan mounted on Delta, WP #2 for RW"; "Load and battery connection options/thoughts"			6.00		129.00	Assembly					20180312
		13	Tu					White sheet notes and drawing "Load and battery connections - Final, Testing & RW": Assembled and implemented into test setup			4.00		133.00					20180313
				White sheet notes "As assembled for RW": Conclusions "…better battery and load connection harness provides for a much better battery voltage regulation …", / "Contrary to previous notes, this system can handle 120 W loads without any significant droop in battery voltages ...", "I now think we could rate this system as 150W maximum."			4.00		137.00	Testing					20180313
				Test setup (Trace, Delta 200W, Genasun mounted under fan, W9, C252): To Mark and Keith 3/27/18 and 5/3/18	IMG EML		3.00		140.00					20180313
				2nd No Charge 200W PS Received (DE_3, S5)	MOU		0.50		140.50					20180313
		14					White sheet notes for further testing 3/13/14 and 3/14/14 "Plans for profiling 150 CW load": / Trace inverter as load, attempted 50% discharge by measuring O.C. voltage, Trace inverter shut down (LVD, moved jumper to Deep discharge) / Conclusions include "Use the Wattmon Coulomb Counting as a guide to when to stop the discharge", "Recovery at 2 W load (Wattmon) ... HICCUPS!!!"	TW2-3 WS		8.00		148.50					20180314
				White sheet notes for experiments with Delta to Genasun connection: / Conclusions include 'Contrary to the 3/11/18 Conclusion, we do need some resistance between the Delta and Genasun to avoid Genasun "hiccups"', / 'The previously used 30" of #22 solid eliminates the problem entirely ...', 'I installed 4" #16 stranded black and 31" of coiled #22 stranded red.'			6.00		154.50	Ready to Install					20180314
		15					White sheet notes "Observations from Wattmon graphs" and "Genasun LED behavior at low loads"			3.00		157.50					20180315
				White sheet notes 'Thought experiments, how to gather and state "real world" discharge/recovery times'			3.00		160.50	DR Testing					20180315
				White sheet notes 'Changes to test setup for better Wattmon performance' and 'Analysis of accuracy of current loops': / Moved Wattmon A1/VIN to directly off the battery, but looped the Wattmon ground lead through the Discharge current sensor / Realized that current loops can handle +-50 Amp range, not +-25; Test setup (Trace, Delta 200W, Genasun mounted under fan, W9, C252)	TW2-3 IMG WS		6.00		166.50					20180315
				Started '150 CW Discharge/Recovery Test' (see 3/19/18 conclusion)	TW2-3		7.00		173.50					20180315
		16					Continued '150 CW Discharge/Recovery Test' (now in Recovery, see 3/19/18 conclusion): / This day's notes include "Browsing (Looking for a better way to do this!)" and "I woke up and started thinking about methodology again"			13.00		186.50					20180316
				White sheet notes and drawing "Discharge / Recovery Times Guide" (for how to publicize performance data): These notes were updated 3/19/18	TW2-3 WS		4.00		190.50					20180316
				Printed and studied Trojan data sheets for 27TMX and T-105	TW2-3		4.00		194.50					20180316
		17					Continued '150 CW Discharge/Recovery Test' (yet in Bulk, see 3/19/18 conclusion): Includes "Further thoughts on methodology"			4.00		198.50					20180317
		18					Continued '150 CW Discharge/Recovery Test' (3% rule met, see 3/19/18 conclusion)			2.00		200.50					20180318
		19					Concluded '150 CW Discharge/Recovery Test': Improvements needed for "Timing Results", "Accuracy of Wattmon", 'Accuracy/Settability of Constant Wattage (CW)" / Notes on "Correlations" (concerning CW errors) and "Suggestions to improve CW accuracy" / "Maximum Wattage Rating s/b based on LVD"; "Methodology - Changes Needed"; "Automate testing"			6.00		206.50					20180319
				Updated white sheet notes and drawing "Discharge / Recovery Times Guide" (for how to publicize performance data): These notes were started 3/16/18	TW2-3 WS		4.00		210.50					20180319
				White sheet notes 'Wattmon - Questions / Need to know / Configuration' (lots of disconnected answers arrived over the next month)			2.00		212.50					20180319
		20					White sheet notes "Very careful calibraton of Wattmon current loops" / Photos of W100 Testing, Calibration of C252 (Delta 200W, Genasun mounted under fan, BK, Trace being used as CW load)	TW2-3 AED IMG WS		6.00		218.50					20180320
				Printout of WhatsApp Chat with Akash concerning ratings on relay outputs (thinking about automation of test setup): / Summary & Conclusions include "… more than enough contact capacity …"; "… start testing using Pro relay for Delta/Genasun …", "Planning on using i3O2 module for trim resistor(s)"	SSC TW2-3 LIB		3.00		221.50					20180320
		21					White sheet notes "Began Wattmon configuration and set up for Discharge Termination using Relay"	TW2-3 WS		4.00		225.50					20180321
		22					White sheet notes '"Morning" thoughts on how to do CW trim (1&2 resistors) (placed in TODO)' and 'Continued Wattmon configuration and setup for Discharge Termination using Relay' (Delta AC power wired through relay on Wattmon Pro)			6.00		231.50					20180322
		23					White sheet notes (3/22/18 to 3/23/18) "After seeing what I was going to have to do with the Actions (and NVRAM) I decided to change my approach to using uPHP scripting for everything (no Actions)" (started Notes and pseudocode in TODO for entire desired system)	TW2-3 AED WRD WS		4.00		235.50					20180323
		24					White sheet notes (3/23/18 to 3/24/18) concerning Wattmon configuration changes and "Rediscovered" file WRD / ("from now on I'll be recording these R&D notes there, and only printing out notable milestones for this paper file"); WISPower #2 is now being called the "W100" / "Discharge/Recovery Test Setup, Using Wattmon Actions - Notes on METHOD ABANDONED 3/23/18, from TODO" / "Wattmon Logged Data - Curious Mystery" (Akash logging algorithm is not averaging properly)			10.00		245.50					20180324
		27					From/to Keith "Re: new item MikroTik mUPS": "I am currently bench testing WISPOWER prototype #2, which I'm calling the W100 (see photo attached). It is performing above my original expectations, and this configuration is the one I think will sell hundreds of units."; Competition research, library, 2 pdfs	EML LIB TW2-3		3.00		248.50					20180327
		28					From Keith "RE: new item MikroTik mUPS": 'I thought this might be a way to monitor the power it said it had scripts so for 29 bucks might be a better solution than the netonix.'	EML		0.50		249.00					20180328
				WRD for 3/24/18, 3/27/18, 3/28/18: 'Wattmon: Solving the Curious Mystery of cronsec, cronmin and the logged data for “Solar Watts”'; Also see AED	WRD AED		4.00		253.00					20180328
		29					Batteries from RW charging on W100_1 (20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4); Began Recovery Test, ~25w load from ~8% SoC by OCV	WRD		0.50		253.50			B8-11			20180329
2018	Apr	1					White sheet notes "RD trim calibration algorithm": a lot of thought went into this but it is yet to be implemented [as of 5/5/19]	TW2-3 WS		4.00		257.50					20180401
				Finished recovery test, (4) T-105s with ~25w load from ~8% SoC by OCV; Test setup changed (Variacs on all Trace loads)	WRD		2.00		259.50					20180401
		2		~	15:15			Wattmon DR Test Setup (Bench, Wattmon_9, C252_2, I302_1, W100_1, DE_2, Genasun_3, TS_1, 20160421_1/4, 20160421_2/4, 20160421_3/4, 20160421_4/4, BK_1): / Photo sent to Akash	IMG EML		2.00		261.50					20180402
		3					Test setup changed, (4) T-105s -> 27TMX (20150422) / See AED for details on configuring, setting up and programming Wattmon #9 for automating Discharge/Recovery testing (as they won’t be recorded here)	WRD AED		3.00		264.50			B1			20180403
		10					Added Summary for WISPers and History sheet WP1			2.00		266.50					20180410
		11					Bug report for cronmin resolved; Test setup improved (I3O2 and trim resistors on Variac #2)	WRD AED		4.00		270.50					20180411
		12					White sheet notes "DR Trim Calibration": Further thoughts on 4/1/19 ideas	TW2-3 WS		4.00		274.50					20180412
				Test setup improved; Tested trim calibration algorithm ideas	WRD		4.00		278.50					20180412
2018	May	1					Test setup modified to test logging algorithm changes (4/29-5/1, also see AED "Logging for 'total_watts' Not Averaged")	WRD AED		3.00		281.50					20180501
				History sheet WP1 entries from emails and WISPOWER / TurboNet paper file 3/29/17 to 8/31/17			4.00		285.50					20180501
		2					From Keith "backup power supply": He ordered WISPer for Wellington Water Tower; Details, battery size estimate, battery pricing	EML WRD TW2-3		4.00		289.50	On Order					20180502
		3					$780 20180503 Invoice - Wellington.doc Emailed to Mark and Keith with 3/13/18 photo; Mark applied the $400 he paid me on 2/26/18 to it, and will mail me a check on Fr5/4 (I had never given him an invoice, I thought the $400 was for the WISPer for the Rayville Water Tower, but in his mind he's not ready for that one yet)	DBT TW2-3 EML		4.00		293.50					20180503
				07:45		10:15	Assembled another battery/load harness (less 15)	WRD		2.25		295.75					20180503
		5	Sa			~	06:22	Batteries installed in W100 test setup slated for TurboNet (Wellington Water Tower) / B9 and B10 were chosen for this sale because they are the 'oddballs' in the set of (4), with different man'f dates/codes / B10 required more water than B9: B10 ~1/8", B9 ~1/16" (and cells 1 and 3 were high enough to begin with) / I was generous with the water because it may be a long time before they are watered again; Mileage 78 miles @ $0.54 (BFMS KC 2015 to pick up batteries) / 20160421_2/4, 20160421_3/4; Bought inline ATM fuse holders and 20A fuses at Scott's Bargain Barn ($6.97 + 15 miles @ $0.54)	TW2-3	$345.19	3.00	$558.65	298.75			B9-10			20180505
				Began 40w DR Test (W100_1) …	WRD		3.00		301.75					20180505
		7					Updates in red pen to white sheet notes and drawing "Load and battery connections - Final, Testing & RW" (3/13/18); Mark and Keith, arrangements for delivery / Met Mark in parking lot of WalMart in Richmond and rec'd $380.00 check #3065 (mileage, meet @ Lexington tomorrow for delivery), also TODO discussed "Send Invoice for RW, WISPer $400, AC install labor + (~$300?)"	TW2-3 WRD WS	$1.08	3.00	$559.73	304.75					20180507
				Concluded 40w DR Test (W100_1) which was started 5/5/18	WRD		1.00		305.75					20180507
		8			06:00		11:00	Disconnected from test setup; Cleaned; Labels; Brief test; Finished product photos (L0, W100_1, DE_2, Genasun_3); Loaded Subaru	WRD IMG		5.00		310.75					20180508
				11:00		14:45	Onsite, Lexington and Wellington: Installed; Photos and video at WWT (W100_1, DE_2, Genasun_3, 20160421_2/4, 20160421_3/4) / $0.88 distilled water (for TurboNet to water batteries, replaced 5/10/18)		$0.88	3.75	$560.61	314.50	Sold	L6				20180508
				15:30		17:15	Photos and Video transferred and edited	WRD		1.75		316.25					20180508
				18:45		20:30	4 shots + video to Mark and Keith	WRD EML TW2-3		1.75		318.00					20180508
		9			07:00		10:00	Further followup: this .xlsx (Batteries, Genasun, began WP2 summary); Stuff for detailed parts list (AED, printed for file); MailCOPA reminder for watering batteries at WWT	WRD AED TW2-3		3.00		321.00					20180509
				10:00		14:30	History sheet entries for WP1 completed; History sheet entries for WP2 partial; Adding "Photos / Videos" columns to all History sheets, adding data from photos files …			4.50		325.50					20180509
		10			04:30		09:00	Finished adding “Photos / Videos” columns to all History sheets, adding data from photos files …			4.50		330.00					20180510
		11			06:00		17:00	Finished adding all references to photos/videos for all History sheets we have so far / Added Summary sheets ‘Supplies’ (Power Supplies) and ‘Chargers’ (Battery Chargers) …; Started History sheet for Heathkit …; (Less 1 hr)			10.00		340.00					20180511
		12			05:00		14:00	Summary sheets “Supplies” and “Chargers” improved and mostly filled out; Added History sheets for “Supplies” and “Chargers” (but they aren’t filled out yet); (Less 1 hr)			8.00		348.00					20180512
		13			05:45		21:45	Defined Names 'Sheets' and 'SheetNames' (using Excel 4 macro function 'Get.Workbook'); Added sheet "Sheets" with links to all sheets in the workbook / Hyperlinks added to all History sheets headers for column lookups (row 4 LOOKUP, row 5 HYPERLINK in green), LOOKUPs don't error if nothing in column, HYPERLINKs go to sheet 'Sheets' if no matching sheet name / Hyperlinks added to all Summary sheets "Current" columns for values fetched from History sheets (green), History sheet is found from column A, Rows can be easily copied down for added items / “Locations” Summary, more History sheets; Deleted locations we don’t need anymore; Organized / Created detailed History sheets L,L0,L3,L4,L5,L6; Latitude, Longitude column with links to google maps			16.00		364.00					20180513
		14			05:30		12:00	Reordered sheets, Summaries 1st (alphabetical), Histories 2nd (alphabetical); Row 1 link info moved to row 2 (hidden), All Summary and History Sheets use the same columns in row 2			6.50		370.50					20180514
				15:15		16:45	Added “Charger” column to all batteries …, Links to A,BC,C,WP as needed (and updated those sheets as well)			1.50		372.00					20180514
		15			04:15		08:30	Searched sources for information needed to complete summaries and histories for Locations (Shop, Bench, RCWT, TL, RHS, WWT, HAPS, SAPS), Battery Chargers (TS_1, BTJ_1, ENC, SCP_PS1, SCP_PS2), Power Supplies (HZ_1, BK_1, DE_1, DE_2, DE_3), WISPers (WP1, WP2, WP3), UPSs (JC) ...			4.25		376.25					20180515
		16			01:30		07:30	Searched sources (as above for 5/15/18) …			6.00		382.25					20180516
				12:15		19:15				7.00		389.25					20180516
		17			04:30		11:00				6.50		395.75					20180517
		18			02:30		08:30				6.00		401.75					20180518
				14:00		20:30				6.50		408.25					20180518
		19			06:30		13:00				6.50		414.75					20180519
				21:00		01:45				4.75		419.50					20180519
		20			07:00		14:15				7.25		426.75					20180520
		21			05:15		07:45				2.50		429.25					20180521
2018	Jul	26			04:00		06:45	Transferred hours from WRD to here for 4/10/18 to 5/21/18; Completing entries for WP1 and WP2 history sheets …			2.75		432.00					20180726
				11:15		12:30	Completed entries for WP2 history sheet (and other entries here and there for other detail sheets)			1.25		433.25					20180726
		28			03:45		05:15	WP2A Assembly / Parts List …			1.50		434.75					20180728
		29			05:30		05:55				0.42		435.17					20180729
				06:10		06:40				0.50		435.67					20180729
		30			05:45		08:30				2.75		438.42					20180730
2018	Aug	1		~	02:15	~	06:00				3.75		442.17					20180801
		2			06:25	~	06:55				0.50		442.67					20180802
				08:25		08:35				0.17		442.83					20180802
		3			02:45		04:30	WP2A Assembly / Parts List completed			1.75		444.58					20180803
2019	May	5					Finished review and final correction of WP1/WP2 entries from TW2-3			2.00		446.58					20190505
		6					Finished review and updates for WP2 from WRD			1.00		447.58					20190506
		8					Finished review and updates for WP2 from emails and business documents			0.25		447.83					20190508
				Finished history sheet for L6 (WWT)			0.50		448.33					20190508
2021	Mar	12	Fr	~	13:30	~	16:05	Onsite at WWT for the Backup Power Supply Maintenance Program; See L6 for details	DBT TM21S SMS SSC					L6	B9-10			20210312
		13	Sa					Email Report to Mark and Keith; Recommended tshooting high power levels; Run-time Estimate ">12 Hrs @ 133 watts"	EML TM21S					20210313
2022	Jun	28	Tu	~	15:15	~	16:30	Onsite at WWT: W100_1 and ambient ~34⁰C; W100 fan is running; T-105s 13.515vM (13.44vF equivalent, good Float V for current battery T); Removed to take to shop	TM22 L6					Subaru	-	S4	C4	20220628
		30	Th					W100_1 boxed, labeled and on North bench	TM22					L				20220630
2023	Jan	14	Sa					R&D TODO: WP2 should be cleaned up and offered as a Spare (make it available to Keith and Mark)	DWP WP12

## WP3
WISPers: WP3	A					W100_2 ― 1st Production Run ― Delta PS 24v/200w, Genasun, Fan, 27TMX, Service Calls					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$139.95	97.41	Sold	L1	B54	S5	C6
2018	May	7					WalMart parking lot discussion with Mark (after picking up $ for WWT W100_1): Send invoice for RW, WISPer $400, AC install labor + (~$300?)	TW2-3		0.25		0.25	On Order					20180507
				Trojan 27TMX battery 20150422 will be used (TurboNet paid for this in 2015); DE_3 will be used (3/9/18 $0.00 no charge replacement for lost FedEx shipment)		$0.00		$0.00			L	B1	S5		20180507
	Jun	5	Tu					Phone call and EML to Mark Webb "Rayville Water Tower - Initial Estimate - Request for Advance"; Missouri One Call ticket opened	EML TW2-3		0.50		0.75					20180605
		6	We					Met with Mark Webb at USB in Richmond, rec'd and deposited $400.00 check for "Rayville electrical hook -up (half)" / 1/2 the mileage and time because some of this is for AC installation (not WISPer #3)	TW2-3	$5.40	0.50	$5.40	1.25					20180606
		8	Fr					Onsite at RW to meet with Christ Adams (USIC), Doug Alberti (AUE) and Stan Barr (PWSD) to locate and discuss AC installation for TurboNet (no expense recorded for WISPer #3)			0.00		1.25					20180608
	Jul	3	Tu					To Stan Barr of PWSD (and Mark and Keith) with 20180703 PWSD Proposal.pdf: This is all about the AC installation, no expense for W100_2)	EML DBT TW2-3		0.00		1.25					20180703
		20	Fr					Onsite at RW with Stan Barr of PWSD: Installed AC outlet inside equipment box; Removed Genasun_5 (slated to be used for W100_2, 9/10/15 cost) / Also removed P_3 (slated for SAPS)		$105.41	0.25	$110.81	1.50					C6	20180720
		24	Tu	~	02:00	~	04:00	Invoice sent to Mark Webb for "Rayville Water Tower - AC and WISPer Installation"; Most of the time spent to do this was for AC installation	DBT EML TW2-3		0.50		2.00					20180724
		25	We	~	04:00	~	06:15	DigiKey order prepared (fan, guard/filter, 4mm screws)			2.25		4.25					20180725
				~	11:15	~	11:30	DigiKey order placed	EML DKE	$26.99	0.25	$137.80	4.50					20180725
		27	Fr	~	02:30	~	03:45	WP3 History Sheet up to date; DigiKey order rec'd	DKE		1.25		5.75					20180727
		31	Tu		08:00		08:15	Called Mark and LMVM			0.13		5.88					20180731
				08:35		08:40	Call from Mark: Meet in Richmond and he'll give me check			0.08		5.96					20180731
				09:25	~	10:45	Call from Mark: Meet in WalMart; Went to Richmond and rec'd $498.50 check (final payment, AC and W100 @ RW) / 1/2 the mileage and time because some of this is for AC installation (not WISPer #3)	TW2-3	$5.40	0.67		6.63					20180731
	Aug	3	Fr		04:30		05:00	WP3A Assembly / Parts List …			0.50		7.13					20180803
		4	Sa		03:00		06:25				3.42		10.54					20180804
				11:15		11:30	WP3A Assembly / Parts List more or less completed and printed for assembly stage			0.25		10.79	Assembly	L0				20180804
		5	Su		03:50		04:00	Unpacked DigiKey order			0.17		10.96					20180805
				05:15		05:45	AC Input cord: Cut, tin and label colors; Attach and test Power Supply; Updated WP3A for zip ties			0.50		11.46					20180805
				07:20		07:35	WP3A Assembly / Parts List (Assembled column)			0.25		11.71					20180805
				07:35		08:10	Genasun: Cover removed; labelled; C6 History			0.58		12.29					20180805
				08:40		09:15	Planned holes for Genasun and fan assembly; Template made and printed (20180805 W100_2 Genasun & Fan Template - Scan.jpg); Genasun mounted	TW2-3		0.58		12.88					20180805
		8	We	~	07:45		08:15	Analysis: Without the 3rd panel at RW we lose 1% WSoC on a good sunny day (currently 42%, low of 11.3v) / But charge efficiency is very high, so we could be breaking even or even a little better; In any case, a few cloudy days and we can drop a lot / I only have a few more days to finish the installation at RW			0.50		13.38					20180808
				08:15		13:15	Fan mounted on power supply cover: See 20180805 W100_2 Genasun & Fan Template - Scan.jpg "8/5/2018" / As part of this I had to clean up around the garage bench in order to make space to collect the hardware, I smoked a little bit, played cards, updated WP3A for stock, dealt with Marcus & Sharon (lawn mowing $40), replied to Mark Webb's inquiry "did you get it done?", walked over to talk to the guys working at the other house demolition project near 2nd and Alley, showed Danny & Michael what sheet metal they could take, started a batch of laundry / Although 5 hours, for this one I estimate it took 3 hours, and projection of 2 hours is good (with no distractions)	TW2-3 SMS		3.00		16.38					20180808
		9	Th		01:45		02:20	Cut, tin and wire Genasun to Power Supply			0.58		16.96					20180809
				02:20		03:05	Attached 20A fuse holder and fuses to harness (which was the 1st one made for bench testing)			0.75		17.71					20180809
				03:05		04:00	Calibration tweaked on C252_2 (which will be installed at RW), but realized I needed to do this for zero balance at ~30 watts load, so no changes yet	WRD		0.92		18.63					20180809
				04:00		08:30	Harness attached, testing (initial Absorption, no load) / Attached Trace and adjusted Variac #1 for 26 watts (a good year-round average for RW now, it will be lower in winter and higher in summer) / Calculated battery capacity by calculating PC for C/100 and C/20 (1.072083554) and then the AH battery capacity for 26 watts @ 12v = 2.17 amps (111.90 AH ~ 112 AH) / Applied this to Wattmon_9 (and will be applied to Wattmon_8 @ RW); Entries began in WRD for DR Test @ 26w / Adjusted calibration on C252_2 for a positive balance (see Master Configuration) / Examined how W9 is configured to be sure the actions will work as intended for an unattended discharge to 50% WSoC / Made sure W9 is logging, both log file for portal and log file for later analysis (Test Averaging) / Started DR test, but aborted a few minutes later when I realized the zeroes for C252_2 need to be adjusted again (Solar Charge is 2w positive when no charging) / (most of the changes s/b to loop 2, which never sees zero); Waiting for Genasun Absorption to finish ...	WRD AED		4.50		23.13	Testing					20180809
				18:30		19:40	Tweaked calibration on C252_2 (now have a good positive balance at ~26w) but Charge Efficiency must be 100%; Started 26w DR Test …	WRD		1.17		24.29					20180809
		10	Fr	~	02:45	~	03:00	Observations and TODO, 26w DR Test …			0.25		24.54					20180810
		11	Sa	~	05:00	~	05:30				0.50		25.04					20180811
				~	09:00		09:30	26w DR Test Concluded and Summarized			0.50		25.54					20180811
		12	Su	~	06:45	~	08:15	Removed from DR Test Setup; Labels			1.50		27.04	Slated for RW					20180812
		13	Mo	~	00:45	~	04:30	Finished product photos; Watered battery (20150422, B1) / Gathered tools & stuff to take to RW (mounting hole template printed, see "20180813_032752 Screenshot.jpg AcroRd32"); TODO for onsite	IMG SSC		3.75		30.79	Ready for RW	L				20180813
				~	09:00		13:30	Loaded Subaru and left for tower; Onsite at RW 09:15; AC OK; Photos (before); Removed solar panels, Genasuns, (2) T-105s in main equipment box and C252_1 / Installed W100_2 (with C252_2) and 27TMX (Netonix running); Set up for onsite Tshooting of W8 corruption issues; SD Card Copy (not checked, decided to Tshoot at shop) / Removed W8; Removed (2) T-105s, battery box and battery bus bar; More photos (after); Returned to Shop ~12:30; Subaru unloaded (but lots of stuff to sort through and put away) / T450s problems (no drives, keyboard, mouse)	IMG W8		4.50		35.29	Sold	L1				20180813
		14	Tu	~	00:00		04:10	Tshooting T450s ...; Photos transferred and organized; This .xlsm entries ...; Parts and tools sorted …			4.17		39.46					20180814
				05:50		06:05	Tshooting T450s …			0.25		39.71					20180814
				06:20	~	06:40	Tshooting T450s …; Tshooting TurboNet (slow speeds); Contacted Mark Webb; This .xlsm entries ...; Parts and tools sorted …;	SMS		0.33		40.04					20180814
				07:05	~	07:20	Tshooting T450s … but the problem is chronic, and I must work on it later, so will focus on T450s later after getting some things done about RW and the W100			0.25		40.29					20180814
				07:20	~	09:45	This .xlsm entries …; Called Mark Webb; .xlsm entries caught up for status and location changes yesterday; TODO caught up			2.42		42.71					20180814
		15	We	~	00:55		08:20	Wattmon_8 (W8) on bench: Corruption issues fixed; Calibrated A1/Vin; Updated FW & OS; Configured Devices for C252_1 removal / Changed Device Name; Battery and Charge Settings Modified; Description changed on my.wattmon.com to L1W8M2O2	W8		7.42		50.13					20180815
		16	Th	~	02:00		06:20	Studied what I need TODO for SMTP Notifications; Experimented with ems.wattmon.com (not capable enough) / Decided to write as Action based using NVRAM and /config/mail.ini; TODO for Actions system			4.33		54.46					20180816
		17	Fr	~	02:00	~	03:45	Wrote script nvram_unset.cgi and cleaned NVRAM			1.75		56.21					20180817
				~	04:00	~	06:00	Actions system TODO (NVRAM, mail.cgi, mail.ini)			2.00		58.21					20180817
		18	Sa	~	00:15	~	07:50	Actions system TODO (NVRAM, mail.cgi, mail.ini); Edited, uploaded and tested /config/mail.ini and smtp.cgi (problems encountered with NVRAM full errors) / Email to Akash '"NVRAM full" but it's not!'	W8 EML		7.58		65.79					20180818
				~	23:00	~	00:45	TODO, idea for not using NVRAM; nvram.dat created, examined, sent to Akash			1.75		67.54					20180818
		19	Su	~	01:15	~	02:45	TODO	W8		1.50		69.04					20180819
				~	03:30	~	06:45	TODO; Global Variables listed in Variables Widget; Edited, uploaded and tested /config/mail.ini and smtp.cgi			3.25		72.29					20180819
		20	Mo	~	01:30	~	06:00	TODO; /config/mail.ini; /config/Jeff/smtp.cgi			4.50		76.79					20180820
				~	21:20		00:00	TODO; Variables Widget; Actions deleted; /config/mail.ini; /config/Jeff/smtp.cgi			2.67		79.46					20180820
		21	Tu		00:00		03:25	Problems with lockups, only when Variables Widget is enabled and trying to display a string variable that doesn't evaluate to a numeric / Modified /scripts/runonce.cgi for testing and restored the original version; Email to Akash "Bug Report: Variable Widget Package"	W8 EML		3.42		82.88					20180821
				03:25		05:45	From 8/13/18 installation of AC, removal of solar stuff and installation of W100_2: Parts and tools sorted and put away; (4) T-105s cleaned, VoC measured, charging on Trace			2.33		85.21					20180821
				05:45		06:45	From Akash "Re: Bug Report: Variable Widget Package"; Uploaded ajaxdata.cgi he provided and tested (that fixed it); Restored Variables Widget configuration (role=31, vars=Run,Msg,Exceptions,Ready,C01,V13,V11,SOC100,SOC050,SOC000); smtp.cgi is now working to the die point; To Akash "Re: Bug Report: Variable Widget Package"	W8 EML		1.00		86.21					20180821
		22	We	~	03:30	~	04:45	From Akash 'Re: "NVRAM full" but it's not!'; FW patched with file Wattmon_Core.production.hex (1.1113->1.1114); /scripts/tests/nvram.cgi?defrag=1 / NVRAM Free went from -20DEFRAG! to 7996; Tested nvram functions (using /scripts/tests/nvram.cgi and /config/Jeff/nram_unset.cgi) and FW patch seems to be successful in fixing the NVRAM problems; To Akash 'Re: "NVRAM full" but it's not!' (fixed) / Hours are here because this was related to installing the W8 SMTP Notifications system, but I've decided not to use NVRAM for that, as every Action calls smtp.cgi	EML W8		1.25		87.46					20180822
				~	04:45	~	05:45	Coding and testing smtp.cgi, ran into problems again with Variables Widget (fails with empty string, works with space string ' '); Email to Akash "Bug Report 2: Variable Widget Package"	W8 EML		1.00		88.46					20180822
2019	Apr	29	Mo		11:00		14:05	Prep., travel, onsite at RW and follow up: Battery watered; Checked AC outlet & installed cover plate; Removed the last of the Wattmon stuff / Cleaned W100 fan/filter (compressor); Ant trap installed	TW2-3		3.08		91.54					20190429
	May	4	Sa					Invoice sent to Mark via email & USPS "Revised Invoices as per our agreement", $160 and $120 but "Paid in Full by Service Rendered (Internet before 5/1/19)" / Income for $120 added to revenue for WP3	DBT TW2-3		1.00		92.54					20190504
		5	Su					Finished review and update of these chronological notes from TW2-3			0.50		93.04					20190505
		6					Finished review and updates for WP3 from WRD			0.25		93.29					20190506
		8					Finished review and updates for WP3 from emails and business documents			0.25		93.54					20190508
		15	We		08:38		09:28	Power outage including Rayville, Wood Heights …; Power restored after 50 minutes; Load during this time was about 28 Watts/~2.3 Amps; Therefore battery discharged to ~98 %SoC			0.25		93.79					20190515
	Jun	27	Th		08:11	~	09:45	Call from Mark Webb: He asked that I come over and help him remove the battery and box, and store it at my place / I volunteered to keep it float charged (but it doesn't really need to be if we're down for less than 6 months); I should charge him for this time, and settle on the internet / Stopped my work with W100 Testing, got dressed, loaded toals and went in the Subaru ...; Returned and moved box and battery to W storage, and the poles to the old house driveway / Chargeable time at least one hour / Onsite I agreed with Mark that if he considered the $110 invoice as paid in full (worth about $60 to me, because it hasn't been 10 Mbps CIR) than I won't bill him for my time / Updated status on L1, B1 and WP3; WP3 hours increased by this time; WP3 income increased by $60	TW2-3 IMG		1.57		95.36		L				20190627
		29	Sa	~	09:00			B1 Moved to bench for W100 testing	WRD		0.10		95.46			-			20190629
	Aug	7	We	~	08:15	~	14:55	Called Keith, NA; SMSs …; Call from Keith: He's in California setting up wireless for a wine train; He'll be back from CA and FL in 1-2 weeks / B54 and W100_2 won't be installed at Lexington until he is back and there is time to do it; I mentioned that RW tower may be finished in about 2 weeks and he said "I don't care"	SMS L1 WP5 B54		0.10		95.56					20190807
	Sep	5	Th	~	10:00	~	10:45	New label applied to equipment box …; Keith and Brandon left for RW with equipment box, battery and my post driver			0.20		95.76		L1	B54			20190905
		6	Fr		13:13		14:20	Call to Keith who is onsite at RW; Mark is on the tower; Please come and help with AC; Prep. and on site; AC connection finalized; Zip ties; WP3 is in Float / Mark and I agree to call it even for this service call and this month's internet charge (24/30*$110=$88 added to revenue for WP3); Returned to shop; On site again, silicone in conduit			1.12		96.88					20190906
		9	Mo					Mark Webb knocks on the door and asks me for a fuse (internet outage this weekend was caused by the Netonix shorting down during a thunderstorm) / I tell him there is one silver taped to the cable next to the fuse holder; I also gave him (2) from stock (cost and procurement time from WP5A) / [Note added after talking with Brandon: Keith replaced the DC Netonix with an AC Netonix, because they don't have another DC unit in stock / Battery is probably being charged by WP3]	SMS	$2.15	0.33	$139.95	97.21					20190909
				14:41	~	14:45	Call to Keith NA; Call to Mark NA; To Keith "So from what I learned from Mark and Brandon, when the DC Netonix went down it shorted out the power supply, but the fuse I designed did what it was supposed to do and kept there from being a fire. And that now, the water tower is running on an AC Netonix. Correct?"	SMS		0.10		97.31					20190909
				14:51	~	14:56	Call from Mark, who confirmed the facts stated above (but that they used some cheap switch, not an AC Netonix)			0.10		97.41					20190909
2021	Mar	10	We	~	14:30	~	16:25	Onsite at RW for contracted maintenance: 14.2v Float and 28.9w Load; See B54 for details	TM21S SMS EML SSC					L1	B54			20210310
		11	Th	~	08:45	~	09:00	Onsite at RW to reapply AC power and shoot a photo showing the watering system in use; See B54 for details	TM21S SMS SSC IMG					20210311
				11:19			Screenshot of Netonix Input Voltage graph showing Bulk/Absorption transition; See B54 for details	TM21S SSC					20210311
				13:36			Screenshot of Netonix Input Voltage graph showing transition from Absorption to Float; See B54 for details					20210311
	Dec	23	Th	~	10:27	~	10:30	Logged into Netonix, cleared log, no power losses in past 24 hours, Float 13.7-13.8v	TM21F EML					L1				20211223
		27	Mo	~	06:55			Logged into Netonix: Load ~56w; Float 13.78v	TM21F SSC					20211227
2022	Jan	5	We	~	11:19			Logged into Netonix, no power losses in past 24 hours, Load ~56w, Float 14.0v	TM22 SSC EML					L1				20220105
	Mar	1	Tu	~	17:30	~	17:50	Onsite at RW: Float 14.03vF equivalent (14.11vM) at 75⁰F Fluke IRT (slightly high for that temperature, Genasun has not reset lately); Fan not checked, filter not cleaned	TM22					L1				20220301
	Apr	24	Su	~	09:49	~	19:20	No charging: Netonix notification EML 09:52; Logged into Netonix, SSCs; Load ~18w ...; Charging resumed (not sure yet why)	TM22 EML SSC					L1				20220424
		25	Mo	~	00:00			No charging again: Netonix notification EML 00:06; SSCs, 08:00 shows the entire event so far					20220425
		26	Tu	~	14:40	~	15:35	Onsite at RW: No AC Power; Power restored by wiggling plug in PWSD's exterior outlet; Load ~18w	TM22 EML SMS SSC					L1				20220426
		27	We	~	07:00	~	12:40	Logged into Netonix: Float 13.6vN (the Genasun was reset yesterday when the power was restored and the battery was ~19degC)	TM22 SSC					20220427

## WP4
WISPers: WP4	A					W100_3 ― 2nd Production Run ― Delta PS 24v/200w, Genasun, Fan, 27TMX					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$487.70	122.37	Sold	L7	B1	S6	C1
2019	Apr	27	Sa					[WP4-6] Purchased (3) in-line fuse holders @ Westlake Ace Hardware (planning on building at least 3 more W100s, WP4-WP6), Cost is for one	TW4-5	$3.90	0.17	$3.90	0.17	Orders…	L0				20190427
		28	Su	~	17:30	~	18:15	[WP4-6] History sheets created for WP4, WP5 and WP6; Assembly sheet created WP4A (but not completed yet)			0.25		0.42					20190428
2019	May	10	Fr					[WP4-6] Purchased (5) 20 amp ATM fuses @ WalMart; I have (1) in stock, now have enough for 3 more W100s; Cost is divided equally for WP4, WP5 and WP6	TW4-5	$1.43	0.17	$5.33	0.58					20190510
2019	Jun	3	Mo		13:51		13:54	Mark Webb called to request I contact Keith to discuss W100 for Odessa	AED		0.25		0.83					20190603
		4	Tu		08:50	~	15:05	Attempted contact with Keith; Mark Webb called and confirmed order for W100, smallest size battery and onsite installation at Odessa / Contacted BFMS for quotes, 27TMX is $166.50 (pickup We6/5) … / Keith called, Odessa has DC Netonix and a "900" which runs on AC (which he does not care to battery back even though we could buy a small inverter), / confirmed order for W100, I have 2-3 weeks (but I told him I needed 1-2 weeks)			2.00		2.83					20190604
		5	We					Purchased Trojan 27TMX at BFMS, $166.50 + 78 miles @ $0.58; On this trip I also went to Wabash to recycle batteries, visited Karen Thomas, went to Lowe's and Price Chopper in Liberty, therefore Mileage and Hours is 1/4 what it would normally take; 20190605 (B54)	TW4-5	$177.81	0.75	$183.14	3.58			B54			20190605
		7	Fr	~	08:15	~	08:30	Completed entries for this sheet 6/3 to 6/5/19			0.25		3.83					20190607
		8	Sa	~	02:15	~	03:30	Started sheet for battery (20190605/B54) and cleaned up shipping cost on Batteries Summary Sheet			1.25		5.08					20190608
				~	03:30	~	04:30	Created Invoice for TurboNet "20190604 Invoice - Odessa W100"; Emailed to Mark and Keith	DBT TW4-5 EML		1.00		6.08					20190608
				~	04:30	~	08:00	WP4A Parts List partially reviewed and updated (it had been copied from WP3A but not completed); Genasun_1 (C1) 4/22/15 cost w/S&H		$106.63	3.50	$289.77	9.58					C1	20190608
				~	09:15	~	10:05	27TMX (20190605/B54) moved from Subaru, cleaned, water checked, charging, labeled			0.83		10.42					20190608
		9	Su	~	02:00	~	04:00	Finished review and update of WP4A Parts List, most of the time spent considering what to do about the LM-01 "Top Fixing Brackets"			2.00		12.42					20190609
		11	Tu		08:50		09:50	Called Mark (c): Relayed info from Stan Barr; Complained again about <1Mbps service; Was told not to bother to pay $110 for June until after we see when RW goes down and if they can possibly give me a temporary link; Will meet @ USB in Richmond for check for W100 in Odessa	TW4-5		0.20		12.62					20190611
				~	11:00			Mark met me @ USB in Richmond and I rec'd $796.50 check in payment of invoice 20190604 [mileage and time 1/2 due to other errands in town]		$5.22	0.50	$294.99	13.12					20190611
		12	We	~	01:20	~	02:00	[WP4-5] DigiKey order placed: (2) each of power supplies, fans and fan filter/guards [cost and hours divided 1/2 for W100_3 & W100_4]	EML DKE	$66.20	0.33	$361.18	13.45				S6		20190612
				~	02:00	~	02:30	[WP4-5] BoltDepot.com order placed: (100) each of 6-32x3" and M4x0.7x6 screws / [cost and hours divided 1/2 for W100_3 & W100_4]	EML TW4-5 BDC	$12.85	0.25	$374.03	13.70					20190612
				[WP4-5] Westlake Ace Hardware: Purchased (8) Corner Braces (alternative to "Top Fixing Bracket") / [cost and hours divided between W100_3 & W100_4, mileage & hours is 1/2 typical due to other errands]; All needed parts for W100_3 and W100_4 are on order	TW4-5	$6.49	0.25	$380.52	13.95	Waiting Parts					20190612
		13	Th	~	04:30	~	05:45	Updated WP4A for corner brace alternative to Delta LM-01			1.25		15.20					20190613
				~	06:00	~	06:30	Created sheets S6, S7 (power supplies) and updated WP4 and WP5			0.50		15.70					20190613
		14	Fr					[WP4-5] DigiKey and BoltDepot orders received	DKE TW4-5 BDC		0.00		15.70					20190614
		17	Mo	~	04:30	~	05:30	[WP4-5] Began Assembly: DigiKey and BoltsDepot orders rec'd, unpacked, labelled and sheets S6/S7/Supplies updated (During Assembly phase all Hrs split 1/2 W100_3/4)	TW4-5		0.50		16.20	Assembly					20190617

		18	Tu	~	00:20	~	00:50	[WP4-5] Supply: AC Power Cord prepared and attached to power supply			0.25		16.45					20190618
				~	00:50	~	01:50	[WP4-5] Genasun: Cover removed, stickers applied, WP4A and WP5A modified to show stickers			0.50		16.95					20190618
				~	01:50	~	02:20	[WP4-5] Genasun: Mounted on Power Supply			0.25		17.20					20190618
				~	02:40	~	04:40	[WP4-5] Fan: Mount over Genasun (bend LED out); Remount cover on power supply; Cut leads 5.5" beyond fan, 5.25" shrink …			1.00		18.20					20190618
				~	15:15	~	15:45	[WP4-5] Fan: … strip and tin fan leads; Attach fan to L & N; Test; 2 units side by side	IMG		0.25		18.45					20190618
				~	17:00	~	18:45	[WP4-5] Supply: Cut, tin and wire Genasun to Power Supply; Improved 20190618 W100 Genasun, Fan & Wire Ties Template.jpg	SSC TW2-3		0.88		19.33					20190618
		19	We	~	07:15	~	08:00	[WP4-5] Harness: Improved and scanned 3/13/18 drawing for harness for WISPer #2 (W100_1) 20180313^14;20190619 W100 Harness Assembly Scan.jpg			0.37		19.70					20190619
				~	08:00	~	09:00	[WP4-5] Harness: Gathered all parts and notated upcoming stock needs on some of them			0.50		20.20					20190619
		20	Th	~	02:55	~	04:30	[WP4-5] Harness: Assembled / Improved WP4A/WP5A (better order for listing of parts, this consumed about 30 mins as I had a "hickup" with Excel and had to restore the previous version) / I screwed up several times, and had to add some extra 3/8" shrink to one of the inline splices ...			0.79		20.99					20190620
				~	13:00	~	18:30	[WP4-5] Harness: … I worked on fixing the Blazer Micro Torch (which is a far better tool for the inline splices than the big torch) / Disassembled and measured o-rings; Ordered from "Global O-Ring and Seal" (split 1/2 W100_3/4)	EML	$6.55	2.75	$387.06	23.74					20190620
		21	Fr	~	06:20	~	07:35	[WP4-5] Harness: … assembled and attached …			0.63		24.37					20190621
				~	08:15	~	08:45	[WP4-5] Harness: … moved dessicating oven from test bench …			0.25		24.62					20190621
				~	10:00	~	10:15	Called Keith, LMVM, then SMS: to let him know that the W100 is ready for Odessa and that we need to talk	SMS		0.25		24.87					20190621
				~	10:10	~	10:25	Called Mark, LMVM, then SMS: also to let him know that the W100 is ready for Odessa and that we need to talk; SMS reply "…We'll have to do it Monday."			0.25		25.12					20190621
				~	13:37	~	13:55	Keith called: Odessa will be installed Tuesday or Wednesday; RW internet sucks, resonances in cables, very low speeds, nothing to be done about it / He provided 200 Mbps to Van Till, but there is no way to get a connection from there to here; Helium balloon, omni antenna, dirigible?			0.30		25.42					20190621
		22	Sa	~	04:45	~	04:55	27TMX removed from ENC, moved to test bench and water levels checked			0.17		25.58					20190622
				~	04:55	~	05:35	[WP4-5] Harness: … Trace inverter moved from Subaru to test bench; Quick test of W100_3 and W100_4 (no load, immediate Absorption 14.44 vdc)			0.33		25.92					20190622
				~	05:35	~	07:35	[WP4-5] Labels: Printed, ran out of 1/2" tape and will have to reorder in order to finish W100_4 / Redesigned W100 SN Man'f.lbx for 1" tape instead of 1.5" (the old design covers the mounting screw for the "Top Fixing Bracket"); Applied labels	LBX		1.00		26.92					20190622
				~	07:35	~	09:20	[WP4-5] Ordered label tapes from Amazon (1/4", 1/2", 3/4", 1", 1" yellow) [split 1/2 W100_3/4]	EML	$53.66	0.88	$440.72	27.79					20190622
				~	09:20	~	11:00	[WP4-5] W100 Mount: Installed brackets: Refined WP4A & WP5A for lock/star washers, and mounting brackets are no longer optional; W100 Mounting Screws.lbx created / WP4A and WP5A are up to date (During further testing phase all Hrs split 1/2 W100_3/4)	LBX		0.83		28.63	Parallel Test					20190622
		23	Su	~	03:30	~	11:00	[WP4-5] Designed Parallel Test setup using W10, A10, M1 and M2 (see white sheet schematic 20190623^0629;0726 Parallel Test Schematic Scan.jpg) / Setup and calibration of Wattmon and C252 modules (problems with firmware and OS) …	TW4-5 AED SSC WCX WS		3.75		32.38					20190623
				~	23:15	~	04:45	[WP4-5] … Setup and calibration of W10 (still having problems with firmware, will need to let Akash tshoot via AnyDesk) …	AED		2.75		35.13					20190623
		24	Mo	~	12:15	~	13:45	[WP4-5] … Setup and calibration of W10 (completed basic review of config, next need to add devices) …			0.75		35.88					20190624
		25	Tu	~	03:50	~	08:35	[WP4-5] … Setup and calibration of W10, Devices, calibration of C252_1 …	AED TW4-5		2.38		38.25					20190625
				~	09:55		10:05	[WP4-5] Mark Webb called: He wanted to install W100_3 in Odessa tomorrow, but I told him "No, I'm booked" (E.S. food pantry day) / He proposed Thursday, but I said I wouldn't know until tomorrow afternoon / (I'm hoping to get a parallel/series test finished but it isn't looking good because there's so much Wattmon setup to do) / He'll call me tomorrow afternoon to find out about Thursday; If not Thursday he'll want to do Friday			0.08		38.33					20190625
				~	21:00	~	23:15	[WP4-5] … Setup and calibration of W10, Devices, calibration of C252_1 completed	AED		1.13		39.46					20190625
				~	23:15	~	01:15	[WP4-5] … Setup and calibration of W10, Devices, calibration of C252_2 completed			1.00		40.46					20190625
		26	We	~	01:15	~	04:00	[WP4-5] … Setup and calibration of W10, Devices, A10_1 calibration checked	AED TW4-5		1.38		41.83					20190626
		27	Th	~	04:00	~	08:30	[WP4-5] … Setup of W10, integrated (2) C252s and A10 into test setup with Trace; Configured Roles …			2.25		44.08					20190627
				10:38		10:42	[WP4-5] Mark called, Odessa installation scheduled for Mo7/1 10:00, meet at TurboNet office in Lexington and go from there			0.03		44.12					20190627
		28	Fr	~	03:30	~	13:30	[WP4-5] … Setup of W10, configuring Roles; C252_1 Calibration changed (Invert); ajax_refresh_time adjusted; Finished review of config; List of issues yet to resolve in TODO / SD Card copy; FW 2.1128->2.1135 (can't connect); SD Card copy; Restored FW 2.1128; To Akash with .zip for his t-shooting of FW upgrade problem / Battery capacity for 200w DR test calculated and configured; Began 200w DR test (manual adjustments of load wattage trim and manual cutoff @ 50% SoC) / Photos of W100 Parallel Test setup: BK_1, WP4, WP5, S6, S7, Genasun_1, Genasun_2, A10_1, B54, Trace, W10, I302_1, W9, O1, C252_1 & C252_2, S1 / Some extra time in the next 5-6 hours for trimming the DR test (these notes @ 12:45) ...	AED WCX WRD EML IMG		5.00		49.12					20190628
		29	Sa	~	05:15	~	08:00	[WP4-5] … Thoughts on future products W200P and W200S (TODO); Analysis of results from yesterday's 200w Parallel DR Test #0 / Thoughts on max wattage ratings of the W100 as a function of battery voltage (TODO); Maximum Power Testing, W100_3 and W100_4 in parallel / Parallel Testing Concluded (I will analyze the .csv a little closer later, but I've learned what I needed to learn) / See white sheet schematic "W100_3 (WP4) & W100_4 (WP5) Parallel Test" (Su6/23 to Sa6/29/19) 20190623^0629;0726 Parallel Test Schematic Scan.jpg	WRD TW4-5 SSC WS		1.38		50.49					20190629
				~	08:00	~	13:00	[WP4-5] Disassembled Parallel Setup; More thoughts on W200P vs. W200S (the series version is preferable, as it lowers all the currents and will need smaller wire) / Series Test Setup (20190629;0702;0726 Series Test Schematic Scan.jpg), calibration of W10 A1/Vin (problems connecting, quit) …	WRD TW4-5 SSC		2.50		52.99	Series Test					20190629
		30	Su	~	01:00	~	12:00	[WP4-5] … Series Test Setup, problems connecting resolved (bad ethernet cable connection); Calibration of W10 A1/Vin completed; W10 Dashboard Widgets moved / I3O2 attached, Roles and Logging configured; RL5 wired to power both WP4 and WP5 from T1 Main; I3O2 outputs wired to trim resistors; (2) Actions for Trim created and tested	WRD AED		5.50		58.49					20190630
				~	13:15	~	15:45	[WP4-5] … Final trim and setup; Details and summary of 200w Series Test (Discharge started at 14:00); Stopped giving it my 100% attention at ~15:00 / I will have to "Bird Dog" this test over the next ~18 hrs [Note added later: I estimated about 45 mins for watching it and taking notes for the rest of Su6/30]	WRD		1.25		59.74					20190630
2019	Jul	1	Mo	~	04:25	~	13:25	[WP4-5] … 200w Series Test, detailed notes; The test is flawed, will have to repeat, but finished it anyway (we went to 34.7% SoC) / Thoughts and notes on red sheet "DR System w/2 Trim Loads 7/1/19" 20190701^0702;0726 DR System with 2 Trim Loads Scan_3pages.pdf / 08:00-08:30 Called Keith Jones to reschedule Odessa installation (giving me more time, until Wednesday or Friday) ...; Concluded flawed 200w Series Test	WRD TW4-5 SSC		4.50		64.24					20190701
		2	Tu	~	00:00		11:00	[WP4-5] … Caught up on notes and schematics for Parallel Test and 1st Series Test / See white sheet schematic "Series Test W100_3 (WP4) & W100_4 (WP5)" Sa6/29 Assembly, Tu7/2 Schematic 20190629;0702;0726 Series Test Schematic Scan.jpg / See white sheet "DR System w/2 Equal Trim Loads" (4-5 Actions) 7/2/19; Setup for 2nd DR Test; [Interupted for 1 hour by phone call from Karen Thomas] … / Began 2nd Series Test @ 200w	WRD TW4-5 SSC WS		5.00		69.24					20190702
				11:00	~	12:00	[WP4-5] Birddogging test until I'm sure it's all OK and notes are caught up …; All is stable, I'm going to take a break and go to Richmond for beer	WRD		0.50		69.74					20190702
				[WP4-5] Birddogging & notes, total of about 35 mins			0.25		69.99					20190702
				~	12:55	~	13:25	[WP4-5] I didn't make it to Richmond yet: Test Failed @ 12:59 when W10 rebooted itself; Notes (and then I left for Richmond)			0.25		70.24					20190702
		3	We	~	03:50	~	05:15	[WP4-5] Load killed; Notes; Screenshots; End of 2nd Series Test (200w) [Failed]			0.71		70.95					20190703
				~	06:30		09:00	[WP4-5] Corrections to Wattmon setup and configuration …; Began 3rd Series Test (200w)	AED WRD		1.25		72.20					20190703
				09:00	~	09:30	[WP4-5] Birddogging test until I'm sure it's all OK and notes are caught up	WRD		0.25		72.45					20190703
				[WP4-5] Birddogging, various times, estimated			0.54		72.99					20190703
		4	Th	~	00:45	~	02:45	[WP4-5] Absorption; Notes, Birddogging; Initial Summary of Results (now in Float)			1.00		73.99					20190704
				~	00:50		06:30	[WP4-5] Examined log files directly on W10 to see if I can judge 3% ratio rule, killed Liebert to see if I can judge 3% rule with Live Energy; End of 3rd Series Test (200w)			2.83		76.83					20190704
				~	08:45	~	10:30	[WP4-5] Began setup for 4th Series Test @ 300w …; WP4/B54 went into Absorption, must wait to finish Pre-Launch Checklist	AED WRD		0.88		77.70					20190704
				~	14:00		14:30	[WP4-5] Continued setup for 4th Series Test @ 300w …; Began 4th Series Test (300w)			0.25		77.95					20190704
				14:30	~	15:00	[WP4-5] Birddogging	WRD		0.25		78.20					20190704
				[WP4-5] Birddogging, various times, estimated			0.42		78.62					20190704
		5	Fr	~	04:00	~	05:25	[WP4-5] Examined data collection (2 data spikes causing 2 reboots); Calculated ETA Absorption; Notes			0.71		79.33					20190705
				[WP4-5] Birddogging, various times, estimated			0.25		79.58					20190705
				~	16:15	~	17:15	[WP4-5] Reviewed W10 log and notated events			0.50		80.08					20190705
				~	17:30	~	18:50	[WP4-5] Notes; Modifed Actions (double-tap with 2 sec between each tap, all Actions that Switch relays) / Modified flawed Action 'SoC<50%' (delay 5 to avoid premature end of discharge if W10 reboots); Notes	WRD AED		0.67		80.74					20190705
				[WP4-5] Birddogging, various times, estimated	WRD		0.08		80.83					20190705
				~	20:15	~	20:30	[WP4-5] Advertising thoughts, verbage			0.13		80.95					20190705
				~	20:35	~	21:40	[WP4-5] Thoughts and notes, "LL & LH range s/b less than trim wattage", verbage for datasheet/brochure concerning capacities, Excel setup			0.54		81.49					20190705
				[WP4-5] Birddogging, various times, estimated			0.54		82.03					20190705
		6	Sa	~	08:30	~	09:40	[WP4-5] In Float, found transitions, notes			0.58		82.62					20190706
				~	10:30	~	12:00	[WP4-5] Killed Load and observed; 2 Hr Equalization started			0.75		83.37					20190706
				~	13:00	~	13:15	[WP4-5] 2 Hr Equalization ended			0.13		83.49					20190706
		7	Su	~	02:40	~	05:20	[WP4-5] End of 4th Series Test (300w); SD Card Copy; Setup for 5th Series Test @ 100w; Began 5th Series Test @ 100w / Aborted 5th Series Test @ 100w after only 5 minutes (need to adjust trim)	AED WRD		1.33		84.83					20190707
				~	07:25	~	09:45	[WP4-5] Setup (2nd try) for 5th Series Test (100w); Began 5th Series Test @ 100w; Thoughts on Actions improvements needed (to align RL5 display in Control Widget with reality)	WRD		1.17		85.99					20190707
				~	12:50	~	13:55	[WP4-5] Adjusted trim; Notes			0.54		86.53					20190707
				~	20:00	~	21:45	[WP4-5] Adjusted trim; Watched transition from Discharge to Bulk; Notes			0.88		87.41					20190707
				~	23:00	~	23:15	[WP4-5] / Checked trim			0.13		87.53					20190707
				~	23:45	~	00:00				0.13		87.66					20190707
		8	Mo	~	05:00		10:18	[WP4-5] In Float; Found transitions; Notes, CONCLUSIONS (not enough trim); End of 5th Series Test (100w); 30 min Equalization; Setup for next test …; Began 6th Series Test @ 100w	AED WRD		2.65		90.31					20190708
				10:18	~	11:50	[WP4-5] Birddogging; Thoughts and notes on improvements to Test Setup …; System is stable, all notes caught up (I'm going to work on other things until later tonight)	WRD		0.77		91.08					20190708
				~	14:25	~	15:10	[WP4-5] Called Keith Jones about scheduling and the possibility of leaving B54 here and installing B1 from RW @ Odessa: / WP4 and B1 to be installed in Odessa tomorrow, meet in Lexington at 1pm (OK to swap RW/Odessa batteries so that I can continue testing with B54, which is the better battery) / RW W100, B1 and DC Netonix to be installed next week at Lexington Water Tower (LWT, currently 29w) / Keith wants me to bring it to Lexington, labor charges will apply, contact Keith when W100 testing with B54 is completed) / Hopefully they'll order WP5 and another battery for RW when tower is completed in about a month			0.37		91.45					20190708
				~	15:10	~	16:40	[WP4-5] Videos and photos of Series Test setup shot and transferred for backup: / WP4, WP5, S6, S7, Genasun_1, Genasun_2, B1, B54, W9, W10, A10, I3O2 (videos), C252_1, C252_2, Liebert A3, BK_1, 6-pack (Heathkit), ENC, BTJ_1	IMG		0.75		92.20					20190708
				[WP4-5] Birddogging, various times, estimated	WRD		0.42		92.62					20190708
		9	Tu	~	03:10	~	04:40	[WP4-5] Adjusted trim (was high in Absorption); Notes …			0.75		93.37					20190709
				[WP4-5] Birddogging, various times, estimated			0.17		93.53					20190709
				~	11:20		12:45	[WP4-5] Initial Conclusions; Load Killed; Series Test setup disassembled; SD Card Copy; End of 6th Series Test (100w) and End of Series Testing			0.71		94.24	Delivery					20190709
				12:45	~	17:25	Loaded Subaru; Travel to Lexington, followed Keith to Odessa South Water Tower (OSWT) / Onsite 14:05-15:25; Helped Keith install W100_3 and B1, Photos, Netonix is currently using 24-28w; Return travel (less 30 mins other errands); 81 miles roundtrip	IMG	$46.98	4.17	$487.70	98.41	Sold	L7	B1			20190709
		10	We	~	04:40	~	06:50	Entries in this workbook for yesterday's delivery; Photos transferred for backup			2.17		100.58					20190710
				~	07:30	~	08:20	[WP4-5] Liebert (A3, used for Series Test) moved back to rear room for Network and N Desk; T2 bypass; A3 connected to batteries; T1 and T2 bypass NOT / Network and N Desk brought down and moved to T1; T450s (R)	A3		0.42		100.99					20190710
				[WP4-5] From/To Keith Jones: "Latest power usage" (screenshot); "Seems to bounce between 25-33" / "Assuming 29 watts is the average the battery will go 24 hours to 50% discharge (a safe discharge for the battery) ... Or 48 hours if you don't mind abusing the battery (100% depth of discharge, totally dead)."; "Thanks Jeff" / "Be sure to set a notification SMS from the Netonix if the battery voltage drops below 13.0 volts as otherwise you may not know the AC power is off until 48 hours after happens." / "Gotcha thanks again"	SMS TW4-5		0.25		101.24					20190710
		26	Fr	~	10:15	~	11:00	[WP4-5] Scans: Parallel Test Schematic; Series Test Schematic; DR System w/2 Trim Loads (see above references, split 1/2 W100_3/4)	SSC		0.37		101.62					20190726
		27	Sa	~	05:00	~	13:50	[WP4-5] Columns for "Other Sources" added to this workbook (primarily because it would simplify W100 sheets); Partially finished updating History sheets; Split 1/2 W100_3/4 …			4.42		106.03					20190727
		28	Su	~	03:30	~	06:10	[WP4-5] ... Updating History sheets to use column "Other Sources"; Split 1/2 W100_3/4 …			1.33		107.37					20190728
		29	Mo	~	13:15	~	15:00				0.88		108.24					20190729
2019	Aug	5	Mo					[WP4-5] 2 Gallons distilled water purchased at WalMart (for batteries that go with WP4/5, split 1/2)	TW4-5		0.08		108.33					20190805
		6	Tu	~	11:10	~	12:00	[WP4-5] Updated WP4A and WP5A to show distilled water, jar and labels (split 1/2)			0.42		108.74					20190806
		7	We	~	06:00	~	07:45	[WP4-5] ... Updating History sheets to use column "Other Sources"; Split 1/2 W100_3/4 …			0.88		109.62					20190807
		8	Th	~	01:15	~	05:00				1.88		111.49					20190808
				~	13:50	~	17:40				1.92		113.41					20190808
		12	Mo	~	11:15	~	12:30				0.63		114.03					20190812
		13	Tu	~	03:55	~	06:00				1.04		115.08					20190813
		17	Sa	~	5:00	~	7:45				1.38		116.45					20190817
		18	Su	~	03:30	~	06:50				1.67		118.12					20190818
		19	Mo	~	03:55	~	06:15				1.17		119.28					20190819
2019	Sep	8	Su	~	05:00	~	09:30				1.88		121.16					20190908
		9	Mo	~	00:35	~	03:00	[WP4-5] ... Completed updating History sheets to use column "Other Sources"; Split 1/2 W100_3/4			1.21		122.37					20190909
2021	Apr	5	Mo	~	14:45	~17:15		Onsite at OSWT for the Backup Power Supply Maintenance Program; See L7 for details	TM21S SMS					L7	B1			20210405

## WP5
WISPers: WP5	A					W100_4 ― 2nd Production Run ― Delta PS 24v/200w, Genasun, Fan, 27TMX, Electrical Work (Outlets)					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$546.59	287.07	Sold	L10	B56	S7	C2
2019	Apr	27	Sa					WP4-6	TW4-5	$3.90	0.17	$3.90	0.17	Orders…	L0				20190427
		28	Su	~	17:30	~	18:15				0.25		0.42					20190428
2019	May	10	Fr					TW4-5	$1.43	0.17	$5.33	0.58					20190510
2019	Jun	8	Sa					Genasun_2 (C2) 5/4/15 cost		$111.57	0.25	$116.90	0.83					C2	20190608
		12	We	~	01:20	~	02:00	WP4-5	EML DKE	$66.20	0.33	$183.09	1.17				S7		20190612
				~	02:00	~	02:30		WP5 BDC	$12.85	0.25	$195.94	1.42					20190612
				WP5	$6.49	0.25	$202.43	1.67	Waiting Parts					20190612
		14	Fr					WP4-5	DKE TW4-5 BDC		0.00		1.67					20190614
		17	Mo	~	04:30	~	05:30		TW4-5		0.50		2.17	Assembly					20190617

		18	Tu	~	00:05	~	00:20	Corrected WP5A (different Genasun than WP4A)			0.25		2.42					20190618
				~	00:20	~	00:50	WP4-5			0.25		2.67					20190618
				~	00:50	~	01:50				0.50		3.17					20190618
				~	01:50	~	02:20				0.25		3.42					20190618
				~	02:40	~	04:40				1.00		4.42					20190618
				~	15:15	~	15:45		IMG		0.25		4.67					20190618
				~	17:00	~	18:45		SSC TW2-3		0.88		5.54					20190618
		19	We	~	07:15	~	08:00				0.37		5.92					20190619
				~	08:00	~	09:00				0.50		6.42					20190619
		20	Th	~	02:55	~	04:30				0.79		7.21					20190620
				~	13:00	~	18:30		EML	$6.55	2.75	$208.97	9.96					20190620
		21	Fr	~	06:20	~	07:35				0.63		10.58					20190621
				~	08:15	~	08:45				0.25		10.83					20190621

		22	Sa	~	04:55	~	05:35	WP4-5			0.33		11.17			B54			20190622
				~	05:35	~	07:35		LBX		1.00		12.17					20190622
				~	07:35	~	09:20		EML	$53.66	0.88	$262.63	13.04					20190622
				~	09:20	~	11:00		LBX		0.83		13.88	Parallel Test					20190622
		23	Su	~	03:30	~	11:00		TW4-5 AED SSC WCX		3.75		17.63					20190623
				~	23:15	~	04:45		AED WCX		2.75		20.38					20190623
		24	Mo	~	12:15	~	13:45				0.75		21.13					20190624
		25	Tu	~	03:50	~	08:35		AED WCX TW4-5		2.38		23.50					20190625
				~	09:55		10:05				0.08		23.58					20190625
				~	21:00	~	23:15		AED WCX		1.13		24.71					20190625
				~	23:15	~	01:15				1.00		25.71					20190625
		26	We	~	01:15	~	04:00		AED WCX TW4-5		1.38		27.08					20190626
		27	Th	~	04:00	~	08:30		AED TW4-5		2.25		29.33					20190627
				10:38		10:42				0.03		29.37					20190627
		28	Fr	~	03:30	~	13:30		AED WCX WRD EML IMG		5.00		34.37					20190628
		29	Sa	~	05:15	~	08:00		WRD TW4-5 SSC		1.38		35.74					20190629
				~	08:00	~	13:00				2.50		38.24	Series Test		B1			20190629
		30	Su	~	01:00	~	12:00		WRD AED WCX		5.50		43.74					20190630
				~	13:15	~	15:45		WRD		1.25		44.99					20190630
2019	Jul	1	Mo	~	04:25	~	13:25		WRD TW4-5 SSC		4.50		49.49					20190701
		2	Tu	~	00:00		11:00				5.00		54.49					20190702
				11:00	~	12:00		WRD		0.50		54.99					20190702
				0.25		55.24					20190702
				~	12:55	~	13:25				0.25		55.49					20190702
		3	We	~	03:50	~	05:15				0.71		56.20					20190703
				~	06:30		09:00		AED WRD		1.25		57.45					20190703
				09:00	~	09:30		WRD		0.25		57.70					20190703
				0.54		58.24					20190703
		4	Th	~	00:45	~	02:45				1.00		59.24					20190704
				~	00:50		06:30				2.83		62.08					20190704
				~	08:45	~	10:30		AED WRD		0.88		62.95					20190704
				~	14:00		14:30				0.25		63.20					20190704
				14:30	~	15:00		WRD		0.25		63.45					20190704
				0.42		63.87					20190704
		5	Fr	~	04:00	~	05:25				0.71		64.58					20190705
				0.25		64.83					20190705
				~	16:15	~	17:15				0.50		65.33					20190705
				~	17:30	~	18:50		WRD AED		0.67		65.99					20190705
				WRD		0.08		66.08					20190705
				~	20:15	~	20:30				0.13		66.20					20190705
				~	20:35	~	21:40				0.54		66.74					20190705
				0.54		67.28					20190705
		6	Sa	~	08:30	~	09:40				0.58		67.87					20190706
				~	10:30	~	12:00				0.75		68.62					20190706
				~	13:00	~	13:15				0.13		68.74					20190706
		7	Su	~	02:40	~	05:20		AED WRD		1.33		70.08					20190707
				~	07:25	~	09:45		WRD		1.17		71.24					20190707
				~	12:50	~	13:55				0.54		71.78					20190707
				~	20:00	~	21:45				0.88		72.66					20190707
				~	23:00	~	23:15				0.13		72.78					20190707
				~	23:45	~	00:00				0.13		72.91					20190707
		8	Mo	~	05:00		10:18		AED WRD		2.65		75.56					20190708
				10:18	~	11:50		WRD		0.77		76.33					20190708
				~	14:25	~	15:10		L10		0.50		76.83					20190708
				~	15:10	~	16:40		IMG		0.75		77.58					20190708
				WRD		0.42		77.99					20190708
		9	Tu	~	03:10	~	04:40				0.75		78.74					20190709
				0.17		78.91					20190709
				~	11:20		12:45				0.71		79.62	Further Tests		B54			20190709
				79.62
				79.62
				~	07:30	~	08:20	WP4-5	A3		0.42		80.03					20190709
		10	We					L10 TW4-5		0.50		80.53					20190710
		11	Th	~	04:45	~	08:35	Cleaned and tested APC 12v UPS I got for free when I was at OSWT; Appears operational, listed; See APC_1 for details of setup for use in W100 testing	A32		3.83		84.37					20190711
				~	18:10	~	20:45	Finished setting up APC 12v UPS; Test setup assembled and running	A32		2.58		86.95					20190711
				~	20:45		02:00	Setup for 7th Test (100w) …; Began Discharge on 7th DR Test (100w)	AED WRD		5.25		92.20					20190711
		12	Fr		02:00	~	03:30	Birddogging DR test	WRD		1.50		93.70					20190712
				~	10:15	~	11:00				0.75		94.45					20190712
				Birddogging, various times, estimated			0.33		94.78					20190712
		13	Sa	~	00:15		03:00	End of 7th DR Test (100w); Setup for 8th Test (50w) …; Began Discharge on 8th DR Test (50w)	AED WRD		2.75		97.53					20190713
				03:00	~	05:00	Birddogging DR test	WRD		2.00		99.53					20190713
				~	13:30	~	14:10				0.67		100.20					20190713
				Birddogging, various times, estimated			0.25		100.45					20190713
				~	15:45	~	17:50	Birddogging DR test			2.08		102.53					20190713
		14	Su	~	05:00		08:00	End of 8th DR Test (50w); Setup for 9th Test (150w) …; Began Discharge on 9th DR Test (150w)	AED WRD		3.00		105.53					20190714
				08:00	~	09:30	Birddogging DR test	WRD		1.50		107.03					20190714
				~	11:15	~	13:45	Birddogging DR test; Photos shot and transferred for backup: APC_1 (A32), WP5, C2, S7, B54, W9, W10, C252_1/2, I3O2_1, A10, BK, 6-pack (Heathkit), BTJ_1 and B0 (under bench)	WRD IMG		2.50		109.53					20190714
				~	15:15	~	15:30	Observations and notes on an episode of severe trim flip/flops	WRD		0.25		109.78					20190714
		15	Mo	~	00:35	~	01:50	Action modified to loosen restraints 149/151 -> 148.8/151.2 LL/LH; Birddogging	AED WRD		1.25		111.03					20190715
				~	20:25	~	20:50	Birddogging DR test	WRD		0.42		111.45					20190715
				~	21:15	~	21:30				0.25		111.70					20190715
		16	Tu	~	05:30	~	07:00				1.50		113.20					20190716
				~	08:15	~	08:25	End of 9th DR Test (150w)			0.17		113.37					20190716
				08:28		08:30	SMS to Keith Jones …	L10		0.25		113.62					20190716
				~	09:15	~	10:30	Further thoughts and TODO (trim, C252_2 calibration, Fluke-BK comparison, observations of Genasun behavior in Float with fully charged battery)	WRD		1.25		114.87					20190716
		17	We	~	02:00	~	06:25	C252_2 Calibration Improved	WCX AED WRD		4.42		119.28					20190717
				~	09:20	~	09:35	Notes on W10 reboot and %Soc-->0	WRD		0.25		119.53					20190717
				~	19:00	~	00:00	Installed cooling fan in APC; IMG, modified APC in W100 Test Setup; Inverter power comparison, before and after fan installation; Set 0.8w trims @ 50w; Worked on logic for Action(s) to insure that if battery_cur_ah changes more than it should that it is reset ...	WRD A32 IMG		5.00		124.53					20190717
		18	Th	~	01:15	~	02:30	Continued to work on logic for Action(s) to insure that if battery_cur_ah changes more than it should that it is reset …			1.25		125.78					20190718
				~	10:30	~	16:15	Modified L+ and L- Actions to Increase Delay 3->4; Action(s) to insure that if battery_cur_ah changes more than it should that it is reset …	AED WRD		5.75		131.53					20190718
		19	Fr	~	01:30	~	03:00	Continued to work on logic for Action(s) to insure that if battery_cur_ah changes more than it should that it is reset; White sheet 20190804 172149 Scan.jpg	SSC TW4-5 WS		1.50		133.03					20190719
				~	05:00	~	05:30	Continued to work on logic for Action(s) to insure that if battery_cur_ah changes more than it should that it is reset (TODO); White sheet 20190804 172742 Scan.jpg			0.50		133.53					20190719
				~	12:00	~	12:30	Played with Charge Efficiency setting (still in Float @ 50w); Improved Action 'AH Watchdog Update2 No Change' (delay 61)	WRD AED		0.50		134.03					20190719
				~	23:45	~	00:00	Couldn't sleep, good thoughts on improvements to Watchdog	TW4-5		0.25		134.28					20190719
		20	Sa	~	00:00	~	05:45	Played with Charge Efficiency setting (still in Float @ 50w); Continued to work on logic for Watchdog Actions; Discovered and corrected NVRAM corruption	WRD TW4-5 W10		5.75		140.03					20190720
		21	Su	~	01:00	~	07:30	Further NVRAM corruption issues; Writing scripts for ini_set and ini_get (to stop using NVRAM for W100 test setup); White sheet 20190804 173043 Scan.jpg	SSC TW4-5 W10 WS		6.50		146.53					20190721
				~	14:30	~	15:30	Writing scripts for ini_set and ini_get (to stop using NVRAM for W100 test setup) …	W10 WRD		1.00		147.53					20190721
				~	16:15	~	19:45	Debugging scripts for ini_set and ini_get (to stop using NVRAM for W100 test setup) …			3.50		151.03					20190721
		22	Mo	~	04:00	~	08:00	Trim system modified for 2kOhm on Main Variac (much easier to adjust at 50w, not as touchy) and 1w on Trim Variac (probably safer level for entire test, LL/LH remains 49.6/50.4); From/To Akash concerning NVRAM Corruption issues and Data Collection "Disk write interval"; Cleared NVRAM as per Akash; FW & OS Updates; Problems with OS Update, To Akash ...	WRD EML W10		4.00		155.03					20190722
		23	Tu	~	01:30	~	05:30	From/To Akash concerning OS 3.3 Update errors; Repeated tries to upgrade to OS 3.3; Waiting response from Akash or I'll go back to OS 3.2 and get on with the DR Test Setup (scripts/actions to replace NVRAM)	W10 EML		4.00		159.03					20190723
				06:22		06:27	From Akash "Hmmm. Can you try and extract it all via your PC and see if that solves it?"			0.08		159.12					20190723
				~	11:50	~	14:55	SD Card on T450s to extract wattmonos3.3.tar, which proved that upgrade to OS 3.3 is probably complete; Discovered that at 07:39 battery_cur_ah->0, this is another Akash fart, and it reinforces the fact that I must have the AH Watchdog system functioning, as I’ve seen this happen many, many times; To Akash concerning this %SoC corruption			3.08		162.20					20190723
				~	16:40	~	17:40	Trimmed up @ 150w for next test to see how deep the APC can go, etc. …	WRD W10		1.00		163.20					20190723
		24	We	~	01:35		02:45	One last attempt to fix scripts and actions to use DR.ini instead of NVRAM, but I couldn't find something that doesn't trigger an Exception when ini_set.cgi is run from Action 'AH Watchdog1 Change'; Actions for Watchdog disabled, and Action 'After Reboot' modified to use NVRAM for RL5	W10 AED		1.17		164.37					20190724
				02:45	~	04:05	Setup for DR Test #10; Began Discharge, DR Test #10, 150w to as Low as APC will Go ...	AED WRD W10		1.33		165.70					20190724
				Birddogging, various times, estimated; Thoughs on using Blockly and creating my own AH system (no Watchdog)	WRD		1.75		167.45					20190724
				~	09:55	~	10:25	APC quit, killed all loads to be able to measure OCV and left for Excelsior Springs			0.50		167.95					20190724
				~	15:30	~	16:50	OCV and actual %SoC evaluated; Charging very slowly with 150w load from either 30% SoC (actual) or 10% SoC (by man'f specs)			1.33		169.28					20190724
		25	Th	~	01:15	~	02:00	Trim analyzed (OK), battery recovery VERY SLOW if at all, looks like it's gaining, but days predicted to full charge			0.75		170.03					20190725
				~	15:45	~	16:30	%SoC-->100, 6 hours ago; Applied estimated correction			0.75		170.78					20190725
				Birddogging, various times, estimated			0.25		171.03					20190725
		26	Fr	~	10:15	~	11:00	WP4-5	SSC		0.37		171.41					20190726
				Birddogging, various times, estimated	WRD		0.33		171.74					20190726
		27	Sa	~	05:00	~	13:50	WP4-5			4.42		176.16					20190727
		28	Su	~	01:30	~	02:30	Estimated and corrected battery_cur_ah for Akash farts (%SoC->0 then %SoC->100)	WRD		1.00		177.16					20190728
				~	03:30	~	06:10	WP4-5			1.33		178.49					20190728
				~	13:00	~	16:30	Concluded DR Test #10 (150w to as Low as APC will Go); Equalization …	WRD		3.50		181.99					20190728
				17:00	~	18:55	… Equalization concluded; Began setup for DR Test #11 (50w to as Low as APC will Go)	WRD AED		1.92		183.91					20190728
				~	22:10	~	22:40	Setup is complete, but I decided to get some sleep before Pre-Launch and Discharge for #11 test	WRD		0.50		184.41					20190728
		29	Mo	~	08:35	~	10:30	Pre-Launch Checklist; Began Discharge, DR Test #11 (50w to as Low as APC will Go)			1.92		186.33					20190729
				~	13:15	~	15:00	WP4-5			0.88		187.20					20190729
				Birddogging, various times, estimated	WRD		0.58		187.78					20190729
				~	19:15	~	19:30	AH Correction			0.25		188.03					20190729
		30	Tu	~	03:40	~	04:30	Discharge observations and TODO			0.83		188.87					20190730
				Birddogging, various times, estimated; Discharge Ended; OCV Measured; Recovery Started			1.83		190.70					20190730
				~	20:00	~	21:30	Observations; Trim errors and CONCLUSIONS on Trim setup; Absorption; TODO			1.50		192.20					20190730
				~	22:00	~	00:00	Float; Started and aborted OCV measurement; Another Absorption; CONCLUSIONS regarding "How to State Fully Charge on Datasheet"; TODO			2.00		194.20					20190730
		31	We	~	00:15	~	01:30	To Akash 'Re: OS 3.3 Update errors' [sic]: "Thank you very much for your insight into whether or not I could use NVRAM in this way (new values every minute)"; ini-set.cgi won't run in Action; Suggestion to add Action choices for ini_set or ini_get of a group of global variables; Offered 3 PROs for 1 MEGA	EML		1.25		195.45					20190731
				~	07:25	~	10:40	Ratio<3%; Concluded DR Test #11 (50w to as Low as APC will Go); Began setup for next test; Pre-Launch Checklist; Began Discharge, DR Test #12 (100w to 10% WSoC)	AED WRD		3.25		198.70					20190731
				Birddogging, various times, estimated; AH Fart corrected; Trim correction; 50% WSoC	WRD		2.00		200.70					20190731
2019	Aug	1	Th	~	04:30	~	06:55	APC quit after I went to bed last night; OCV and ~25% actual SoC; Began recovery; Thoughts on simplified AH Watchdog (TODO)			2.42		203.12					20190801
				Thoughts and research on how to get CC load for testing 27TMX and T-105s as per man'f specifications @ C/100, C/20 and C/10 (estimated) / [see white sheet "CC DR Testing Equipment"]	TW4-5 WS		1.50		204.62					20190801
				Birddogging, various times, estimated	WRD		0.50		205.12					20190801
				~	23:15	~	05:00	Preliminary conclusions on test #12: Reached Float; Ratio calculations; Trim recommendations; Summary of Unified Trim Settings for 50, 100 and 150w Tests w/APC; Notes on Evaluation of “Fully Charged” as per Ratio Rules; TODO; Watching ratio (Genasun Float voltage has shifted) ...			5.75		210.87					20190801
		2	Fr	~	18:05	~	19:15	AH Fart (not corrected); Genasun Float voltage and ratio observations; Final updates to CONCLUSIONS; Concluded DR Test #12 (100w to 10% WSoC, but APC Quit @ 12.8% WSoC); SD Card Copy			1.17		212.03					20190802
				~	20:00		21:15	Battery Capacity Calculations - Revisited'; 'Notes on Evaluation of “Fully Charged” as per Ratio Rules'; 'Summary of Unified Trim Settings for 50, 100 and 150w Tests w/APC'	WRD SSC		1.25		213.28					20190802
				~	21:15	~	21:25	Verified version of cronmin.cgi that is being used on W10 (it's writing Data Collection to SD every minute) and it is identical to what Akash sent me on 7/22	W10		0.17		213.45					20190802
				~	21:25	~	21:40	Screenshots of Energy in Watts Graph added to WRD	WRD SSC		0.25		213.70					20190802
				~	21:50	~	22:20	FW Update; Checked calibration values and NVRAM (OK); TODO	W10		0.50		214.20					20190802
		3	Sa	~	06:10	~	06:55	Observations, Genasun Tcomp & Float Voltage'	WRD SSC		0.75		214.95					20190803
				~	12:05	~	12:25	Reviewed Wattmon_9 Temperature Graphs (it's been logging lab temperature for > 1 year)	W9		0.33		215.28					20190803
		4	Su	~	03:45	~	10:00	Experiments with BK_1 to be used to provide a CC load at 5.100 amps	S2 WRD		6.25		221.53					20190804
				~	17:00	~	00:30	Scans of thoughts and rouch sketch of schematic for using BK_1 for CC; Set up for DR Test #13; Began Discharge, DR Test #13 (5.100 Amps CC to 10.5v as per man’f specs.); Birddogging; Thoughts; TODO (especially "IT’S TIME TO MOVE ON")	S2 WRD AED TW4-5		7.50		229.03					20190804
		5	Mo					Birddogging, various times, estimated	WRD		1.00		230.03					20190805
				WP4-5	TW4-5		0.08		230.12					20190805
		5	Mo		11:10			Response from BK	EML S2		0.08		230.20					20190805
		6	Tu	~	11:10	~	12:00	WP4-5	TW4-5		0.42		230.62					20190806
				~	20:40	~	21:15	Further questions for BK	EML S2		0.58		231.20					20190806
				~	21:15	~	23:30	Concluded DR Test #13 (5.099 Amps CC to 10.5v as per man'f specs.)	WRD		2.25		233.45					20190806
		7	We	~	06:00	~	07:45	WP4-5			0.88		234.33					20190807
				~	08:15	~	14:55	Called Keith, NA; SMSs …; Call from Keith: He's in California setting up wireless for a wine train; He'll be back from CA and FL in 1-2 weeks; B54 and W100_2 won't be installed at Lexington until he is back and there is time to do it; I mentioned that RW tower may be finished in about 2 weeks and he said "I don't care"	SMS B54 WP3 L1 L10		0.25		234.58					20190807
		8	Th	~	01:15	~	05:00	WP4-5			1.88		236.45					20190808
				~	13:50	~	17:40				1.92		238.37					20190808
				17:06			Response from BK	EML S2		0.25		238.62					20190808
		11	Su	~	01:00	~	03:00	Thoughts and TODO on 'When does Genasun reset Tcomp?' and 'When does Genasun do Equalization?'; By my records and calculation there should have been an Equalization yesterday at 20:00, but there was not (examined .csvs); Recorded contact with Keith Jones 8/7; T-105s from Subaru put on Trace under bench (will be used for W100 Testing)	B8 B11		2.00		240.62					20190811
		12	Mo	~	11:15	~	12:30	WP4-5			0.63		241.24					20190812
		13	Tu	~	03:55	~	06:00				1.04		242.28					20190813
		17	Sa	~	5:00	~	7:45				1.38		243.66					20190817
		18	Su	~	03:30	~	06:50				1.67		245.33					20190818
		19	Mo	~	03:55	~	06:15				1.17		246.49					20190819
2019	Sep	5	Th	~	10:00	~	12:30	27 TMX (B54) removed from W100 Test Setup for delivery to RW: BK_1 used to show Genasun 13.2v battery (on UPS); T-105s installed in W100 Test Setup	B54		0.50		246.99			B8,B11			20190905
		8	Su	~	05:00	~	09:30	WP4-5			1.88		248.87					20190908
		9	Mo	~	00:35	~	03:00				1.21		250.08					20190909
				Realizations Concerning Genasun Tcomp and Equalization: "Does it really matter?"	WRD		0.25		250.33	Ordered …					20190909
		26	Th	~	09:15			W100 DR Test Setup used briefly to show Chris Stockton how it works (short discharge)			0.00		250.33					20190926
2019	Dec	9	Fr	~	11:52	~	11:54	Call to Keith …	L10		0.25		250.58					20191209
2020	Feb	5	We	~	13:42	~	13:44	Call to Keith, LMVM ...; Call to Mark, LMVM			0.25		250.83					20200205
		6	Th	~	09:05	~	09:10	Call to Keith …			0.25		251.08					20200206
				10:51		11:05	Call from Keith …			0.25		251.33					20200206
	May	1	Fr					Letter mailed w/payment $220 for Mar and Apr internet …	L10 TW4-5		0.50		251.83					20200501
		4	Mo					SMS from Keith Jones "When would you be able to change the Lexington tower over" …	L10		0.25		252.08					20200504
		5	Tu					Procurement research, Trojan 27TMX and equivalents at Crown (Solar Biz) …	L10 TW4-5		0.25		252.33					20200505
		7	Th		09:06			SMS from Keith "Can you be here today about 11:30 looks like it could be a nice day"; SMSs to Keith "Sorry, no stock on the battery until this afternoon …"	L10		0.25		252.58					20200507
				BFMS: 78 miles roundtrip and about 2.5 hours / Purchased two 27TMX ($333.00)	TW4-5 B56 B57	$188.93	1.25	$451.55	253.83					20200507
				12:59		13:05	Call from Mark while returning from KC (see TW4-5 on back side of BFMS invoice)	TW4-5		0.25		254.08					20200507
				18:25			SMS from Mark: "I can't be at the office until 10:30 in the morning so come to my office at 10:30 please"	SMS		0.13		254.20					20200507
				.xlsm recordkeeping caught up (several hours, I've neglected this system since July 2019)			2.00		256.20					20200507
		8	Fr					(2) 27TMX from BFMS cleaned, labelled and B56 on Trace (45 mins)	B56 B57		0.75		256.95					20200508
				07:15		09:45	.xlsm recordkeeping; Printed and applied missing W100 Power Supply Status sticker; WP5 has been floating on B8/11 since 9/26/19 (now 13.485v Fluke) / Removed and cleaned filter, etc.; Loaded Subaru for delivery to Lexington			2.50		259.45		Subaru	B56			20200508
				10:00		13:45	Travel, onsite at LWT, AB and USB deposits / Overall time includes ~1 hour discussing/addressing other projects (web relays, Eaton power supply, TL maintenance check, other sites maintenance, (3) more W100s ordered) / LWT electrical needs are a direct spinoff from the WISPer project, so will track time and materials on WP5 (30’ today included in time recorded here) / Plans are to install W100/B56 at LWT next week (kept in Subaru for now); Rec'd $690 payment; Round trip mileage	TW4-5	$24.15	2.75	$475.70	262.20	Install …					20200508
		9	Sa	~	01:00	~	04:00	TODO and .xlsm recordkeeping; Photos transferred			3.00		265.20					20200509
				~	14:00	~	15:00	.xlsm recordkeeping to conclude use of W100 Test Setup (W9, W10, C252#2, C252#1, I302#1, A32, A10_1, 20160421-1/4, 20160421-4/4)			1.00		266.20					20200509
		10	Su	~	13:45	~	14:45	T-105s reinstalled in Subaru (used in the W100 Test Setup)	B8 B11 MA2		0.25		266.45					20200510
		19	Tu		10:48		11:18	Call from Mark & Keith: Fr10am LWT install; Confirm w/text; Still go on WebRelays; I told him W100 “parts are on order” (with me!); Eaton UPS not discussed	TW4-5		0.50		266.95					20200519
				16:00		16:30	AE.ods and TODO mostly relating to LWT install			0.50		267.45					20200519
		20	We		04:30		05:15	20200508 Invoice - Lexington Water Tower W100.pdf	DBT TW4-5 EML		1.25		268.70					20200520
				~	06:45	~	07:15	Moved 27TMX to shop and placed on Trace for topping charge (W100 on gray cart)	B56		0.50		269.20		L				20200520
				~	07:15	~	09:45	LWT Electrical: Located stock parts and tools; Procurement (Lowe’s, Home Depot, Thunderbird Electric); Call to Keith (LMVM), SMS	SMS		2.50		271.70					20200520
				~	11:35	~	12:05	LWT Electrical: Westlake Ace Hardware: Purchased boxes, covers, outlets, short nipple and rings; Mileage 1/2 with personal errands; SMSs to Keith and Mark “All go for Fr10am”	TW4-5 SMS	$6.90	0.75	$482.60	272.45					20200520
		22	Fr	~	04:25	~	04:35	27TMX removed from Trace	B56		0.37		272.82					20200522
				~	05:00	~	07:30	LWT Electrical: Swapped my stock for dupes on Ace Hdwe purchase; Changed design to 2x 2-gang boxes with 3 circuits and extra 15A outlet; Partial assembly (1 hr @ $80); Labels for outlets and breakers			2.50		275.32					20200522
				~	09:30	~	10:15	LWT Electrical: SMS to Keith “… I won’t be able to get there until 10:45”; Loaded Subaru; 10:28 SMS to Keith “Sorry, lots of interruptions. 11:15.”	SMS		0.75		276.07		Subaru				20200522
				~	10:45	~	14:15	LWT Electrical: Travel, onsite (3 hrs @ $80), return travel (0.75), mileage; Finished install of electrical, WP5 and B56	TW4-5	$23.58	4.25	$506.18	280.32	Sold	L10	B56	S7	C2	20200522
		23	Sa	~	08:55	~	11:20	LWT Electrical: TODO and .ods; Unloaded Subaru and put away tools (new Subaru wire rack design)			2.42		282.74					20200523
				~	11:20	~	11:30	LWT Electrical: Milwaukee NiCad A on charge	S2		0.17		282.91					20200523
				~	11:30	~	12:30	Trace reinstalled in Subaru (used in the W100 Test Setup)	BC1		1.00		283.91					20200523
		25	Mo	~	13:30	~	13:45	LWT Electrical: Milwaukee NiCads charged (.ods)	S2		0.25		284.16					20200525
		26	Tu	~	03:20	~	03:25				0.08		284.24					20200526
		27	We	~	03:10	~	04:40	LWT Electrical: 20200522 Invoice - Lexington Water Tower Electrical – Materials.ods; 20200522 Invoice - Lexington Water Tower Electrical.doc / Email to Mark and Keith	DBT TW4-5 EML	$55.08	1.50	$561.26	285.74					20200527
		31	Su					Additional cleanup of W100 Test Setup (bulbs boxed, 6-pack removed, large ballast resistor stored under the bench, etc.)	A30		0.50		286.24					20200531
	Jun	1	Mo					LWT Electrical: Extra parts returned to Ace Hdwe (mileage covered by WP6-WP10)	TW4-5	-$14.67	0.50	$546.59	286.74					20200601
	Aug	23	Su	~	06:00	~	06:20	Images ORC Fr5/8 Onsite @ LWT			0.33		287.07					20200823
2021	Apr	16	Fr	~	14:30	~	16:00	Onsite at LWT for the Backup Power Supply Maintenance Program; See L10 for details	DBT TM21S EML					L10	B56			20210416
2022	Mar	7	Mo					Lexington Area Power Outage Yesterday Evening: MMS "screenshot" of LWT Netonix received from Mark; Analysis and conclusions / 20.0w load is much less than ~34w recorded Fr4/16/21; Input Voltage graph shows power outage (~2.2h) and Absorption (~2.5h); WP5 AOK, Float ~13.8v	TM22 SMS IMG SSC					L10				20220307
	Apr	14	Th	~	10:55	~	15:25	Onsite with Keith, Dakota and Cole: W100 mounted on left wall under shelf; Fan checked and filter cleaned; Tightened W100 connections / Battery 12.5⁰C, Genasun ~15⁰C, 14.65vF (Absorption, T-comp is perfect); Netonix load 2.1aE (~31w); Traco input 0.12aE (idle, output not connection, ~1.8w)	T48-2 SMS IMG					L10				20220414
		15	Fr	~	08:35	~	08:36	(5) Netonix screenshots from Keith rec'd 08:40; [2 printed, analyzed and annotated Fr5/13]: Float 13.67vN, Genasun T-comp is perfect for 15⁰C	T48-2 EML IMG					L10				20220415

## WP6
WISPers: WP6	A					W100_5 ― 3rd Production Run ― Delta PS 24v/200w, Genasun, Fan					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$392.14	24.20	Sold	L11	B57	S8	C7
2019	Apr	27	Sa					WP4-6		$3.90	0.17	$3.90	0.17	Parts…	L0				20190427
		28	Su	~	17:30	~	18:15				0.25		0.42					20190428
	May	10	Fr					$1.43	0.17	$5.33	0.58					20190510
	Jun	8	Sa					Decision made not to build (3) W100s now, as I only have (2) Genasuns for W100_3 & W100_4					Waiting Cash		-				20190608
2020	May	8	Fr					[WP6-10] TurboNet order and $1000 advance received for (3) W100s and batteries (WP6-WP8 sales time / 3); Plans are to build (5) units (WP6-WP10)	TW6-10 DBT		0.25		0.83	Procure …					20200508
		19	Tu		10:48		11:18	[WP6-10] Call from Mark & Keith: I told him W100 “parts are on order” (with me!); Time on WP5 (main reason for call)			0.00		0.83					20200519
		20	We		05:15		06:15	[WP6-10] Created History sheets WP7 to WP10 and updated Summary for WP6 to WP10			0.20		1.03					20200520
				[WP6-10] WalMart: 4 gallons distilled water for batteries to be installed with WP6 to WP10	TW6-10	$0.66	0.05	$5.99	1.08					20200520
		22	Fr	~	04:30	~	05:15	[WP6-10] 27TMX: On BK for initial charge (will be used for testing WP6-WP10)	B57		0.15		1.23					20200522
		23	Sa	~	07:00	~	08:45	[WP6-10] 27TMX: .ods recordkeeping for WP6-WP10/B57/S2 (difficulties with hyperlink bug in Calc); Electrolyte levels corrected; Transfered to ENC			0.35		1.58					20200523
				14:41	~	15:00	[WP6-10] Call from Mark: “How soon for another W100? We have an outage at Richmond West (between Richmond and Orrick)” / I said “End of next week (Fr5/29)”; Mark said “… hopefully install w/o Mo 6/1”; TODO	L11 TW6-10		0.06		1.65					20200523
		26	Tu	~	03:30	~	11:50	[WP6-10] Created sheet WP6-10A; Inventory, order list, procurement; AltE store (5 Genasuns); DigiKey	TW6-10 DKE	$178.10	1.27	$184.09	2.91					20200526
		27	We	~	02:40	~	03:10	[WP6-10] Procurement: Updated labor on WP6-10A; Rec’d tracking numbers AltE and DigiKey; Internet search for “Top fixing brackets” (will go to Ace Hardware)	EML DKE		0.10		3.01					20200527
				~	16:50	~	18:30	[WP6-10] Created History sheets C7-C11 (Genasun_6 to Genasun_10); Simplified formulas for “Hours” (entire spreadsheet)	Controllers		0.33		3.35					20200527
		28	Th	~	10:40	~	11:25	[WP6-10] Created History sheets S8-S12 (DE_6 to DE_10)	Supplies		0.15		3.50					20200528
2020	Jun	1	Mo					[WP6-10] Scott’s Bargain Barn and Ace Hardware (mileage and time 1/2 with personal errands)	TW6-10	$7.40	0.10	$191.49	3.60					20200601
		2	Tu	~	07:30	~	12:40	[WP6-10] Procurement: Accounting and .ods updates SBB/Ace (Mo6/1), DigiKey (rec’d Fr5/29 and Mo6/1); Restructered WP6-10A to group all Labels together	TW6-10 DKE		0.85		4.45					20200602
		3	We	~	04:20	~	05:05	[WP6-10] Procurement: Accounting and .ods updates AltE rec’d Tu6/2	TW6-10		0.15		4.60	Assembly…	L0				20200603
				~	14:46			Missed call and VM from Mark Webb “Call me”			0.00		4.60					20200603
		4	Th	~	05:05	~	06:40	[WP6-10] Labels printed			0.32		4.91					20200604
				~	06:40	~	06:55	[WP6-10] Power Supply: Inventory Labels applied			0.05		4.96					20200604
				~	08:20	~	08:55	[WP6-10] Power Supply: Power Cords …			0.12		5.08					20200604
				~	09:00	~	10:05	Call to Mark, LMVM; Call from Mark: Discussed scheduling on W100 man’f (Monday soonest) / They need electrical work from me for a “new tower” in about 2-3 weeks (he has a picture, KCPL will trench, we need a meter base, etc.); Mark will be gone to FL w/o Mo6/15 / Scheduled Tu6/9 10am installation of WP6 and battery at Richmond West Water Tower (RWWT); Updates to .ods and TODO	L11 L15		1.08		6.16					20200604
				~	19:15	~	19:45	Created Summary entry and History sheet for L11 (RWWT)	L11		0.50		6.66					20200604
		5	Fr	~	07:25	~	09:00	[WP6-10] Power Supply: Power Cords; Removed covers & marked with template; .ods	TW6-10		0.32		6.98				S8		20200605
				~	09:50	~	11:30	[WP6-10] Genasun: Genasun_# & Inventory Label; Remove cover; FLA/SLA jumpers; Mount on Power Supply; .ods			0.33		7.31					C7	20200605
		6	Sa	~	03:00	~	03:55	[WP6-10] Investigations, LibreOffice Calc hyperlinks, Help; Photos of assembly line; Label for Dad’s stock (W100 Genasun 6-32.lbx) [Phone dropped in MO River Su6/7]	IMG LBX		0.18		7.50					20200606
				~	03:55	~	05:10	[WP6-10] Fan: Remove fan filter; Mount Fan over Genasun …			0.25		7.75					20200606
				~	05:10	~	05:30	[WP6-10] Photos [Phone dropped in MO River Su6/7]	IMG		0.07		7.81					20200606
				~	05:30	~	08:00	[WP6-10] Fan: … Mount Fan over Genasun; Replace Power Supply cover; Replace fan filter; Bend LED out; Cut leads 5.5" beyond fan, 5.25" shrink, strip and tin fan leads (pencil iron)			0.50		8.31					20200606
		7	Su	~	03:05	~	04:45	[WP6-10] Supply: Cut; Strip 22 guage so end can be doubled back; Tin (pencil iron); Wire Genasun to Power Supply (7 loops)			0.33		8.65					20200607
				~	04:45	~	05:45	[WP6-10] Harness: Modified plan to put inline splice 3” from Genasun not 12”; Planned extra negative black to dedicate to DR Test Setup; TODO	TW6-10		0.20		8.85					20200607
		8	Mo					[WP6-10] On Fr6/5 I started thinking about ordering (4) 27TMX (enough to fulfill orders for WP7-WP10, but I only have orders from TurboNet for WP6-WP8) / Checked AB balance and at that time thought I could swing for all (4); Tried to call Mark but NA, SMS, missed call, SMS; Yesterday I dropped my phone in the river / I’m looking at $250 to $850 for a replacement phone; So the decision is to order only enough batteries to fufill orders I have (2) / Time for Fr6/5, emails and Facebook messages to/from Mark and Keith	EML TW6-10		0.20		9.05					20200608
				~	10:50	~	12:15	[WP6-10] Drive to Richmond to meet Mark: Rec’d $265 check for WP5 LWT Electrical; W100 order extended to all five WP6-WP10 (will order four 27TMX); Mileage	L14-15	$2.07	0.28	$193.56	9.33					20200608
				~	12:35	~	13:50	[WP6-10] Updates to SPF, TODO and .ods; Purchased Viber Out Credit / Called John at BFMS and ordered (4) 27TMX ($157.25x4=$629); Email from John, can pick up on or after Wednesday; Email to Mark and Keith	TW6-10 EML	$0.40	0.25	$193.96	9.58					20200608
		9	Tu	~	05:30	~	06:30	[WP6-10] Harness redesign (see white sheet schematic); Harness items reordered on WP6-10A	TW6-10 WS		0.20		9.78					20200609
				~	06:30	~	07:35	[WP6-10] Harness: / Positive fuse butt splice (slow progress, I’m not feeling well)			0.22		10.00					20200609
				~	09:30	~	10:25				0.18		10.18					20200609
				~	23:10	~	00:15	[WP6-10] Design thoughts for harness in TODO: Go ahead with build of (5) as designed this morning, but do not make an extra negative black cable / Later I’ll build a harness set using #12			0.22		10.40					20200609
		10	We	~	00:15	~	03:00	[WP6-10] Harness: Inline splices, torch, 2x (Red/Blk)			0.55		10.95					20200610
				~	03:00	~	05:00	[WP6-10] Harness redesigned again (see white sheet schematic and scan in Setup Notes & TODO ... 20200610 WISPer Harness Redesign, WP11 Onward, Scan.jpg) / Built Red/Blk harness set with new design, no fuse and no stickers (for testing, and if it works, could dedicate to DR test setup or sell by adding fuse) / [Note added Sa9/3/22: There's never going to be a W100_10, the W100 Product Line was discontinued soon after all of them were installed / BUT there IS going to be a WP11 in the new W150 Product Line (W150_1)]	TW6-10 WS		0.40		11.35					20200610
				~	05:00	~	06:10	[WP6-10] Harness: Ring connectors, 2x (Battery Red/Blk); Strip/tin, 2x (Load Red/Blk); Strip/tin/bend into S for zip tie to PS, 2x (Genasun Red/Blk); Labels, 4x (Battery/Load/Red/Blk) / Install fuse and silver tape spare fuse [3 positive sets completed …]			0.23		11.58					20200610
				[WP6-10] BFMS: Purchased (4) 27TMX (slated for WP7-WP10) $629; Round trip time ~2.5 Hrs; Mileage / I called Mark from Murphy’s on the way and told him that I could deliver any or all (5) units Th6/11 / [but not true as of Th6/11 10:45 as I’m still working on the batteries and assembly of W100s]	TW6-10	$188.93	0.00	$382.88	11.58			B57			20200610
		11	Th	~	05:10	~	05:50	[WP6-10] TODO and .ods related to purchases of batteries (5/7 and yesterday 6/10)			0.13		11.71					20200611
				~	08:40	~	08:50	Electrolyte level checked			0.17		11.88			B57			20200611
				~	08:50	~	10:45	[WP6-10] Battery costs and labor to prep on WP6-10A			0.38		12.26					20200611
				0.00		12.26
		12	Fr	~	02:00	~	03:20	[WP6-10] Corrected Battery labor on WP6-10A			0.27		12.53					20200612
				~	03:20	~	04:10	[WP6-10] Harness: … all sets completed as per We6/10, but no stickers on one negative set (for testing) / Improvements to WP6-10A; Installed wire nuts on Load ends			0.17		12.70					20200612
				~	04:45	~	06:40				0.38		13.08					20200612
				~	06:40	~	08:50	[WP6-10] W100 Mount: Brackets installed and mounting screws packaged as per WP6-10A (also improved) / Label printed for Metric M4 M3 screws bin			0.43		13.51					20200612
				~	08:50	~	09:40	[WP6-10] Misc: As per WP6-10A but also improved WP6-10A and removed the ENC from B57 for the quick tests / Quick tests at 72°F Absorptions are +0.06 to +0.11 VDC above specifications for 70°F (nominal)	B57		0.17		13.68					20200612
				~	09:55	~	12:45				0.57		14.25					20200612
				~	12:45	~	13:25	[WP6-10] Called (Viber Out) Keith (NA, LMVM, NA) and Mark (LMVM, then we talked) to confirm delivery date/times, etc.; They tried to contact me that we cannot do any installs this week due to problems they had [later rec’d voice mail from Th6/11 “… give me a call when you get a chance”; Mark is going to FL as planned (returns Fr6/19) / Send invoice for (3) installs next week and Mark will write check and leave it with Keith before leaving; Keep trying to contact Keith (in a few hours, say 15:00 today); TODO			0.13		14.38					20200612
				~	13:25	~	15:40	[WP6-8] 20200612 Invoice - RWWT, RHST and 'Skeeter' WP6-WP8 and batteries B57-B59; Call to Mark to confirm reception via email (LMVM, then later we talked) / Updates to .ods for “Sold” [reversed Sa6/13] / Mark is “still in the dark” as to cost (I told them they are $680 with battery installed) but he was printing my check and rushing out the door to go to FL	DBT TW6-10 EML		0.75		15.13					20200612
		13	Sa	~	03:30	~	03:55	[WP6-8] Corrected .ods Status for WP6-WP8, B57-B59, S8-S10 and C7-C9 (not “Sold” until I have the check in hand, and we are still finishing Assembly DR and Burn-In Tests)			0.14		15.27					20200613
				~	03:55	~	05:45	[WP6-10] DR Test Setup Prepared: Cleaned; Organized; B58 removed from BK; B0 charged and placed on Heathkit / W9 SD Card Copy and boxed; W10 SD Card Copy and initial test OK / DR Test Setup is ready for quick DR tests (back to Assembly…)	B0		0.37		15.64					20200613
				~	06:05	~	09:10		S1		0.62		16.25					20200613
				~	13:50	~	17:15		W10		0.68		16.94					20200613
				~	17:15	~	22:15	[WP6-10] Misc: 1 Hr DR tests, zip ties on harness and burn-in started as per WP6-10A (all five units individually); TODO and .ods updates; Examined W10 graphs and logs / See B57 for the only anomaly observed (unusually long absorption >4.2 Hrs); This long Absorption was probably also on WP7-WP9 (B58-B60) although not observed; I think it is normal (as they have programmed the firmware) due to loss of “Solar” soon after start of Absorption period so on the next “Solar day” the Absorption time is cumulative			1.00		17.94			B57			20200613
		14	Su	~	06:10		09:15				0.62		18.55					20200614
				~	09:15		10:45	[WP6-10] TODO and thoughts concerning further testing, delivery, Installation and Owner’s Manual, The Future			0.30		18.85					20200614
		15	Mo	~	02:00	~	03:10	[WP6-10] Examined W10 Actions and AED: My documentation on the systems is poor, not up to date and difficult to decipher / TODO for W10 and further testing (priority moved down until after I get an Owner’s Manual); Shut down W10 and updated Status on associated equipment	AED		0.23		19.09					20200615
				~	03:10		03:55	[WP6-10] Battery: Check/correct/record electrolyte levels and status B57-B61			0.15		19.24			B57			20200615
				~	03:55	~	04:30	[WP6-10] WP6-10A improvements (column widths); Reviewed WP6-10A for any final changes to comments			0.12		19.35					20200615
				~	04:30	~	06:00	[WP6-10] Misc: Retighten screws on Genasun and PS (WP6-WP9, WP10 is still on the DR Test Setup); Ready for Delivery; Put away tools and extra stock; Clean bench and sweep / WP6-10A completed ($375.64 parts, S&H and tax; 13.68 Hrs per W100); Status and location changes			0.30		19.65	Float	L				20200615
				0.00		19.65
				~	13:40	~	15:45	[WP6-10] WP6-10A improvements (count of Sub Assemblies and Parts); Began draft W100 Installation and Owner's Manual 1.0.odt	WRD		0.42		20.07					20200615
				~	15:45	~	16:10	[WP6-8] Called Keith (Viber Out): He sent FaceBook messages this morning that I hadn’t seen yet, at 10:34 “Do you want to do that stuff tomorrow starting about 10:30” and “Don’t call me Dakota has been in a wreck and I am on phone with hospital”; Scheduled delivery of WP6-WP8 (B57-B59) starting tomorrow morning Tu6/15 10:30 at RWWT / TODO and .ods updates for L11-L13	FaceBook Viber L11 L12 L13		0.14		20.21					20200615
				~	16:55	~	17:35				0.22		20.43					20200615
				~	17:35	~	18:00	[WP6-10] Continued draft of W100 Installation and Owner's Manual 1.0.odt	WRD		0.08		20.51					20200615
		16	Tu	~	02:05	~	07:10				1.02		21.53					20200616
				~	08:45	~	09:15	[WP6-8] Loaded Subaru for delivery of WP6-WP8 and B57-B59	TW6-10		0.17		21.70	Install…	Subaru	B57			20200616
				~	09:30	~	13:40	[WP6-8] Travel and on (3) sites RWWT, RHST and ST; Mileage; Rec’d $1450 TurboNet Check; Printout of Manual draft given to Keith; Installed w/o loads (Keith will return to install and configure DC Netonix); Deposit at USB; Unloaded Subaru and put away parts and tools		$11.92	1.39	$394.80	23.09	Sold	L11	B57	S8	C7	20200616
				~	14:00	~	14:10	[WP6-10] Emails from/to Keith Jones concerning MicroCom CRS112-8P-4S-IN / Keith mentioned when onsite at ST that he was considering using these instead of DC Netonix, as they are less expensive / I promised to take a look at the specs. and get back to him (I should examine closely, paying attention to power requirements); TODO	EML T48P		0.03		23.12					20200616
		17	We	~	02:40	~	05:25	[WP6-8] TODO and .ods updates for deliveries to L11-L13 yesterday	TW6-10		0.92		24.04					20200617
				~	11:45	~	12:15	[WP6-10] Returned expensive and unneeded corner braces to Westlake Ace Hardware (I have stock, I’ll find another source); Mileage 1/2 with personal		-$2.66	0.17	$392.14	24.20					20200617
				0.00		24.20
2021	Apr	16	Fr	~	12:00	~	14:00	Onsite at RWWT for the Backup Power Supply Maintenance Program; See L11 for details	DBT TM21S EML					L11	B57			20210416
	Dec	27	Mo	~	07:55			Logged into Netonix: Load ~38w; Float ~13.5v (13.38v Netonix adjusted up 0.8% as per onsite error observed 4/16/21)	TM21F SSC					L11				20211227

## WP7
WISPers: WP7	A					W100_6 ― 3rd Production Run ― Delta PS 24v/200w, Genasun, Fan					Batteries	Power Supply	Genasun	As

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$366.35	26.79	Sold	L3	B9-10	S9	C8

				0.00

2020	May	8	Fr					WP6-10	TW6-10 DBT		0.25		0.25	Procure …					20200508
		19	Tu		10:48		11:18				0.00		0.25					20200519
		20	We		05:15		06:15				0.20		0.45					20200520
				TW6-10	$0.66	0.05	$0.66	0.50					20200520
		22	Fr	~	04:30	~	05:15		B57		0.15		0.65					20200522
		23	Sa	~	07:00	~	08:45				0.35		1.00					20200523
				14:41	~	15:00		L11		0.06		1.06					20200523
		26	Tu	~	03:30	~	11:50		TW6-10 DKE	$178.10	1.27	$178.76	2.33					20200526
		27	We	~	02:40	~	03:10		EML DKE		0.10		2.43					20200527
				~	16:50	~	18:30		Controllers		0.33		2.76					20200527
		28	Th	~	10:40	~	11:25		Supplies		0.15		2.91					20200528
	Jun	1	Mo					TW6-10	$7.40	0.10	$186.16	3.01					20200601
		2	Tu	~	07:30	~	12:40		TW6-10 DKE		0.85		3.86					20200602
		3	We	~	04:20	~	05:05		TW6-10		0.15		4.01	Assembly…	L0				20200603
				0.00		4.01
		4	Th	~	05:05	~	06:40	WP6-10			0.32		4.33					20200604
				~	06:40	~	06:55				0.05		4.38					20200604
				~	08:20	~	08:55				0.12		4.50					20200604
				0.00		4.50
				~	19:45	~	21:30	Created Summary entry and History sheet for L12 (RHST); Improved Summary sheet Locations to show WISPer and Batteries	L12		1.75		6.25					20200604
		5	Fr	~	07:25	~	09:00	WP6-10			0.32		6.56				S9		20200605
				~	09:50	~	11:30				0.33		6.90					C8	20200605
		6	Sa	~	03:00	~	03:55		IMG LBX		0.18		7.08					20200606
				~	03:55	~	05:10				0.25		7.33					20200606
				~	05:10	~	05:30		IMG		0.07		7.40					20200606
				~	05:30	~	08:00				0.50		7.90					20200606
		7	Su	~	03:05	~	04:45				0.33		8.23					20200607
				~	04:45	~	05:45				0.20		8.43					20200607
		8	Mo					EML TW6-10		0.20		8.63					20200608
				~	10:50	~	12:15		L14-15	$2.07	0.28	$188.23	8.91					20200608
				~	12:35	~	13:50		TW6-10 EML	$0.40	0.25	$188.63	9.16					20200608
		9	Tu	~	05:30	~	06:30		TW6-10		0.20		9.36					20200609
				~	06:30	~	07:35				0.22		9.58					20200609
				~	09:30	~	10:25				0.18		9.76					20200609
				~	23:10	~	00:15				0.22		9.98					20200609
		10	We	~	00:15	~	03:00				0.55		10.53					20200610
				~	03:00	~	05:00		TW6-10		0.40		10.93					20200610
				~	05:00	~	06:10				0.23		11.16					20200610
				TW6-10	$168.46	0.63	$357.09	11.79			B58			20200610
		11	Th	~	05:10	~	05:50				0.13		11.92					20200611
				~	05:50	~	08:40	[WP7-10] B58-B61 Summary and created History sheets; Moved batteries to shop; Cleaned; Stickers applied; WP6-10A updated to show Battery Inventory stickers / Electrolyte levels checked; OCV measured and recorded			0.71		12.63					20200611
				~	08:50	~	10:45	WP6-10			0.38		13.01					20200611
				~	10:45	~	12:35	Started B58 Initial Charge Charge on BK (custom 6’+ #10 cables made up with ring connectors)	S2		1.83		14.85			B58			20200611
		12	Fr	~	02:00	~	03:20	WP6-10			0.27		15.11					20200612
				~	03:20	~	04:10				0.17		15.28					20200612
				~	04:45	~	06:40				0.38		15.66					20200612
				~	06:40	~	08:50				0.43		16.10					20200612
				~	08:50	~	09:40		B57		0.17		16.26					20200612
				~	09:55	~	12:45				0.57		16.83					20200612
				~	12:45	~	13:25				0.13		16.96					20200612
				~	13:25	~	15:40	WP6-8	DBT TW6-10 EML		0.75		17.71					20200612
		13	Sa	~	03:30	~	03:55				0.14		17.85					20200613
				~	03:55	~	05:45	WP6-10	B0		0.37		18.22			B58			20200613
				~	06:05	~	09:10		S1		0.62		18.84					20200613
				~	13:50	~	17:15		W10		0.68		19.52					20200613
				~	17:15	~	22:15				1.00		20.52			B58			20200613
		14	Su	~	06:10		09:15				0.62		21.14					20200614
				~	09:15		10:45				0.30		21.44					20200614
		15	Mo	~	02:00	~	03:10		AED		0.23		21.67					20200615
				~	03:10		03:55				0.15		21.82			B58			20200615
				~	03:55	~	04:30				0.12		21.94					20200615
				~	04:30	~	06:00				0.30		22.24	Float	L				20200615
				0.00		22.24
				~	13:40	~	15:45		WRD		0.42		22.65					20200615
				~	15:45	~	16:10	WP6-8	FaceBook Viber L11 L12 L13		0.14		22.79					20200615
				~	16:55	~	17:35				0.22		23.01					20200615
				~	17:35	~	18:00	WP6-10	WRD		0.08		23.10					20200615
		16	Tu	~	02:05	~	07:10				1.02		24.11					20200616
				~	08:45	~	09:15	WP6-8	TW6-10		0.17		24.28	Install…	Subaru	B58			20200616
				~	09:30	~	13:40			$11.92	1.39	$369.01	25.67	Sold	L12	B58	S9	C8	20200616
				~	14:00	~	14:10	WP6-10	EML T48P		0.03		25.70					20200616
		17	We	~	02:40	~	05:25	WP6-8	TW6-10		0.92		26.62					20200617
				~	11:45	~	12:15	WP6-10		-$2.66	0.17	$366.35	26.79					20200617
				0.00		26.79
2021	Mar	16	Tu	~	13:00	~	13:45	Onsite at RHST for the Backup Power Supply Maintenance Program; See L12 for details	DBT TM21S SMS EML					L12	B58			20210316
	Sep	22	We	~	14:45	~	15:15	Onsite at RHST for Fall 2021 Maintenance; Battery removed & W100 AC disconnected (there has been no Netonix load since 6/16/20, will take battery to shop for maintenance)	TM21F IMG					-			20210922
	Dec	16	Th	~	16:25	~	16:45	Onsite at RHST: Met Mark in parking lot and 27TMX to Subaru ...; Finished pulling W100 from RHST; B58 and WP7 to be installed at RCWT	TM21F SMS					Subaru				20211216
				~	17:20	~	19:15	Onsite at RCWT: Installed (see L3 for details)					L3	B58	S9	C8	20211216
2022	Jun	28	Tu	~	17:20	~	19:20	Onsite at RCWT to swap batteries: B58 27TMX (high on top of electrical box) ~26⁰C (~79⁰F); Ambient ~27⁰C (81⁰F); W100_6 fan is running / 14.00vM (13.93vF equivalent, Float V is too high for current battery T, compensation has not reset lately) / W100_6 filter/fan cleaned (compressor), screws tightened; W100 AC connected, initial charge >11aE (Bulk) / ~19:00 ambient & T-105s ~29⁰C (~84⁰F), ~14.31vM (~14.24vF equivalent, good Absorption V for current battery T); Photos	TM22 IMG					L3	B9-10			20220628

## WP8
WISPers: WP8	A					W100_7 ― 3rd Production Run ― Delta PS 24v/200w, Genasun, Fan					Batteries	Power Supply	Genasun	As

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$366.35	25.87	Sold	L13	B59	S10	C9

				0.00

2020	May	8	Fr					WP6-10	TW6-10 DBT		0.25		0.25	Procure …					20200508
		19	Tu		10:48		11:18				0.00		0.25					20200519
		20	We		05:15		06:15				0.20		0.45					20200520
				TW6-10	$0.66	0.05	$0.66	0.50					20200520
		22	Fr	~	04:30	~	05:15		B57		0.15		0.65					20200522
		23	Sa	~	07:00	~	08:45				0.35		1.00					20200523
				14:41	~	15:00		L11		0.06		1.06					20200523
		26	Tu	~	03:30	~	11:50		TW6-10 DKE	$178.10	1.27	$178.76	2.33					20200526
		27	We	~	02:40	~	03:10		EML DKE		0.10		2.43					20200527
				~	16:50	~	18:30		Controllers		0.33		2.76					20200527
		28	Th	~	10:40	~	11:25		Supplies		0.15		2.91					20200528
	Jun	1	Mo					TW6-10	$7.40	0.10	$186.16	3.01					20200601
		2	Tu	~	07:30	~	12:40		TW6-10 DKE		0.85		3.86					20200602
		3	We	~	04:20	~	05:05		TW6-10		0.15		4.01	Assembly…	L0				20200603
				0.00		4.01
		4	Th	~	05:05	~	06:40	WP6-10			0.32		4.33					20200604
				~	06:40	~	06:55				0.05		4.38					20200604
				~	08:20	~	08:55				0.12		4.50					20200604
				0.00		4.50
				0.00		4.50
		5	Fr	~	07:25	~	09:00	WP6-10			0.32		4.81				S10		20200605
				~	09:50	~	11:30				0.33		5.15					C9	20200605
		6	Sa	~	03:00	~	03:55		IMG LBX		0.18		5.33					20200606
				~	03:55	~	05:10				0.25		5.58					20200606
				~	05:10	~	05:30		IMG		0.07		5.65					20200606
				~	05:30	~	08:00				0.50		6.15					20200606
		7	Su	~	03:05	~	04:45				0.33		6.48					20200607
				~	04:45	~	05:45				0.20		6.68					20200607
		8	Mo					EML		0.20		6.88					20200608
				~	10:50	~	12:15		L14-15	$2.07	0.28	$188.23	7.16					20200608
				~	12:35	~	13:50		TW6-10 EML	$0.40	0.25	$188.63	7.41					20200608
		9	Tu	~	05:30	~	06:30		TW6-10		0.20		7.61					20200609
				~	06:30	~	07:35				0.22		7.83					20200609
				~	09:30	~	10:25				0.18		8.01					20200609
				~	23:10	~	00:15				0.22		8.23					20200609
		10	We	~	00:15	~	03:00				0.55		8.78					20200610
				~	03:00	~	05:00		TW6-10		0.40		9.18					20200610
				~	05:00	~	06:10				0.23		9.41					20200610
				TW6-10	$168.46	0.63	$357.09	10.04			B59			20200610
		11	Th	~	05:10	~	05:50				0.13		10.17					20200611
				~	05:50	~	08:40	WP7-10			0.71		10.88					20200611
				~	08:50	~	10:45	WP6-10			0.38		11.26					20200611
				0.00		11.26
		12	Fr	~	02:00	~	03:20				0.27		11.53					20200612
				~	03:20	~	04:10				0.17		11.70					20200612
				~	04:45	~	06:40				0.38		12.08					20200612
				~	06:40	~	08:50				0.43		12.51					20200612
				~	08:50	~	09:40		B57		0.17		12.68					20200612
				~	09:55	~	12:45				0.57		13.25					20200612
				~	12:45	~	13:25				0.13		13.38					20200612
				~	13:25	~	15:40	WP6-8	DBT TW6-10 EML		0.75		14.13					20200612
		13	Sa	~	03:30	~	03:55				0.14		14.27					20200613
				~	03:55	~	05:45	WP6-10	B0		0.37		14.64					20200613
				~	06:05	~	09:10		S1		0.62		15.25					20200613
				~	13:50	~	17:15		W10		0.68		15.94					20200613
				~	17:15	~	22:15				1.00		16.94			B59			20200613
		14	Su	~	06:10		09:15				0.62		17.55					20200614
				~	09:15		10:45				0.30		17.85					20200614
		15	Mo	~	02:00	~	03:10		AED		0.23		18.09					20200615
				~	03:10		03:55				0.15		18.24			B59			20200615
				~	03:55	~	04:30				0.12		18.35					20200615
				~	04:30	~	06:00				0.30		18.65	Float	L				20200615
				~	06:00	~	07:00	Created and updated History sheet for ‘Skeeter’	L13		1.00		19.65					20200615
				~	13:40	~	15:45	WP6-10	WRD		2.08		21.74					20200615
				~	15:45	~	16:10	WP6-8	FaceBook Viber L11 L12 L13		0.14		21.87					20200615
				~	16:55	~	17:35				0.22		22.10					20200615
				~	17:35	~	18:00	WP6-10	WRD		0.08		22.18					20200615
		16	Tu	~	02:05	~	07:10				1.02		23.20					20200616
				~	08:45	~	09:15	WP6-8	TW6-10		0.17		23.36	Install…	Subaru	B59			20200616
				~	09:30	~	13:40			$11.92	1.39	$369.01	24.75	Sold	L13	B59	S10	C9	20200616
				~	14:00	~	14:10	WP6-10	EML T48P		0.03		24.79					20200616
		17	We	~	02:40	~	05:25	WP6-8	TW6-10		0.92		25.70					20200617
				~	11:45	~	12:15	WP6-10		-$2.66	0.17	$366.35	25.87					20200617
				0.00		25.87

## WP9
WISPers: WP9	A					W100_8 ― 3rd Production Run ― Delta PS 24v/200w, Genasun, Fan					Batteries	Power Supply	Genasun	As

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$395.54	36.31	Sold	L14	B60	S11	C10

				0.00

2020	May	8	Fr					WP6-10	TW6-10 DBT				0.00	Procure …					20200508
		19	Tu		10:48		11:18				0.00		0.00					20200519
		20	We		05:15		06:15				0.20		0.20					20200520
				TW6-10	$0.66	0.05	$0.66	0.25					20200520
		22	Fr	~	04:30	~	05:15		B57		0.15		0.40					20200522
		23	Sa	~	07:00	~	08:45				0.35		0.75					20200523
				14:41	~	15:00		L11		0.06		0.81					20200523
		26	Tu	~	03:30	~	11:50		TW6-10 DKE	$178.10	1.27	$178.76	2.08					20200526
		27	We	~	02:40	~	03:10		EML DKE		0.10		2.18					20200527
				~	16:50	~	18:30		Controllers		0.33		2.51					20200527
		28	Th	~	10:40	~	11:25		Supplies		0.15		2.66					20200528
	Jun	1	Mo					TW6-10	$7.40	0.10	$186.16	2.76					20200601
		2	Tu	~	07:30	~	12:40		TW6-10 DKE		0.85		3.61					20200602
		3	We	~	04:20	~	05:05		TW6-10		0.15		3.76	Assembly…	L0				20200603
				0.00		3.76
		4	Th	~	05:05	~	06:40	WP6-10			0.32		4.08					20200604
				~	06:40	~	06:55				0.05		4.13					20200604
				~	08:20	~	08:55				0.12		4.25					20200604
				0.00		4.25
				0.00		4.25
		5	Fr	~	07:25	~	09:00	WP6-10			0.32		4.56				S11		20200605
				~	09:50	~	11:30				0.33		4.90					C10	20200605
		6	Sa	~	03:00	~	03:55		IMG LBX		0.18		5.08					20200606
				~	03:55	~	05:10				0.25		5.33					20200606
				~	05:10	~	05:30		IMG		0.07		5.40					20200606
				~	05:30	~	08:00				0.50		5.90					20200606
		7	Su	~	03:05	~	04:45				0.33		6.23					20200607
				~	04:45	~	05:45				0.20		6.43					20200607
		8	Mo					EML		0.20		6.63					20200608
				~	10:50	~	12:15		L14-15	$2.07	0.28	$188.23	6.91					20200608
				~	12:35	~	13:50		TW6-10 EML	$0.40	0.25	$188.63	7.16					20200608
		9	Tu	~	05:30	~	06:30		TW6-10		0.20		7.36					20200609
				~	06:30	~	07:35				0.22		7.58					20200609
				~	09:30	~	10:25				0.18		7.76					20200609
				~	23:10	~	00:15				0.22		7.98					20200609
		10	We	~	00:15	~	03:00				0.55		8.53					20200610
				~	03:00	~	05:00		TW6-10		0.40		8.93					20200610
				~	05:00	~	06:10				0.23		9.16					20200610
				TW6-10	$168.46	0.63	$357.09	9.79			B60			20200610
		11	Th	~	05:10	~	05:50				0.13		9.92					20200611
				~	05:50	~	08:40	WP7-10			0.71		10.63					20200611
				~	08:50	~	10:45	WP6-10			0.38		11.01					20200611
				0.00		11.01
		12	Fr	~	02:00	~	03:20				0.27		11.28					20200612
				~	03:20	~	04:10				0.17		11.45					20200612
				~	04:45	~	06:40				0.38		11.83					20200612
				~	06:40	~	08:50				0.43		12.26					20200612
				~	08:50	~	09:40		B57		0.17		12.43					20200612
				~	09:55	~	12:45				0.57		13.00					20200612
				~	12:45	~	13:25				0.13		13.13					20200612
				0.00		13.13
				0.00		13.13
				~	03:55	~	05:45	WP6-10	B0		0.37		13.50					20200612
				~	06:05	~	09:10		S1		0.62		14.11					20200612
				~	13:50	~	17:15		W10		0.68		14.80					20200612
				~	17:15	~	22:15				1.00		15.80			B60			20200612
		14	Su	~	06:10		09:15				0.62		16.41					20200614
				~	09:15		10:45				0.30		16.71					20200614
		15	Mo	~	02:00	~	03:10		AED		0.23		16.95					20200615
				~	03:10		03:55				0.15		17.10			B60			20200615
				~	03:55	~	04:30				0.12		17.21					20200615
				~	04:30	~	06:00				0.30		17.51	Float	L				20200615
				0.00		17.51
				~	13:40	~	15:45		WRD		0.42		17.93					20200615
				0.00		17.93
				0.00		17.93
				~	17:35	~	18:00	WP6-10	WRD		0.08		18.01					20200615
		16	Tu	~	02:05	~	07:10				1.02		19.03					20200616
				0.00		19.03
				0.00		19.03
				~	14:00	~	14:10	WP6-10	EML T48P		0.03		19.06					20200616
				0.00		19.06
		17	We	~	11:45	~	12:15	WP6-10	TW6-10	-$2.66	0.10	$354.43	19.16					20200617
		23	Tu	~	19:20	~	19:25	[WP9-10] SMSs to Mark and Keith “When can we install the last two W100s and batteries that you ordered, they are ready. This week?” / Photos and videos of DR Test Setup showing WP9/10	SMS IMG		0.02		19.18					20200623
	Jul	1	We		13:42		13:52	[WP9-10] Phone call from Mark: Scheduled Mo7/6 09:30 Lexington to go onsite at Odessa North and install WP9/B60 / Also discussed “new tower” which needs electrical work and is slated for WP10/B61	L14-15		0.08		19.26					20200701
		2	Th	~	02:40	~	05:20	[WP9-10] TODO and .ods; Locations Summary and Histories L14 and L15 created			1.33		20.60					20200702
		6	Mo	~	07:30	~	08:10	20200706 Invoice - Odessa North W100.doc	DBT TW6-10		0.67		21.26					20200706
				~	09:00	~	14:30	Preparation, travel and onsite at TurboNet office in Lexington and at ONWT for installation; Mileage / Photos and videos TurboNet Office, MikroTik Cloud Router Switch, W100 ONWT Installation, Keith Jones, Mark Webb	TW6-10 IMG L4	$41.11	5.50	$395.54	26.76	Sold	L14	B60	S11	C10	20200706
				~	15:10	~	15:15	[WP9-10] To Keith and Mark “Chillin’ with AC and a beer ))) I bet you’re still out there baking in the sun. Let me know when I can go to the new tower site with you.”	SMS		0.04		26.81					20200706
		7	Tu	~	02:00	~	06:45	TODO and .ods updates mostly related to WP9 and spinoffs therefrom; Milwaukee NiCd A charge started; Images from yesterday partially Organized	TW6-10 S2		4.75		31.56					20200707
				~	23:45	~	00:15	Milwaukee NiCd A charge terminated and B charge started	S2		0.50		32.06					20200707
		8	We	~	02:30	~	06:45	Images ORC (photos/videos shot Mo7/6)			4.25		36.31					20200708
2021	May	11	Tu	~	09:50	~	11:10	Onsite at ONWT for the Backup Power Supply Maintenance Program; See L14 for details	DBT TM21S EML SSC					L14	B60			20210511
	Nov	23	Tu	~	12:20	~	15:40	Onsite at ONWT with Mark, Keith, Dakota and ?; Installed Mier Enclosure with Schauer, B68/69, Traco and Dinico fan system / Keith has started moving antennas to the 48v system but it may be awhile before the W100 and B60 are no longer needed	TOI					L14				20211123
2022	Feb	19	Sa					Mimosas stopped working; Keith onsite; (Nothing was said about WP9 in the old system enclosure)	TM22 SMS					L14				20220219
		21	Mo	~	09:45	~	11:10	Onsite at ONWT with Keith and Dakota: His future plans for the old system is to clean up the rat's nest and keep it operational for the Netonix and B11 backbone connection to Lexington (as soon as the weather improves); We can connect directly from the old box to the new box so that we can access web relay(s) and etc. even if the new box Mimosas go down	TM22 IMG					L14				20220221

## WP10
WISPers: WP10	A					W100_9 ― 3rd Production Run ― Delta PS 24v/200w, Genasun, Fan					Batteries	Power Supply	Genasun

Date/Time CST/CDT					Description	Other Sources	Cost	Hours	Total Cost	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				$731.40	76.26	Sold	L15	B61	S12	C11

				0.00
				WP6-WP10

2020	May	8	Fr					WP6-10	TW6-10 DBT				0.00	Procure …					20200508
		19	Tu		10:48		11:18				0.00		0.00					20200519
		20	We		05:15		06:15				0.20		0.20					20200520
				TW6-10	$0.66	0.05	$0.66	0.25					20200520
		22	Fr	~	04:30	~	05:15		B57		0.15		0.40					20200522
		23	Sa	~	07:00	~	08:45				0.35		0.75					20200523
				14:41	~	15:00		L11		0.06		0.81					20200523
		26	Tu	~	03:30	~	11:50		TW6-10 DKE	$178.10	1.27	$178.76	2.08					20200526
		27	We	~	02:40	~	03:10		EML DKE		0.10		2.18					20200527
				~	16:50	~	18:30		Controllers		0.33		2.51					20200527
		28	Th	~	10:40	~	11:25		Supplies		0.15		2.66					20200528
2020	Jun	1	Mo					TW6-10	$7.40	0.10	$186.16	2.76					20200601
		2	Tu	~	07:30	~	12:40		TW6-10 DKE		0.85		3.61					20200602
		3	We	~	04:20	~	05:05		TW6-10		0.15		3.76	Assembly…	L0				20200603
				0.00		3.76
		4	Th	~	05:05	~	06:40	WP6-10			0.32		4.08					20200604
				~	06:40	~	06:55				0.05		4.13					20200604
				~	08:20	~	08:55				0.12		4.25					20200604
				0.00		4.25
				0.00		4.25
		5	Fr	~	07:25	~	09:00	WP6-10			0.32		4.56				S12		20200605
				~	09:50	~	11:30				0.33		4.90					C11	20200605
		6	Sa	~	03:00	~	03:55		IMG LBX		0.18		5.08					20200606
				~	03:55	~	05:10				0.25		5.33					20200606
				~	05:10	~	05:30		IMG		0.07		5.40					20200606
				~	05:30	~	08:00				0.50		5.90					20200606
		7	Su	~	03:05	~	04:45				0.33		6.23					20200607
				~	04:45	~	05:45				0.20		6.43					20200607
		8	Mo					EML		0.20		6.63					20200608
				~	10:50	~	12:15		L14-15	$2.07	0.28	$188.23	6.91					20200608
				~	12:35	~	13:50		TW6-10 EML	$0.40	0.25	$188.63	7.16					20200608
		9	Tu	~	05:30	~	06:30		TW6-10		0.20		7.36					20200609
				~	06:30	~	07:35				0.22		7.58					20200609
				~	09:30	~	10:25				0.18		7.76					20200609
				~	23:10	~	00:15				0.22		7.98					20200609
		10	We	~	00:15	~	03:00				0.55		8.53					20200610
				~	03:00	~	05:00		TW6-10		0.40		8.93					20200610
				~	05:00	~	06:10				0.23		9.16					20200610
				TW6-10	$168.46	0.63	$357.09	9.79			B61			20200610
		11	Th	~	05:10	~	05:50				0.13		9.92					20200611
				~	05:50	~	08:40	WP7-10			0.71		10.63					20200611
				~	08:50	~	10:45	WP6-10			0.38		11.01					20200611
				0.00		11.01
		12	Fr	~	02:00	~	03:20				0.27		11.28					20200612
				~	03:20	~	04:10				0.17		11.45					20200612
				~	04:45	~	06:40				0.38		11.83					20200612
				~	06:40	~	08:50				0.43		12.26					20200612
				~	08:50	~	09:40		B57		0.17		12.43					20200612
				~	09:55	~	12:45				0.57		13.00					20200612
				~	12:45	~	13:25				0.13		13.13					20200612
				0.00		13.13
				0.00		13.13
				~	03:55	~	05:45	WP6-10	B0		0.37		13.50					20200612
				~	06:05	~	09:10		S1		0.62		14.11					20200612
				~	13:50	~	17:15		W10		0.68		14.80					20200612
				~	17:15	~	22:15				1.00		15.80			B61			20200612
		14	Su	~	06:10		09:15				0.62		16.41					20200614
				~	09:15		10:45				0.30		16.71					20200614
		15	Mo	~	02:00	~	03:10		AED		0.23		16.95					20200615
				~	03:10	~	03:55				0.15		17.10			B61			20200615
				~	03:55	~	04:30				0.12		17.21					20200615
				~	04:30	~	06:00				0.30		17.51	Float	L				20200615
				0.00		17.51
				~	13:40	~	15:45		WRD		0.42		17.93					20200615
				0.00		17.93
				0.00		17.93
				~	17:35	~	18:00	WP6-10			0.08		18.01					20200615
		16	Tu	~	02:05	~	07:10				1.02		19.03					20200616
				0.00		19.03
				0.00		19.03
				~	14:00	~	14:10	WP6-10	EML T48P		0.03		19.06					20200616
				0.00		19.06
		17	We	~	11:45	~	12:15	WP6-10	TW6-10	-$2.66	0.10	$354.43	19.16					20200617
		23	Tu	~	19:20	~	19:25	WP9-10	SMS IMG		0.02		19.18					20200623
2020	Jul	1	We		13:42		13:52		L14-15		0.08		19.26					20200701
		2	Th	~	02:40	~	05:20				1.33		20.60					20200702
		6	Mo	~	15:10	~	15:15	WP9-10	SMS		0.04		20.64					20200706
		27	Mo	~	11:29	~	12:15	Call to Keith, NA; Call to Mark "Hopefully they're going to get the power run to the new tower in the next week", also discussed new office building electrical and Swafford (Ubiquiti keeps needing a reset, suggested MicroTek w/quality 12-24vdc converter $150+); Missed call and call to Keith "Waiting KCPL", also discussed new building electrical (3-phase power, "come over and reroute some stuff") and Swafford [New Tower Electrical and New Building Electrical are direct spinoffs from WP10 and costs/time will be recorded here]	L15 L16 L2		0.77		21.41					20200727
		30	Th	~	10:27	~	10:30	Call from Mark, the H&C work in the new building is done, "please come discuss the electrical changes/improvements needed," 109 S 10th ST, W of courthouse, 2 story brick building, Fr7/31 09:30 appointment	L16		0.05		21.46					20200730
				~	10:55	~	11:10				0.25		21.71					20200730
		31	Fr	~	09:07	~	09:12	SMS to Mark and Keith: "Sorry, can’t make our 930. Maybe this afternoon, Saturday or Monday. I’ll contact you."	SMS		0.08		21.79					20200731
				~	12:20	~	12:53	SMSs and calls from/to Mark: Meet at new tower in Richmond ~14:00-15:00, then go on to Lexington new building/office; "2 is not good, but I can make 3 in Richmond"			0.55		22.34					20200731
				~	14:25	~	18:40	Prep; Travel and onsite at New Tower [OT] and New Building [TLNB]; Other calls/SMSs enroute; Notes and photos of needs at both sites / WM stop -40 mins but TODO +40 mins / Mileage; See white sheet for TW6-10 for details	TW6-10 SMS IMG L15 L16 WS	$27.72	4.25	$382.15	26.59					20200731
2020	Aug	3	Mo	~	17:13	~	17:29	Call from Mark: Discussed Building Electrical (I gave him a rough estimate, but I will send something more concrete tomorrow morning) / New Tower (wants to get it done this week); Swafford's; Send him quotes/estimates Tu8/4 AM	L16 L15 L2		0.27		26.86					20200803
		4	Tu	~	06:20	~	08:30	TODO and .ods related to New Building and New Tower; Research for quote on New Building Electrical (decided to "pass") / Phone calls/SMSs to Keith and Mark (also discussed Swafford); TODO Priorities rearranged / See TW6-10 printouts of research and phone calls	TW6-10 SMS L16 L15 L2		2.17		29.02					20200804
				~	09:00	~	10:00				1.00		30.02					20200804
		5	We	~	06:00	~	08:40	TODO and .ods related to New Building, New Tower and Swafford (another spinoff) / Includes time for T400s crash (dumped a bunch of stuff, needed to try to determine why)			2.67		32.69					20200805
				~	09:15	~	14:30				5.25		37.94					20200805
				~	14:30	~	14:40	Call to Keith: LMVM and SMS "Again, please give me a call, I've got 3 things/points to discuss with you quickly, thank you."	SMS		0.17		38.11					20200805
		7	Fr	~	10:35	~	11:10	New Tower: Preliminary list of materials and tools; Call to Keith, cleared the air over having "passed" on doing New Building Electrical, discussed New Tower (does he have any brackets for Netonix? he'll look), discussed Swafford (reasons for best recommendation DC Netonix), Keith is not looking at doing New Tower or Swafford until the end of next week but he said "call Mark, his plans are not always my plans"			0.58		38.69					20200807
				~	11:10	~	11:40	New Tower [OT] and Swafford [RN]: Call to Mark to discuss scheduling; New Tower meter s/b in place already (he'll go onsite and check) / Swafford DC Netonix s/b in stock today; Mark wants to do New Tower and possibly Swafford on We8/12; Quotes are not necessary (just get it done and send a bill); TODO Priorities			0.50		39.19					20200807
		10	Mo	~	10:28	~	10:31	Call from Mark: Swafford tomorrow after lunch; Meet at zipline office 13:00; New Tower discussed, Mark will check to see if meter is in place and wants to do it We8/12	L2 L15		0.05		39.24					20200810
				~	20:20	~	20:25	SMS from Mark: Keith may arrive in Rayville earlier, 11:00-12:00	SMS L2		0.08		39.32					20200810
		11	Tu	~	04:45	~	09:45	TODO and .ods related to Swafford and New Tower; [Interruptions -45]; Swafford Procurement (load cables with fuse); Looked up average Watts from when Wattmon was running (15.8w 3/17); Gathered materials and tools to take onsite; SMSs to Mark and Keith; SMSs from/to Mark; New Tower Procurement; Nothing found for box needed that is comfortable (Home Depot may be able to get a box that is not as high as I want); Call to Stanion Electric, Liberty (hold on 24x24x8 NEMA 3R $189 in stock); Planned trip to Liberty for New Tower	L2 L15 SMS		4.25		43.57					20200811
				~	12:05	~	13:45	Swafford: Onsite at RN with Keith; Mileage / While with Keith he related that he had just gotten the fiber setup with UPS moved to the New Building (A2/B22_28 L4->L16)	L2 SMS IMG TSP L4	$2.30	1.67	$384.45	45.24					20200811
		12	We	~	10:35	~	13:05	TODO and .ods related to Swafford; 20200812 Invoice - Swafford.doc sent by email to Mark and Keith (the email contains a pitch for solar at low powered sites); [-30 for distractions]	DBT TSP L2 EML		2.00		47.24					20200812
				~	13:05	~	13:30	TODO and .ods related to New Tower; Called Stanion Electric, SMS to Keith (see NT)	L15 SMS		0.42		47.66					20200812
				~	14:35	~	14:40	SMS from/to Keith regarding New Tower: "Friday is fine"; "Tx"			0.08		47.74					20200812
				~	21:50	~	23:20	TODO and .ods related to New Tower and move from Old to New Building	L4 L16 A2 B27_28		1.50		49.24					20200812
		13	Th	~	08:00	~	11:00	Procurement, New Tower: Liberty, Lowe's ($38.48) and Stanion Electric ($205.74); Misc. stock items ($10.00); Mileage	TW6-10	$284.58	3.00	$669.03	52.24					20200813
				~	18:50	~	20:20	New Tower: TODO and .ods related to procurement run and tomorrow's scheduled installation			1.50		53.74					20200813
		14	Fr	~	07:30	~	08:35	New Tower: 20200814 Invoice - New Tower W100.doc; Mark called (meter was installed yesterday, OK to go onsite ~9:30, he'll bring check or checks $90 + $370) / Emailed $370 invoice to Mark and Keith	DBT TW6-10 EML		1.08		54.82					20200814
				~	08:35	~	10:05	New Tower: Prep. to go onsite; WP10 removed from test setup (final assembly); Cleaned fan filter; Loaded Subaru	B61		1.50		56.32	Install	Subaru				20200814
				~	10:15	~	17:10	New Tower: Onsite 2x; Mileage; 1st onsite 35 mins (Mark called, Keith won't be out today, Milwaukee batteries dead); Returned to shop for tools / 2nd onsite 3 hrs 45 mins (Mark came by and I rec'd $370 check for WP10/B61 and $90 cash for Swafford); Installed box and electrical service; Installed WP10 and B61; Photos / MMS to Mark and Keith (replies rec'd 16:18 from Mark and Sa8/15 03:30 from Keith)	TW6-10 IMG SMS	$32.20	6.92	$701.23	63.24	Sold	L15	B61	S12	C11	20200814
		17	Mo	~	08:00	~	09:15	TODO and .ods related to New Tower; Call to Keith, NA, SMS "I need to go back ..."; Call to Mark, ditto, he said he was going to be onsite tomorrow 9:30-10:00; SMS to Keith	SMS		1.25		64.49					20200817
		18	Tu	~	10:50	~	11:00	Call from Mark: They are onsite, wants me to come (but I didn't commit myself)			0.17		64.66					20200818
		19	We	~	12:30	~	12:40	Call from Mark: He planned to go onsite to finish Netonix installation; I told him I was not feeling well (true, I was exhausted); I said I would get back onsite for "3 little things" / He said he would lock it up after I get there, let him know (and I could tell he was curious about the invoice)			0.17		64.82					20200819
		21	Fr	~	05:00	~	08:05	TODO and .ods for Fr8/14+; 20200821 Invoice - New Tower Electrical.doc; Emailed invoice to Mark and Keith; SMS to Mark; WP10 summary $; Budget reschedule	TW6-10 DBT EML SMS		3.08		67.91					20200821
				~	08:05	~	08:15	SMS from/to Mark: Meet at New Tower at ~11:00, he'll text once he's at high school (they need to put up and take down a radio there)	SMS		0.17		68.07					20200821
				~	09:50	~	12:00	Procurement, ant traps, WalMart, Orscheln's, Harp's ($3.77); Called Mark (they're not coming into Richmond today, they'll be in Richmond Monday ~10:00); Onsite New Tower / Tried to install relief clamp for 1/2" knockout but Ethernet cables won't fit; Plugged top of 1" conduit; Installed ant trap; Photo; Mileage; [-20 personal]	IMG TW6-10	$20.62	1.83	$721.84	69.91		L15				20200821
		22	Sa	~	04:20	~	04:45	TODO and .ods for New Tower Fr8/21			0.42		70.32					20200822
				~	05:45	~	06:05	Lowe's return gathered and some unloading of Subaru			0.33		70.66					20200822
		23	Su	~	04:40	~	06:00	Images ORC: New Tower and New Building Fr7/31; Swafford Tu8/11; New Tower Fr8/14 and Fr8/21			1.33		71.99					20200823
		24	Mo					I went to Richmond for Swafford's Ford appointment (inspection); Mark was in town, but he forgot to bring the check	SMS		0.17		72.16					20200824
		25	Tu	~	09:00	~	09:05	SMS to Mark "Bring the check with you wherever you go today, I'm going to hunt you down on either side of the river. )))"			0.08		72.24					20200825
				~	09:14	~	09:20	Call to Mark: Meet at WalMart at 10:00			0.10		72.34					20200825
				~	09:45	~	11:25	SMSs to/from Mark; Onsite at New Tower and rec'd check for $610.62 from Mark for "Oak tower Electrical and Box work" / Discussions with Mark and Keith concerning future projects (Web Relays YES, Maintenance by 10/15 YES, 24v and 48v systems YES); Photos of Keith and Mark; US Bank D&W; Mileage	SMS IMG TW6-10	$14.95	1.67	$736.79	74.01		L15				20200825
				~	11:55	~	13:15	SMSs to Mark and Keith to confirm that it is called "Oak Tower" (yes, edited Location Short Name and Description); TODO and .ods; USB/SPF; Invoice filed as paid	SMS TW6-10		1.33		75.34					20200825
		28	Fr					Lowe's, Liberty: Return of unneeded parts from New Tower procurement Th8/13; No mileage (I had another more important reason for going all the way to Lowe's)	TW6-10	-$5.39	0.25	$731.40	75.59					20200828
		31	Mo	~	12:20	~	13:00	Unloaded Subaru and put tools away; Cleared bench (WP project is finished for now)			0.67		76.26					20200831
2021	Mar	16	Tu	~	14:10	~	15:50	Onsite at OT for the Backup Power Supply Maintenance Program; See L15 for details	DBT TM21S SMS IMG SSC					L15	B61			20210316
	Sep	30	Th	~	13:00	~	19:30	Email notifications (6) 13:11-18:14; W100 needed to be reset; See L15 for details	EML SSC SMS TM21F					L15				20210930

## WP11
WISPers: WP11	A					W150_1 ― 4th Generation Prototype ― Dual Supply, Diode Isolation at Traco Input; Modular Assembly on Backplate; 52.8v Output

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L17	B58	BC9	S17	V11
2022	Jun	10	Fr					Conceived, but not born and named yet: I didn't know it at the time, but on this day the request for the new LSWT site eventually led to the new W150 product line; Due to problems with the Schauer chargers (T-comp reversed above ~35⁰C) I needed a new battery charger / power supply design ASAP; Therefore decided to pursue a Float Only Battery Charger design I soon called "Dual Supply with Traco Isolation"	T48S T48-3 L17	On Order					20220610
		16	Th					Proof of Principle tests of Traco and ~54v power supply on output: The new approach "Dual Supply with Traco Isolation" looked promising (but inconclusive) [abandoned Mo8/22]	T48-3 L17 IMG	R&D	L0			S13	V11	20220616
		23	Th					Completed 20220621 Proposal - LSWT Installation.pdf; 20220623 Email to Mark & Keith 'Proposal - Lexington South Water Tower Installation'.pdf; / Proposal included 20220621 Diagram 'Dual Supply with Traco Isolation' SSC Scan.jpg; Planning on assembling components on Wiegmann back plate; / Calls and SMSs Mark & Keith: Mark will pay $1,600 advance Mo-Tu next week and "go ahead and order"	T48-3 DBT EML SMS L17	Assembly					20220623
		27	Mo					[WP11-14] DigiKey orders placed: Fuses (SCP-75-12 10a); (4) Power Cable Switches [Sa9/10/22 slated for WISPers for LSWT, CFS, Spare and ONWT or LWT]	T48-3 EML DKE L17					20220627
2022	Jul	19	Tu					[WP11-14] New CFS site ordered, and it also needs to be the new "Dual Supply" design, so it was added to the new W150 product line (but neither one was yet born and named!)	T48-4 L18 T48-3 L17					20220719
2022	Aug	10	We					[WP11-14] Finished fabrication of (4) Power Cable Switch Assemblies; Labels printed TurboNet Disable Switch 48V Power Cable ON OFF 0.7.lbx; Photos / [Sa9/10: These Power Cable Switch Assemblies are slated for WISPers for LSWT, CFS, Spare and ONWT or LWT]	T48-3 IMG LBX L17					20220810
		20	Sa					Dual Supply Bench Testing Setup Assembled: Wiegmann Back Panel on bench; Back Panel wired up; Instrumentation connections; Stabilizing towards +25.0⁰C	T48-3 L17	Testing		B58	BC9	S13	V11	20220820
		22	Mo					Bench Testing: Traco transition from idle (Load Supply) to battery drops the output below 5v (120w load); Paradigm Shift: Back to R&D; New Design "Isolation at INPUT of Traco"	T48-3 L17 WS	R&D					20220822
		23	Tu					White sheet diagram: Dual Supply Isolation at Traco INPUT showing relay contact in parallel with diode; Can use a standard diode instead of a Schottky					20220823
		27	Sa					[WP11-12] White sheet diagram: Dual Supply with Cathode Grounded Diode Isolation (SSC DBT); Placed DigiKey and Mouser Orders ($124.44); Saved datasheets to Library / [Su9/11: We now know the diodes that were ordered are slated for WP11/12; The 2nd diode was ordered in case I blew the first one in Testing, but I'll most likely use it for WP12]	T48-3 SSC DBT EML DKE MOU LIB L17 WS					S17		20220827
		30	Tu					[WP11-12] The W150 Product Line is Born and Named: Massive Alternative Energy.ods expansions [4 days Fr9/2 to Mo9/5]; / Before Tu8/30 the R&D and assembly records were pivoted on the Locations history sheet for LSWT and columns were used for the components (Charger, Load Supply, DC-DC); But at this point I decided to start taking an integrated approach to these new WISPers, placing the component columns on the WISPer history sheets, and no longer using the columns on the Locations sheets (by adding a reference to the WISPer in a new column); Future Locations sheets will not need the component columns (Charger, Load Supply, DC-DC) as there will be a WISPer reference column; Locations sheets won't have to be used for all the R&D and Assembly details (which from now on should be here on these WISPer history sheets); Before Tu8/30 see L17 (LSWT) for R&D and Assembly details of the prototype W150_1	T48-3 L17			B58	BC9	S17	V11	20220830
		31	We					DigiKey and Mouser orders received (but not opened): Load Supply, (2) diodes and a diode suppression relay; / Library > Mean Well AND Vishay: 20220828 DigiKey Invoice, Annotated; Load Supply and Diodes; T48-3 (LSWT) WP11 S17 (MW_5); 20220906 Scan.jpg; / Library > Omron: 20220829 Mouser Invoice, Annotated; Diode Suppression Relay; T48-3 (LSWT) WP11; 20220906 Scan.jpg	T48-3 DKE MOU SSC LIB					20220831
2022	Sep	1	Th					Unpacked and examined DigiKey and Mouser orders: The relay is a contactor (no pole connection) but they should work (see diagram on MOU invoice); / Discovered Test Report for RSP-200-13.5: Very interesting and helpful info for this new design; / BACKPLATES design s/b as small as possible: Various sites considered (ONWT, LWT, CFS, LSWT); ~10x14" (<=3.5" high) will fit inside Engel (big advantage, can test at -15 and +50degC); / TODO for [T48-4] "Approach Mean Well": Considered possibilities for obtaining 30mV/⁰C T-comp and a higher power battery charger for full redundancy	T48-3 LIB LBX DKE MOU L14 L10 L18 L17					20220901
		3	Sa					Design of Modular Assembly on Backplate: Use this approach immediately (don't do the "Proof of Principle" bench testing on the Wiegmann backplate) / Need a Barrier Strip for Traco 52.8v Output, near Power Cable Switch: Availability research started / Off-module connections listed and considered / Considered onsite replacement or repair of module: Procedure for Module Replacement / Considered interconnections on the module / Considered Backplate construction and mounting holes: Standard hole spacing, as large as will fit in Engel ~10x14", prototype to use aluminum baking sheet, layout design drawing needed / [Mo9/12 ordered 1 piece aluminum sheet from MBTF (Metal By The Foot, KC): This stuff is probably good for prototype and production runs] / Considered billing politics and future production man'f of the W150s: WP11 for LSWT, then WP12-13 production run (CFS and spare), then WP14-16 production run for sites that need upgrades / Considered possible paradigm shifts for the prototype to obtain full redundancy, faster charging, and elimination of Load Supply: / (2) SCP-75-12 in parallel?; Eliminate Load Supply, Diode and Relay? / Examined SCP-75-12 load regulation figures (see BC9): Datasheet (2%); Test Report found and saved to library, Load Regulation result is promising (-0.08% to +0.12%) / These paradigm shift questions to be decided after measuring the SCP-75-12 load regulation performance ... / Modified test setup to measure SCP-75-12 load regulation 0~105w: Disconnected V11 and S13; ITECH on battery; Started measurements at 0w …	T48-3 LIB S13 PLN				BC9		V11	20220903
		4	Su					Measured SCP-75-12 Load Regulation 0~105w (see BC9 for details); CONCLUSIONs: / Stay with diode/relay isolation design scheme, and only one SCP-75-12: / Even after beefing up the connections to reduce the droop it will be more than we'd like to tolerate for good battery health / At high load levels the SCPs run very hot, all of the time, and the charging rate is VERY SLOW TO NON-EXISTANT (as most or all of the battery charger power is going to the load) / See T48-3 for further thoughts and notes including no clear advantage at this time for using (2) SCP-75s with a Load Supply and diode isolation / The whole night was spent considering a design option that is not better than what I had before I started thinking about two SCPs in parallel	T48-3 PLN			B58				20220904
		7	We					[WP11-13] Barrier Strips Research: Selected TE Connectivity AMP Connectors 1546307-4 / We have stock on metric screws for blind mounting of supplies (BC9, S17) / DigiKey Order: (3) Barrier strips (slated for WP11/12/13); $16.68 / Datasheet to Library > TE Connectivity AMP Connectors > 20220907 Datasheet 1546307 Series Barrier Strips (1546307-4 Ordered) ENG_CD_1546307_D9.pdf / Visit from Brandon and Dakota 13:30-14:10: They just showed up while I was on the porch with Caleb; They came to swap my DVS rooftop equipment from Ubiquiti to Mimosa / I told them "not now!"; Appointment for Th9/8 10:30 / They will pickup the MikroTik switch/router and PBP tomorrow, and they can bring me a check from Mark ($638, I was working on Report & Invoice when they showed up)	T48-3 DKE EML LIB L L17					S17		20220907
				20220630 Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps.pdf / 20220907 Email to Mark & Keith 'Report & Invoice - Maintenance, WWT & RCWT Equipment Swaps'.pdf; WP11 mentioned in email	TM22 DBT EML L17					20220907
		10	Sa					Visited Scott's Bargain Barn (SBB) looking for sheet aluminum and red/blk solid #14/16/18: / Aluminum and solid wire not found, but I bought an assortment of stranded wire very useful for my work for TurboNet	T48-3					20220910
		11	Su					Aluminum Sheet (R&D TODO): It would be best to make the prototype with the same material as the production versions; Considered thicknesses and sources (TODO Mo9/12 AM) / Considered TurboNet politics for all new orders/requests (R&D): / Goals Considered: W150 modular assembly at ALL sites; Mier and differential fan cooling for ALL exterior/exposed sites / RWWT is a special case: Install a W150 and install an A/C that always runs at 68degF (20degC) / Price List Product Line considered: W150, Mier, Trojan Batteries, Professional Rate Schedule / Mier with Differential Fan Cooling Assembly: Considered preparation and installation of the Mier/Dinico assemblies / "Stay the Course" (R&D TFTP): / Priorities Considered: Stick to my plan to get the .ods work and the T48-4 invoice done before starting assembly and testing of the prototype W150 / New ETA for LSWT installation week of Mo9/12-Sa9/17	T48-3 L11 L17					20220911
		12	Mo					Aluminum Sheet Local Availability Research: / Considered Specifications: Thicknesses and tapped holes threads list / Calls and Web Research: Selected Metal By The Foot (MBTF) / W150 Backplate Rough Layout Design: Verified dimensions (measured Engel carefully, drawings on PLN); Backplate Size Determined: / W150 O.D.: ~10x14x2.5" / Standard Mounting Hole Spacing: 12" / Sheet Aluminum before bending flanges: ~11x15" / Sheet Aluminum Order Size (MBTF to shear within 1/8"): 11-1/4" x 15-1/4" / Called MBTF To Place Order (Assembly): $13.70; Will pickup in the next few days / Considered backplate fabrication	T48-3 MBTF PLN Z0					20220912
		13	Tu					[WP11-13] White Sheet "If Mark calls about LSWT": Estimated prototype assembly, bench testing and Wiegmann assembly schedule / Earliest onsite install estimated ~Th9/22 to Sa9/24 (end of next week) / Received barrier strips: Library > TE Connectivity AMP Connectors > 20220907 DigiKey Invoice; (3) Barrier Strips T48-3 T48-4 WP11-13; Scan.jpg	T48-3 L17 DKE LIB WS					20220913
		15	Th					[WP11-14] Mentioned in Report, photos and email: / 20220722 Report & Invoice - Power Cable Assembly for CFS.pdf / 20220915 Email to Keith and Mark 'Report & Invoice - Power Cable Assembly for CFS'.pdf	T48-4 DBT EML L17					20220915
				Trip to KC MBTF: Pickup of aluminum sheet ordered Mo9/12; Purchased gloves and 24" combination square; Photos inside and outside MBTF	T48-3 MBTF PLN IMG Z0					20220915
		16	Fr					Billable Hours Revised: Procurement, Parts and Assembly Separated, W150_1 and Wiegmann; Printed and applied new label TurboNet File Folder 0.7x3.25 T48-3.lbx	T48-3 LBX L17					20220916
		17	Sa					Billable Hours Revised > New Totals Fr6/10 to Fr9/16: / Daily Total Hours: 251.1 / W150_1: 19.3 $372.20 94 miles $1,285.20 / Wiegmann: 14.3 $42.93 $614.93 / Reduced Rate: 128.2 / Installation: 1.6 $64.00	T48-3 L17					20220917
				Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG				WP11			20220917
		18	Su					Disassembled Bench Test Setup and Wiegmann Backplate: Removed Power Cable Switch, BC9, V11 and S13; Moved Wiegmann Backplate to garage (with Z20 Assembly still attached) / Bench Setup Changes/Improvements: B58 Float Maintenance on BK; Z19 T2 Epoxied into 5/16" Battery Connector; Plastic Cap on Negative Post; Indirect Comparisons of Z19 T2 with Z20 T2 ...	T48-3 PLN IMG Z19 Z20 S13			B58	BC9		V11	20220918
		19	Mo					Indirect Comparison of Z19 T2 with Z20 T2, CONCLUSIONs: Z19 with Plastic Cap reads +0.35⁰C higher than Z20 / This explains why I thought BC9 needed to be adjusted again for target 13.500vI at 25.0⁰C (because it was adjusted w/o battery using Z19 on Fr8/19, then I made observations using Z20) / I confused the comparison somewhat by installing the Plastic Cap, which appears to drop the battery T readout by about -~0.25⁰C / I think it is safe to state that Z20 T2 reads ~-0.5 degC lower than Z19 T2 / The best way to find out what the comparison is between the two sensors (Z19/Z20) is to install the Z20 T2 lug and the Z19 T2 lug together on the negative post of the 27TMX / But I'm not that interested in knowing this difference, and Z20 is "installed" on the Wiegmann backplate to go to LSWT, so I will not delay assembly of the W150 prototype in order to do this / TODO for ONWT: W150 BTS and Z18 T2 in lug s/b on T-105 negative post under Plastic [Foam] Cap [We9/21 Decided to install these under a Cap on the +6v negative post of a T-105] / Set New PSP=25.4 ... ~10 hours later the battery stabilized at 25.0⁰C	T48-3 PLN Z0 Z19 Z20 L14					20220919
				Design, Drawing, W150 Electrical Schematic: 20220919 W150 Electrical Schematic JAK; T48-3; Scan.jpg / Cardboard template made for visualization / brainstorming on backplate layout: Photo shows layout of BC9, S17, V11 and other components (mostly considered, will finalize later)	T48-3 SSC DBT IMG					S17	V11	20220919
		20	Tu					Bench Setup Changes/Improvements: Moved Z19 T2 and Plastic Cap to Battery +; Rotated Battery (+ near the front); Installed new design Foam Block (Battery +)	T48-3 PLN IMG Z0 Z19					20220920
		21	We					Bench Setup Changes/Improvements: / Engel Heat/Cool Duty Cycle Changed; Rotated 27TMX (+ to left rear); Z19 T2 and Foam Cap on Battery (-); Fabricated and Installed Another Foam Cap on 27TMX +; TODO for ONWT / Mark and Keith: Mark wanted to know if we can install "early next week"; TODO priorities shifted (postponed .ods recordkeeping, invoicing, WP11A) / Earliest onsite install estimated ~We9/28 to Sa10/1 / SMSs to Mark and Keith "Maybe, but late next week is more likely. I promise you it will be worth the wait, the W150 modular dual power supply is impressive (we enter a new era)"	T48-3 PLN SMS Z0 Z19 L14 L17					20220921
		22	Th					Can't Bend Flanges: Abandoned W150 Cardboard Template #1 in favor of flat 10x14x0.090" with 10x1/2x1/2" aluminum bar on (4) edges [Mo10/24 Template #1 pinned to Wall of Memories]	T48-3 PLN					20220922
		23	Fr					Sent EML to Mark & Keith: Project set back another 2 days due to fabrication method change [actual schedule delay turned out to be 5 days] / TFTP on my business plan hopes and desires including plans for 1st and 2nd Production Runs [edited Mo10/24] / Design, Drawings, Backplate Layout: Started work on new Cardboard Template #2 (10x14"); Photo of Template #1 (garage bench) 20220923 0956 IMG_3242 PSE.jpg	T48-3 EML IMG L17					20220923
		24	Sa					... Design, Drawings, Backplate Layout: Progress on Cardboard Template #2 and Wire Routing; W150 Barrier Strip.lbx / TFTP: Do I really need all those Extech test loops? - NO	T48-3 LBX					20220924
		25	Su					… Design, Drawings, Backplate Layout: Progress on Cardboard Template #2 and Wire Routing; Screw changes/improvements for 10" bars; Extech Test Points (3); Strain Relief Points simplified / Engel Stable at +25.0⁰C: PSP found for We9/21 changes/improvements	T48-3 PLN Z0					20220925
		26	Mo					… Design, Drawings, Backplate Layout: Wire Routing Approved, 20220926 W150 Wire Routing Template; T48-3; Scan.jpg; Moved Backplate FG and Diode to the left (Cardboard Template #2)	T48-3 SSC DBT					20220926
		27	Tu					… Design, Drawings, Backplate Layout: Component List Notes completed (they were compiled in TODO Mo9/19 to Tu9/27) / Backplate Layout "finished" [with sidebars], "W150 - Cardboard Template #2 - 9/27/22 JAK", photo on white background (garage) 20220927 0518 IMG_3261 PSE.jpg / Started Assembly: Side bars cut on bandsaw (>2 hours); Cut Backplate down to 10x14" / Changed plans to eliminate side bars: New plan (5) 1/2" high feet	T48-3 IMG L17	Assembly					20220927
		28	We					… Design, Drawings, Backplate Layout "Finished" [but a few minor changes Th9/29]: Modified to eliminate sidebars and show feet locations / "W150 - Cardboard Template #2 - 9/28/22 JAK", photo on white background (kitchen) 20220928 W150 Layout Template #2 JAK; IMG_3262 PSE.jpg / Backplate Painted: Experiments with coating aluminum scrap, red battery terminal protection spray (REJECTED), Rust-Oleum High Heat Enamel (Good) / Plastic covering removed from 10x14" and applied two coats Rust-Oleum; TFTP and notes on how to paint the backplates in production	T48-3 IMG DBT					20220928
		29	Th					Much Needed Mill Improvements; Assembly Approach Thoughts / W150_1 Backplate FINISHED: Minor changes made to "W150 Cardboard Template #2"; Scribed hole locations (photo); Backplate mounted on mill, holes drilled, tapped, deburred and cleaned	T48-3 IMG					20220929
		30	Fr					Parts Assembled Onto Backplate: Hardware Details for Assembly Parts List; Photos / Started Point to Point Wiring and Cabling: Planned battery cable lengths; Marked Wiegmann backplate for W150 mounting stud locations; Cables should extend at least 29" below the W150 backplate bottom (not counting ring connector extension); BTS cable is short but OK for Wiegmann (and maybe OK for any installation); Wiring Details for Assembly Parts List	T48-3 IMG L17				BC9	S17	V11	20220930
2022	Oct	1	Sa					Engel (+25⁰C Target): Found Relay Contacts Fused Closed; B58 ~34⁰C (BK float ~180mA, reduced voltage); Changed relay wiring (both poles for heat) / ... Point to Point Wiring and Cabling: Wiring Details for Assembly Parts List; Wire Label 0.5 W150 Power Supply.lbx; TODO for 1st Production Run "eliminate (4) 1/4" zip-tie holes on right edge" / W150_1 powered up for the first time (w/o Traco output connections): "so far so good" / TFTP RSP Load Supply s/b set 13.8v: Not 15.0v as planned earlier (I didn't take into account the diode drop); [RSP Load Supply set to 13.70vF on Tu10/4 when in testing at -15degC]	T48-3 PLN Z0 LBX			B58				20221001
		2	Su					Engel Stable at +25.0⁰C: Found PSPs for Heat OFF and Heat 5 / ... Point to Point Wiring and Cabling FINISHED; Assembly FINISHED (minus labels): Wiring Details for Assembly Parts List (Traco Outputs) / Bench Testing Started (+25⁰C): Bench testing setup modified; Proof of Principle Tests Passed, Transitions OK (150wI and 175wI Traco load, Von Living 0.00v); It works as I had hoped / Started overnight BURN-IN test (175wI load on Traco) ... / TFTP Political/Financial/Scheduling Concerns: Changes in plans, will not do full environmental testing now (W150_1 in Engel), postponed until we have W150_3 and 27TMX spares / Moving Engel to -15⁰C ...	T48-3 PLN Z0 L17 BC10 Z20	Testing		B58	BC9		V11	20221002
		3	Mo					Bench Testing (-15⁰C): Stabilizing, looking for PSP; Tcomp estimate (during cooldown) -20.7mV/degC (it's looking like we can lower S17 set to 13.7v or 13.6v) [Tu10/4 set 13.7v] / Burn-In Test Passed: W150_1 on bench, no fan, 175wI Traco load, >15h, Z20 T1 48.2⁰C (between supplies above contactor, silver tape), T2 51.0⁰C (1/4"-20 foot bolt near label area, 5/16" lug) / Mark and Keith Communications: They want it now! (see L17, photo)	T48-3 PLN Z0 SMS IMG EML L17					20221003
		4	Tu					… Mark and Keith Communications: Ignore any texts and calls and say nothing today (see L17) / Bench Testing (stable at -15⁰C): PSP and duty cycle; BC9 Float 14.30vF, Tcomp +25 to -15⁰C -20mV/⁰C / Adjusted S17 to 13.70vF, stable throughout range 0-150wI Traco load: Diode +0.608vM (BC9 float 14.30vF, no significant conduction seen with Extech) / Multiple AC OFF/ON Transition Tests with 180wI Traco load during very deep discharge to Traco low voltage cutout (8.2v) / Recovery while heating to +50⁰C: 180wI Traco load; Highest backplate temperatures seen Z20 T1 61.5⁰C, T2 57.2⁰C; TODO for T48-4 (move Contactor and Power Switch down)	T48-3 L17 PLN Z0			B58				20221004
		5	We					Bench Testing (stable at +50⁰C): (Battery is still in recovery); Z0/19 Relay problems, found PSP; BC9 Float 12.85vF, Tcomp +25 to +50⁰C -26mv/⁰C; BTS Compensation Estimates (CONCLUSIONS) / Transitions AC OFF/ON AOK (180wI Traco load); Moving on to +25⁰C / W150_1 Bench Test Setup photos and video (A Hard Day's Night); Mark and Keith Communications (see L17, video)	T48-3 PLN Z0 Z20 Z16 B0 Z17 S2 SMS L17 IMG					20221005
		6	Th					Bench Testing (~25⁰C): Recovery complete; Schauer Equalize Test (AC ON, 180wI Traco load, Engel open, 1h); Bench Testing Finished / Mark Communications: Mark here to move Wiegmann (see L17) / TFTP: The future (W150_2/3, then W150_4/5/6/7/8); Production units configuration plan (simple, fast, easy)	T48-3 PLN BC7 Z0 Z20 Z17 SMS L17	Assembly					20221006
		7	Fr					Final Assembly: BTS zip ties; Tightened all screws; Thermal grease cleaned; Labels designed, printed and applied (see T48-3 for a comprehensive list); Being used for B58 maintenance float / W150_1 Invoice Date: S/N 11-221007 [Invoice emailed to Keith and Mark Fr10/21]	T48-3 LBX L17	Sold	L		BC9	S17	V11	20221007
		8	Sa					Contemplation of W150_1 Creation: History since 7/18/17 "Let There Be WISPOWER" / Photos of W150_1: Product line and orthogonal photos; WP11 and B58 disconnected (they will not be powered again until they are installed at LSWT) / Mark and Keith Communications: "Today … baby pictures."	T48-3 IMG SMS			B58				20221008
		11	Tu					Loaded Subaru for onsite installation at LSWT	T48-3 L17		Subaru					20221011
		13	Th					[WP11-18] Improved plans for W150 Parts and Assembly Labor Sheets: WP11P, WP11A / CFS Proposal Approved (WP12-13): Meeting with Mark at USB, $1600 received, LSWT installation Postponed Again / TFTP/TODO Planning of 2nd Production Run (WP14-18): Power Cable Switches SPST instead of DPST; [Mo10/31: Conceived plan to use the Traco Disable Input, so PCSs will not be used] / [Mo12/12: Plans were changed after receiving a 2nd Murata meter, the 2nd Production Run will be Quantity 2 (WP14-WP15)]	T48-3 T48-4 DWP SMS L17					20221013
		14	Fr					[WP11-16] Planning; WP11P Parts List Started; Ordered (5) Tracos from Sager (WP12-16, V12-16)	T48-4 SPSE SSC EML					20221014
		17	Mo					WP11P Section "Hardware" finished [development paused until Su11/6 until caught up on .ods recordkeeping]	T48-4					20221017
		21	Fr					20221007 Report, Photos & Invoice - W150_1 for LSWT.pdf emailed to Keith and Mark: Includes "Ha ha" 20221008 1036 IMG_3315 PSE Backplate and Eggs.jpg / Onsite at LSWT: Windy but warm; Photos; Installed B58 and WP11 / Installed enclosure MikroTik plug (wired to the barrier strip, ready to be used, but Keith is not planning on installing a MikroTik in the enclosure) / Mark finished installing the PBP and two antennas; Installed power cable and Keith turned on the Power Cable Switch / Power levels measured, Traco Input 32.6w (27TMX runtime estimate ~>36h), Output 27.5w / Onsite at TLNB: Rec'd $813.00 for W150_1 invoice	T48-3 DBT IMG EML		L17	B58	BC9	S17	V11	20221021
		24	Mo					Some work on WP11P Parts and WP11A Assembly Labor sheets: Header references fixed on WP1 to WP14 and WP1A to WP6-10A	T48-4					20221024
		25	Tu					Wiegmann Invoice Draft, DVS Letterhead Redesigned: Photo of W150 output section 20221008 0956 IMG_3305 PSE PSE Crop.jpg	T48-3 DBT		L17					20221025
		28	Fr					20221011 Report, Photos & Invoice - Wiegmann and Power Cable Assemblies for LSWT.pdf: Emailed to Keith and Mark / Report has new letterhead photo: W150_1 output section (Sa10/8) / W150 Prototype mentioned in Report (prerequisite for LSWT) / Photo in Report: We8/17 Wiegmann Back Panel, Before Testing, Dual Supply System (original design)	T48-3 DBT EML					20221028
2022	Nov	6	Su					Continued work on WP11P Parts list at Section "Wiring" …	T48-4					20221106
		11	Fr					WP11P Parts List mostly filled out [but much work needed to be done on it yet]; WP11A Assembly Labor started ...					20221111
		19	Sa					WP11P and WP11A sheets Completed: WP11P was started on Fr10/14 (~5 weeks ago); Fr10/14 to Sa11/19 Reduced Rate R&D 125.8 Hours					20221119
2022	Dec	22	Th					20221021 Report, Photos & Invoice - LSWT Installation.pdf: Emailed to Keith and Mark	T48-3 DBT EML		L17					20221222

## WP12
WISPers: WP12	A					W150_2 ― 1st Production Run ― As Prototype with Minor Changes including 1 Pole PCS

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L18	B70-71	BC10	S18	V12
2022	Jun	27	Mo					WP11-14	T48-3 EML DKE L17					20220627
	Jul	19	Tu					T48-4 L18	On Order	L					20220719
	Aug	4	Th					[WP12-13] Traco Stock Check, DigiKey/Mouser: No Stock	T48-4					20220804
		10	We					WP11-14	T48-3 IMG LBX L17	Assembly					20220810
		14	Su					[WP12-13] Research, Higher Power Chargers (5 hours): I was still hoping for something better than the SCP-75-12 for the Dual Supply design to obtain full redundancy and absorption/equalize / CONCLUSIONs: Kisae has a lot of promise, Victron too complex and expensive but worth looking at, many others	T48-4	R&D					20220814
		27	Sa					WP11-12	T48-3 SSC DBT EML DKE MOU LIB L17					20220827
		30	Tu					T48-3 L18				BC10			20220830
	Sep	7	We					WP11-13	T48-3 DKE EML LIB					20220907
		13	Tu					WP11-13	T48-3 DKE LIB					20220913
		15	Th					WP11-14	T48-4 DBT EML L18					20220915
	Oct	8	Sa					[WP12-13] Traco Stock Check, SPSE: No Stock; RFQ submitted	T48-4 SPSE					20221008
		9	Su					[WP12-18] TFTP/TODO Decision made to order (5) Tracos: Plan to build (7) W150s; 1st Production Run (2), 2nd Production Run (5) using Tracos now at LWT and ONWT / [Mo12/12: Plans were changed after receiving a 2nd Murata meter, the 2nd Production Run will be Quantity 2 (WP14-WP15) and will not use the Tracos at LWT and ONWT] / Reviewed suppliers and submitted RFQs: SPSE (12) In Stock; DKE, MOU, Allied, TRC and TME No Stock	DWP T48-4 SSC L10 L14					20221009
		12	We					[WP12-18] Stock Checks and Additions to Carts (SPSE, DKE, MOU): Tracos (5); Charger (1); Load Supplies (2); Diode (1); Contactor (2); 30A Battery Cable Fuses (25) / Proposal/Estimate/Advance, W150s for CFS and Spare: WP12 and B70/71 slated for CFS; WP13 continues slated for Spare / Mark and Keith EML and SMS: 20221012 Proposal - CFS Installation.pdf (request for $1600 advance)	T48-4 EML SSC DBT SMS L18			B70-71				20221012
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		14	Fr					WP11-16	T48-4 SPSE SSC EML					V12	20221014
		17	Mo					[WP12-13] Possible TODO for W150_2/3: LED on Power Cable Switch [abandoned Mo10/31 in favor of Voltmeters]	DWP L18					20221017
		20	Th					[WP12-13] Ordered (2) 10x14x0.090" Aluminum sheets from MBTF	T48-4 MBTF					20221020
		21	Fr					[WP12-13] UPS delivered the aluminum					20221021
		22	Sa					[WP12-16] Traco and Aluminum Orders Followups; I thanked Sue for promising $10.41 credit on Th10/20 / Priorities Shifted (TFTP/TODO): Recordkeeping, .ods, invoicing and leftovers from T48-3 take priority; 1st Production Run should not be started until we are caught up (stay the course!)	T48-4 SPSE EML MBTF					20221022
		23	Su					[WP12-13] TODO Priorities Cleanup: Further Battery Charger Research Cancelled; No need to approach Meanwell concerning improved SCP-75-12 Tcomp or a higher powered charger with BTS / After seeing how the stock SCP-75-12 performs at high and low Ts I don't see any reason to try to improve things	DWP					20221023
		24	Mo					[WP12-18] Planning for 1st and 2nd Production Runs and 2023 Price List: 1st Production Run should firm up LIP for the W150s / Issue updated Price List by 1/1/23, including ~10% increase in Professional Rates / When the 2nd Production Run is completed near to the point where the hardware s/b assembled to the backplate I will go to ONWT and LWT to get the (2) Tracos needed to complete the run / [Mo12/12/22: Decision made to produce only (2) in 2nd Production Run; I will not request an advance and the Tracos from ONWT and LWT will not be needed]					20221024
		29	Sa					[WP12-13] Planning for Full Environmental Bench Testing (WP13): W150_3, 27TMX and BTS in Engel; Two runs through the T range / TFTP 5th Generation WISPers: W150N networked version; W150-24 bigger battery bank (to meet 24h runtime target with 100-180w loads); W300-24 two banks of (4) T-105s, larger backplate					20221029
		31	Mo					[WP12-18] TFTP (3) Voltmeters, Traco Disable Input: Aborted idea of using an output LED indicator light in favor of a small digital voltmeter / Also decided to use Traco Disable Input instead of Power Cable Switch; Barrier strip can be 2 poles not 4 / Small switches and voltmeter(s) all mount in backplate which eliminates the Power Cable Switch Assembly alltogether [Mo11/21 postponed R&D for all these ideas until before WP14]	DWP Z21					20221031
	Nov	1	Tu					[WP12-13] Call from Mark: Will CFS be ready soon?: "Within about 2 weeks" (including spare)	T48-3 T48-4 L18					20221101
		4	Fr					[WP12-13] TFTP TODO Are there digital ammeters that don't require an external shunt? Oh! Wouldn't it be nice to show Battery, Traco Input and Output Volts and Amps onboard?	DWP					V12	20221104
		15	Tu					[WP12-13] SMS from Mark: "Is the stuff for Carrollton ready? ..."; What to say to Mark? (still working on WP11A/P, priorities examined) / Met Mark in lobby of USB, rec'd $959 (Wiegmann prep for LSWT), discussed scheduling for CFS ("After Thanksgiving"); [Mark relayed this to Keith who had asked for the status update]	T48-4 T48-3 SMS L18					20221115
		18	Fr					[WP12-13] SMS from/to Keith: "Will that power supply be done the week after thanksgiving"; "Yes, Keith, that's what the schedule looks like" (still working on WP11A/P) / SMS from Keith "Awesome"	T48-4 SMS L18					20221118
		21	Mo					[WP12-13] Started WP12-13P and WP12-13A sheets and recorded data for already completed work / Design Changes for 1st Production Run, Voltmeter Modules Availability Research, CONCLUSIONs: / Voltmeter will not mount directly on backplate, the Meter Assembly s/b built on C-Channel; Murata DMR20-10-DCM-R-C looks good, but I need time for more R&D, requested sample / I don't have time now to introduce metering in the 1st Production Run, further development postponed until after WP13 Spare is ready	T48-4 DWP Z21					20221121
		22	Tu					[WP12-13] Other Design Changes for 1st Production Run: Minor changes only (R&D postponed on Meter Assembly and Traco Disable Switch) / Backplate Feet and Mounting Screws specified (DKE, BDC); Battery cable fuses 25A->30A; Use existing PCS Assemblies but only wire up one pole					20221122
		23	We					[WP12-13] Finished Design Changes for 1st Production Run; Working on planning orders (WP12-13P and WP12-13A) / Started Assembly (backplate painted); We may get a sample Murata DMR20-10-DCM-R-C for the Meter Assembly (2nd Production Run, Bill Beets EMLs, MO Murata Rep)	T48-4 DWP EML Z21	Assembly	L0					20221123
		25	Fr					[WP12-13] Production Run #1 Orders Completed: / BDC: Hardware / DKE: Diode (WP13), Load Supplies (S18/19 WP12/13), Bumper Feet, 5/16" Ring Connectors, 1/4" Shrink, Zip Ties, Fuse Holders, 30A Fuses, #16 Stranded Red / MOU: Charger (BC11 WP13), Contactors (WP12/13) / PTD: Yellow labels and additional stock on commonly used sizes	T48-4 EML SSC BDC DKE MOU PTD					S18		20221125
		26	Sa					[WP12-13] Design Changes, Template: Eliminated (4) zip tie holes on right side [T48-3 Sa10/1]; 20221126 W150 Layout Template #2, Modified, Production Run #1; IMG_3391 PSE.jpg	T48-4 IMG DBT					20221126
		28	Mo					[WP12-13] SMS from Mark: "Hey, is that all that stuff ready we're going to go to Carrollton tomorrow if it is call me let me know. Thanks." ...	T48-4 SMS L18					20221128
		29	Tu					[WP12-13] ... Mark and Keith: Apologies, can't deliver CFS today, orders delayed; Keith disgruntled "So ... We have been waiting all this time for this"; Mark proposes We12/7 installation at CFS / DKE Marketplace items shipped today (NTE/Remington), no ETA yet / DKE, PTD and MOU orders received: S18/19, BC11 and many other parts	T48-4 DKE PTD MOU L18					S18		20221129
		30	We					[WP12-13] DKE Marketplace orders tracking checked, Remington (#16 Red) ETA Fr12/2 (USPS), NTE (fuses/holders) ETA Mo12/5 (UPS); BDC order received / We12/7 installation does NOT look feasible unless we substitute the wire/fuses/holders	T48-4 DKE BDC					20221130
	Dec	1	Th					[WP12-13] DKE main order (delivered by Fedex Tu11/29, includes S18/19 and many other parts): Labeled, invoice scanned to LIB, filed / PTD order (delivered by USPS Tu11/29): Labeled, invoice filed / MOU order (delivered by UPS Tu11/29, includes BC11 and contactors); Labeled, invoice scanned to LIB, filed / BDC order (delivered by UPS Tu11/29): Labeled, invoice filed / TFTP TODO Priorities Shifts: Will try to make We12/7 install, but will have to substitute as needed on wire/fuses/holders and postpone all extra .ods work (daily updates)	T48-4 LBX SSC LIB DKE PTD MOU BDC					S18		20221201
		5	Mo					[WP12-13] Backplates finished; Hardware Assembly started	T48-4 L18					20221205
		6	Tu					[WP12-13] Hardware Assembly finished	T48-4					20221206
		7	We					[WP12-16] Wiring and Cabling started; Sager $10.41 credit "has been processed"	T48-4 SSC EML SPSE L18					20221207
		8	Th					[WP12-13] Shrink Tubing Cutting Block fabricated, photo sent to Tom McConnell [see T48-4 Fr12/9 for further communications with Tom]	T48-4 LBX IMG SMS L18					20221208
		9	Fr					[WP12-16] Sager credited $10.41 x 2; I'm not going to say anything about this, they may discover the error and fix it later	T48-4 SMS SPSE					20221209
		13	Tu					Designed and applied W150 Traco Trim R 15.15K 52.8V 0.35.lbx; WP12 Wiring and Cabling finished (WP13 postponed); Improvement to Engel setup; Started WP12 Configuration and Testing	T48-4 LBX PLN WP13 Z0				BC10	S18	V12	20221213
		14	We					As per WP12-13A: Configuration and Testing finished; Labels finished; Ready to be installed at CFS / SMS to Mark and Keith "W150 #2 is ready. I can go to CFS tomorrow if that works for you."; Mark scheduled the installation for We12/21 because "It's too cold to go over there this week ..."	T48-4 PLN L18 Z0	Install	Subaru					20221214
		20	Tu					SMS from Mark: Too cold tomorrow; Installation rescheduled for We12/28 which looks to be much nicer weather	T48-4 SMS L18					20221220
		25	Su					[WP12-16] As per WP12-13A, Procurement > Orders Followup FINISHED: Sager $10.41 double credit accepted/applied (reduced S&H for C8, Fr10/14 T48-4, WISPers and Converters Summaries)	T48-4 SPSE					V12	20221225
		27	Tu					Prep for installation at CFS: W150 mounting stud bolt sets prepared	T48-4 L18					20221227
		28	We		12:00		14:00	Onsite at CFS: Keith had reserved only about 12" space at the bottom of the enclosure, but he angrily removed the bottom shelf to provide almost 24" / Installed W150_2, vertical on left side of enclosure (side panel is removeable); T-105s installed in bottom front (with just enough space above to get your head above the cells); Photos / No loads could be attached, Keith plans to come back "maybe next week" to move all loads to the W150 (some now on AC, some now on WP1/B26) / Power Cable stripped but not attached (ends insulated, it is connected to the PBPs at the top) / There are two MikroTiks in the enclosure, I told Keith what he needs to do to the adapters and how to hook them up to the W150; Did not measure power levels (Traco idle) / Did not check to be sure the W150 is charging (all I know is that Keith plugged it into the AC power strip at the back top of the enclosure)	T48-4 IMG	Applied	L18	B70-71	BC10	S18	V12	20221228
2023	Jan	10	Tu					TFTP TODO: I gave some erroneous advice to Keith when I was onsite We12/28/22 (how to power the Netonix if he wants to keep it at the site)	T48-4		L18					20230110
		14	Sa					[WP12-13] R&D TODO: Load Supply Output Cables Option (WP13 can be used to test this option, offer cables to Keith); W200 Generation (no Traco); WP2 Spare (make it available)	DWP WP2					20230114
		30	Mo					1st Production Run Completed: (WP13 Completed); WP12-13 Invoice Date [emailed to Keith and Mark We2/8]	T48-4 WP13	Sold			BC10	S18	V12	20230130
	Feb	4	Sa					[WP12-13] WP12-13A/P sheets completed and protected	T48-4					20230204
		8	We					[WP12-13] Invoice EML to Keith and Mark: / 20230130 Report & Invoice - W150_2 and W150_3 for CFS and Spare.pdf	T48-4 DBT EML L17 WP14-15		L18					20230208
	Mar	3	Fr					Invoice EML to Keith and Mark: 20221229 Report & Invoice - CFS Installation (W150_2).pdf	T48-4 SMS DBT EML		L18					20230303

## WP13
WISPers: WP13	A					W150_3 ― 1st Production Run ― As Prototype with Minor Changes including 1 Pole PCS

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L		BC11	S19	V13
2022	Jun	27	Mo					WP11-14	T48-3 EML DKE L17					20220627
	Jul	19	Tu					T48-4 L18		L					20220719
	Aug	4	Th					WP12-13	T48-4					20220804
		10	We					WP11-14	T48-3 IMG LBX L17	Assembly					20220810
		14	Su					WP12-13	T48-4	R&D					20220814
	Sep	7	We					WP11-13	T48-3 DKE EML LIB					20220907
		13	Tu					WP11-13	T48-3 DKE LIB					20220913
		15	Th					WP11-14	T48-4 DBT EML L18					20220915
	Oct	8	Sa					WP12-13	T48-4 SPSE					20221008
		9	Su					WP12-18	DWP T48-4 SSC L10 L14					20221009
		12	We					WP12-13	T48-4 EML SSC DBT SMS L18					20221012
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17	On Order					20221013
		14	Fr					WP11-16	T48-4 SPSE SSC EML	R&D					V13	20221014
		17	Mo					WP12-13	DWP L18					20221017
		20	Th					T48-4 MBTF					20221020
		21	Fr					20221021
		22	Sa					WP12-16	T48-4 SPSE EML MBTF					20221022
		23	Su					WP12-13	DWP					20221023
		24	Mo					WP12-18					20221024
		29	Sa					WP12-13					20221029
		31	Mo					WP12-18					20221031
	Nov	1	Tu					WP12-13	T48-3 T48-4 L18					20221101
		4	Fr					DWP					V13	20221104
		15	Tu					T48-4 T48-3 SMS L18					20221115
		18	Fr					T48-4 SMS L18					20221118
		21	Mo					T48-4 DWP					20221121
		22	Tu					20221122
		23	We					T48-4 DWP EML	Assembly	L0					20221123
		25	Fr					T48-4 EML SSC BDC DKE MOU PTD				BC11	S19		20221125
		26	Sa					T48-4 IMG DBT					20221126
		28	Mo					T48-4 SMS L18					20221128
		29	Tu					T48-4 DKE PTD MOU L18				BC11	S19		20221129
		30	We					T48-4 DKE BDC					20221130
	Dec	1	Th					T48-4 LBX SSC LIB DKE PTD MOU BDC				BC11	S19		20221201
		5	Mo					T48-4					20221205
		6	Tu					20221206
		7	We					WP12-16	T48-4 SSC EML SPSE					20221207
		8	Th					WP12-13	T48-4 LBX IMG SMS					20221208
		9	Fr					WP12-16	T48-4 SMS SPSE					20221209
		13	Tu					(WP12 Wiring and Cabling finished); WP13 not finished, postponed, priority is to install WP12 at CFS	T48-4 LBX PLN WP12					20221213
		16	Fr					[WP13-18] TFTP Meter Assembly on Spare? [NO]: I could fabricate the prototype Meter Assembly and install it on WP13; [Su12/18 in reviewing this idea I think it is best to abandon it]	DWP					20221216
		25	Su					WP12-16	T48-4 SPSE					V13	20221225
		28	We		12:00		14:00	[WP13-18] Onsite at CFS to install WP12: Keith read the W150 Operating Range label and questioned what will happen below the "rated" 4degF / TODO for WP13 onwards: There's really no reason not to state -20⁰C as the bottom end; Look up specs on Charger, Load Supply, Contactor and Traco; We might state even lower than -20⁰C	T48-4 L18					20221228
2023	Jan	7	Sa					As per WP12-13A: Wiring and Cabling finished (BTS for BC11); Started Configuration and Testing (BC11)	T48-4 PLN Z0				BC11			20230107
		8	Su					As per WP12-13A Configuration and Testing: BC11 Burn-In completed (17.1h); S19 Configured, 13.729vI / V13 output 52.720vI [somewhat low result kicked off a 4 day R&D project, V13 Trim R assembly replaced Tu1/10]; Started 180wI Burn-In (S19/V13); BTS removed from Engel					S19	V13	20230108
		9	Mo					As per WP12-13A Configuration and Testing: S19/V13 Burn-In completed (16.2h) / Started investigations into Traco Trim R assemblies and output results: Discovered obvious dependency on Traco temperature	T48-4 PLN SSC LIB	R&D					20230109
		10	Tu					[WP13-18] Traco Trim R Investigations Continued: New Trim R Assembly labels (photo); Fabricated and installed solitary 15.0K 1% on V13 (14.96 KΩF, 52.84 VTS, 52.765vI)	T48-4 LBX IMG SSC LIB					20230110
		11	We					[WP13-18] Traco Trim R Investigations Continued: WP14 onwards should use solitary 15.0K	T48-4 PLN LIB					20230111
		12	Th					[WP13-18] Traco Trim R Investigations Concluded: WP12-13A/P edited to reflect what was learned; TODO for 2nd Production Run onwards	T48-4	Assembly					20230112
		13	Fr					R&D TODO: Voltage Reference Calibrations; W150 Full Environmental Testing (We don't need a 27TMX to do what needs to be done with WP13); Measure Engel Effective Cooling Power	DWP Z17 S2 Z0					20230113
		14	Sa					WP12-13	DWP WP2					20230114
		30	Mo					[WP13-18] 1st Production Run Completed: / WP13 Configuration, Testing and Labels completed as per WP12-13A; Modified/new labels designed and applied to WP13; WP12-13 Invoice Date [emailed to Keith and Mark We2/8]	T48-4 LBX SSC WP12	Sold	L		BC11	S19	V13	20230130
		31	Tu					Photo of WP13	T48-4 IMG					20230131
	Feb	4	Sa					WP12-13	T48-4					20230204
		8	We					T48-4 DBT EML L17 WP14-15					20230208
		12	Su					[Design Changes for 2nd Production Run]: WP13, ITECH and an old switch used to test using the Traco Ctrl pin to shut off the output by grounding to RSP-V (Traco -Vin); Works as expected	DWP WP14-15					V13	20230212

## WP14
WISPers: WP14	A					W150_4 ― 2nd Production Run ― Major Changes including elimination of PCS and addition of Meter Assembly

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D	L		BC12	S20	V14	Z21
2022	Jun	27	Mo					WP11-14	T48-3 EML DKE L17					20220627
2022	Jul	19	Tu					T48-4 L18		L					20220719
2022	Aug	10	We					T48-3 IMG LBX L17	Assembly					20220810
2022	Sep	15	Th					WP11-14	T48-4 DBT EML L18	R&D					20220915
2022	Oct	9	Su					WP12-18	DWP T48-4 SSC L10 L14					20221009
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		14	Fr					WP11-16	T48-4 SPSE SSC EML					V14		20221014
		22	Sa					WP12-16	T48-4 SPSE EML MBTF					20221022
		24	Mo					WP12-18	DWP					20221024
		31	Mo					WP12-18					20221031
2022	Dec	2	Fr					[WP14-18] Free Meter Sample Received: Planning on incorporating these into the Meter Assemblies for the 2nd Production Run onwards	DWP EML					Z21	20221202
		6	Tu					[WP14-18] EML from Bill Beets, who wanted to confirm that I had received the sample; Z21 tested on BK and ITECH, photos; EML to Bill Beets with photos	DWP EML IMG					20221206
		7	We					[WP14-18] Bill informed me that a 2nd Sample was being shipped to me (Z22 slated for WP15) / Design Change for 2nd Production Run: No Tapped Holes, KEPS Nuts	DWP EML					20221207
				WP12-16	T48-4 SSC EML SPSE					20221207
		8	Th					[WP14-18] 2nd Free Meter Sample Received: Delivered by UPS, opened and inspected (Z22 slated for WP15)	DWP					Z21	20221208
		9	Fr					WP12-16	T48-4 SMS SPSE					20221209
		12	Mo					[WP14-18] TFTPs For 2nd Production Run / Quantity=2: We have 2 MuRata meters and 3 Tracos; I think I can swing the finances (~$500) to do a run of (2) and not approach TurboNet for an advance / No More Advances: If at all possible do not approach TurboNet for an advance (big benefit, absolutely no obligation or time pressure from them)	DWP					20221212
		16	Fr					WP13-18					20221216
		18	Su					[WP14-15] Murata Meters WP14-15A Procurement Recordkeeping: Meters will be used in the 2nd Production Run so procurement of them is ASSEMBLY LABOR / Murata > 20221218 Datasheet DMR20-10-DCM-R-C - dmr20-10-dcm.pdf; Z21/22 Summary and History sheets created beginning with Mo10/31	DWP LIB					Z21	20221218
		19	Mo					[WP14-15] Murata Meters WP14-15A Procurement Recordkeeping: Designed, printed and applied W150 Meter Inventory Sticker 0.23.lbx; Z21/22 History sheets filled out	DWP LBX					20221219
		22	Th					[WP14-18] 20221021 Report, Photos & Invoice - LSWT Installation.pdf: Emailed to Keith and Mark / Murata meters and displayed voltages (13.5, 13.7 and 52.8v) mentioned in report with photo of Tu12/6 testing of Z21	T48-3 DBT EML L17					20221222
		25	Su					WP12-16	T48-4 SPSE					V14		20221225
		28	We		12:00		14:00	WP13-18	T48-4 L18					20221228
2023	Jan	10	Tu					WP13-18	T48-4 LBX IMG SSC LIB					V14		20230110
		11	We					T48-4 PLN LIB					20230111
		12	Th					T48-4					20230112
		23	Mo					[WP14-18] EML from Bill Beets: "Did you end up approving DMR20-10-DCM-R-C for use in your product?"	DWP EML					Z21	20230123
		29	Su					[WP14-18] EML reply to Bill Beets: / "Two prototypes are being built with the two meters we received. It may be a while before the final decision is made for production, but it looks good for now."					20230129
		30	Mo					WP13-18	T48-4 LBX SSC WP12					20230130
2023	Feb	8	We					[WP14-15] Invoice EML to Keith and Mark: 20230130 Report & Invoice - W150_2 and W150_3 for CFS and Spare.pdf; 2nd Production Run mentioned in report (meter display)	T48-4 DBT EML WP12-13					20230208
		10	Fr					[WP14-15] WP14-15P/A sheets created and initialized; Started considering Design Changes for 2nd Production Run	DWP					20230210
		11	Sa					[WP14-15] ... Design Changes: Meter Switch DP3T: Considered slide switches, abandoned (SSC, won't work, must be a toggle switch) / Selected NKK Switches M2044SS1W01; Printed and notated SSC of M2044 Connected Terminals & Schematic; Considered connections (7) and wires coming into assembly (5)	DWP SSC					20230211
		12	Su					[WP14-15] ... Design Changes: Traco Output Switch SPST: Bench tested idea with WP13 (works as expected); Selected NKK Switches M2011S2S1W01 [changed to larger toggle Sa2/18] / Barrier Strip: 3 position, single row, bottom termination solder turrets (best from user standpoint); Selected Molex 0387203803 / TFTP and TODO on the aluminum base for the Meter Assembly: Free thinking, maybe a flat plate design or directly on backplate?	DWP LIB WP13					20230212
		13	Mo					[WP14-15] ... Design Changes: Paradigm Shift to No Meter Assembly (place the components in the backplate); Selected 1" feet, Essentra Components SOF-15126 / 3 feet instead of 5, moved out to 1/2" from the edge (top center, lower left and right corners); Mounting holes moved down 1/2" (maintains 12" separation)	DWP LIB					20230213
		14	Tu					[WP14-15] ... Design Changes: Conceptual/visualization drawings for backplate changes; New labels designed for Meter and Output / Late Night Thoughts: Concerned about how to protect the wires and components on the underside of the backplate	DWP LBX					20230214
		15	We					[WP14-15] ... Design Changes: Paradigm Shift again to Meter/Output Plate and Assembly; TFTP Listed advantages of Raised Meter Assembly design / Eliminated C-channel approach (required shape and size is not available); Researched PCB Standoffs and selected RAF Electronic Hardware 4542-632-AL	DWP LIB					20230215
		16	Th					[WP14-15] ... Design Changes: Backplate Feet locations considered and settled on four feet 3/8" from edges (1/2" high feet, backplate mounting holes as per WP11-13) / Label "Do Not Overtighten" eliminated because the top and bottom feet are adjacent to the mounting holes / Chat with BoltDepot.com to confirm specifications on K-Lock (KEPS) nuts; Started drawing "Bottom Half of W150"; Designed new label for FG Post; TFTP "W150 LVD" (WP16 onwards)	DWP SSC EML LBX WP16-18					20230216
		18	Sa					[WP14-15] ... Design Changes: Optimized locations and designed new labels here and there / "Finished" drawing "Bottom Half of W150"; 20230218 W150 BackPlate, Bottom Half, Visualization Drawing, WP14+ Scan.jpg / Changed specification for Output Switch: Bigger toggle (same 10.5mm actuator as Meter Switch); NKK Switches M2011SS1W01	DWP LBX SSC DBD					20230218
		19	Su					[WP14-15] ... Design Changes: Labels improved again and applied to drawing "Bottom Half of W150" (scanned, clobbered DBD version made yesterday) / WP14-15P/A: Reviewed Components and updated pricing; Load Supplies look like they're going to be hard to get (DKE & MOU No Stock) / Looked for ATM Fuse Holders with a clip to hold a spare fuse: NONE FOUND / Reconsidered blind mount screws used for Charger and Load Supply (Backplate 0.080" not 0.090"): No changes needed, previously used 3mm and 4mm parts will work AOK / TFTP TODO: Use #18 solid on entire Meter Assembly; Pico [or PIgtail] fuse on Red #18 solid at RSP +V					20230219
		20	Mo					[WP14-15] ... Design Changes: Meter Plate Standoffs reconsidered (no change, see choice made We2/15) / PARTS sheets NEW SCHEME implemented (WP11P, WP12-13P, WP14-15P): Grouped lines structure reformatted/recolored for visibility and ease of use / Meter Assembly Fuse: Ideal specification "2-5A Slow Blow, 30VDC, Pigtail or Pico"; Found (55) small glass fuses from the old days that are perfectly acceptable	DWP					20230220
		21	Tu					[WP14-15] ... Design Changes: / WP14-15P/A Hardware: Contactor (eliminated all #6 flat washers); Traco (eliminated split washers, KEPS underneath); Barrier Strip (new item #6-32x3/4" screws with KEPS underneath)					20230221
		22	We					[WP14-15] ... Design Changes: Considered and rejected idea of using 1/4" bolt for FG Post (instead of 5/16"); WP14-15P/A Hardware PARTS update finished					20230222
		23	Th					[WP14-15] ... Design Changes, Started WP14-15P/A Wire PARTS Review: #18 Solid for entire Meter Assembly; Examined old stocks of thermostat wire, colors chosen / TFTP and Quick Test: The #18 Solid doesn't "pair" well with the #12 Solid Brown on RSP -V [will consider and test the best approach tomorrow]					20230223
		24	Fr					[WP14-15] ... Design Changes, WP14-15P/A Wire PARTS: Added fuse to #18 Solid Brown from RSP -V to Meter Assembly; Considered LSOC option and attachments to RSP / Ideal RSP Connection Configuration, WP14 Onwards: Center +/-V connections not used except if LSOC option; Traco +Vin #12 Solid (not Stranded); Contactor connected to Diode Anode					20230224
		25	Sa					[WP14-15] ... Design Changes: WP14-15P/A Wire PARTS review finished; Started review of Miscellaneous PARTS: Ring connector for Barrier Strip Gnd on the mounting screw NOT NEEDED / (a single piece of #18 Solid Bare can be wrapped around the screw under the KEPS and continue past the Barrier Strip to the Meter Switch) / Eliminated 5/16" Ring Connectors for #14-16: Connections to FG Post for AC input cord and Charger B- eliminated by attaching them to Charger AC Gnd input screw / Simpler assembly, but be sure to apply Penatrox on the blind mounting screws for Charger and Load Supply as they complete the connection to the backplate / Now only (2) Ring Connectors on FG Post (Battery Negative and Contactor Top Left NC Contact)					20230225
		26	Su					[WP14-15] ... Design Changes: WP14-15P/A Procedure Specifications Sections restructured (new codes); TFTP Volume Pricing and Sales Structure for the W150s (for DNT TODO) / Data Vision Services sign from Ft. Collins retrieved from Tom McConnell's truck					20230226
		27	Mo					[WP14-15] ... Design Changes: WP14-15P/A #18 Wire PARTS reordered to align with the overall assembly procedure order by meter assembly connections as I think of them in my head and as they are physically located; Continued reordering and checking subcount titles on PARTS for all ASSEMBLY Procedure Specifications, drafting titles and procedures for [HA] and [WC] for the Meter/Output Assembly					20230227
		28	Tu					[WP14-15] ... Design Changes: WP14-15P/A Miscellaneous and Labels PARTS review completed; TFTP The PARTS and ASSEMBLY sheets should be worked up as a relational database					20230228
2023	Mar	1	We					[WP14-15] Status: Design Changes for WP14-15: All the desired design changes have been considered and pre-planned, BUT ... / Listed remaining work and conditions for being ready to order parts and begin assembly (weeks to go yet) / Good stopping point for now, I need to work on the Subaru as I hit a deer and the front end is mangled					20230301
		7	Tu					[WP14-15] R&D TFTP: Go Ahead and Build (2) W150s; Depression ends when I realized it was time to order parts and build them; Found hole saw and circle cutter for Meter hole		Assembly					20230307
		8	We					[WP14-15] [P] Plan/Place: Orders Placed; Procedure Specification improvements	DWP MBTF SPSE MOU DKE BDC				BC12	S20			20230308
		9	Th					[WP14-15] [P] Track/Receive: All orders have shipped; MBTF aluminum received; Procedure Specification improvements	DWP MBTF					20230309
		10	Fr					[WP14-15] [P] Track/Receive: BDC, SPSE and MOU orders received; USB/SPF total spent We3/8 $505.28	DWP MBTF SPSE MOU DKE BDC				BC12	S20			20230310
		11	Sa					[WP14-15] [P] Receive: Recordkeeping mostly complete (waiting DKE ETA Mo3/13) / R&D Meter: Punch tools $$$, 1.210" not in electrician's punch set (will have to use boring tool I found); Assembly Fuses ideal specification changed to 0.25A (not 2-5A)	DWP DKE SPSE MOU LBX SSC LIB					20230311
		12	Su					[WP14-15] R&D: Struggled with coming up with an Improved System for LIB Invoice Scans and Datasheets (filenames, procedures) [abandoned/simplified Mo3/13]	DWP SSC LIB					20230312
		13	Mo					[WP14-15] R&D: Simplified System for LIB Invoice Scans and Datasheets (WP14-15A changes); Tool/Supplies Preparation; WP14-15P/A Changes, [P] section simplified, Diode wiring / [P] Receive: DKE order received, [P]rocurement is COMPLETE (all orders have been received and recordkeeping is done)	DWP LIB DKE	R&D					20230313
		14	Tu					[WP14-15] Looked for software to produce working drawings for Scribing/Milling (and electrical schematics); Selected LibreCAD (and QElectroCAD) / Assembly Schedule: I do not want to start [PS] until I have the dimensioned drawings; Weather is cold (not good for painting) / There's a few days of Computer Resource Improvements; It will probably be a few days or a week before continuing assembly [sic]	DWP					20230314
		25	Sa					[WP14-15] Many computer resource improvements in the past 10 days (abandoned LibreCAD and installed QCAD); Started draft W150 Backplate WP14+.dxf	DWP DBD					20230325
	Apr	4	Tu					[WP14-15] EML Rec'd from Bill Beets (Murata rep): "Was DMR20-10-DCM-R-C approved?" [response postponed until We4/12]	DWP EML					Z21	20230404
		5	We					[WP14-15] Many learning experiences with QCAD in the past 10 days (W150 Backplate WP14+.dxf almost completed); Started draft W150 Meter Plate WP14+.dxf	DWP DBD					20230405
		12	We					[WP14-15] Drawings for Scribing/Milling Glued to Cardboard (finished and ready for assembly): 20230412 W150 Backplate WP14+.dxf; 20230412 W150 Meter Plate WP14+.dxf / Reply to Bill Beets [see Tu4/4]: Mentioned how I was planning on doing the meter holes (will not use $$$ punch tool); Attached SSC of the meter area of the Meter Plate drawing	DWP DBD / SSC EML					Z21	20230412
		13	Th					[WP14-15] 1-3/16" Hole Saw received yesterday may be OK for meter hole (seems small); EML from Bill Beets; Mill Jigs TFTP and TODO	DWP EML					20230413
		24	Mo					[WP14-15] Mill Jigs (Postponed/Abandoned): Since Th4/13 I worked daily on seeing if I could come up with some improved locating/aligning Mill Jigs for the Clausing Mill table that would make milling the Backplates and Meter plates easier or more efficient; There was a lot learned about QCAD and the Clausing, but in the end it became apparent that these hopes were "Pie in the Sky," not necessary and too complex until (or if) we have orders to justify making more than ~10 plates at a time / QCAD files for Mill Jigs ideas/trials/experiments in LIB > Clausing Mill: / 20230417^15 [DWP] Clausing Mill Table Slot Locators (abandoned).dxf / 20230423^17 [DWP] Clausing Mill Table Edge Locator Clamps (incomplete, postponed, abandoned).dxf / TFTP and Experiments: How to clamp a stack of Meter Plates into relative alignment by using the same technique as I used for the Backplates in the 1st Production Run / The Meter Plates can be milled by starting with aligning and clamping them in the small 90⁰ vise; THEREFORE will move on to preparing to resume Assembly without any new jigs	DWP LIB					20230424
	May	25	Th					[WP14-15] On Su5/20 after almost a month of other concerns I returned to finishing this production run: / Long lingering changes to the Assembly Procedures: Edits/drafts for [HA], [WC], [CT] and [CM] to incorporate KEPS, Meter/Output Assembly and other miscellaneous changes / Today: [PS] Paint Aluminum Plates; [CM] Clean and Oil	DWP					20230525
		26	Fr					[WP14-15] [PS] Scribe; [CM] Prep	DWP					20230526
	Jun	2	Fr					[WP14-15] On Mo5/29 I encountered another Paradigm Shift: "Split" the run and produce Base, X, M and XM variants as needed / WP14=W150XM Flagship Model; WP15=W150 Base variant (with extra X Contactor and M Meter/Output assemblies bagged for immediate installation on a W150)	DWP SSC WS					20230602

## WP15
WISPers: WP15	A					W150_5 ― 2nd Production Run ― Major Changes including elimination of PCS and addition of Meter Assembly

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D	L		BC13	S21	V15	Z22
2022	Oct	9	Su					WP12-18	DWP T48-4 SSC L10 L14	R&D					20221009
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		14	Fr					WP11-16	T48-4 SPSE SSC EML					V15		20221014
		22	Sa					WP12-16	T48-4 SPSE EML MBTF					20221022
		24	Mo					WP12-18	DWP		L					20221024
		31	Mo					WP12-18					20221031
2022	Dec	2	Fr					WP14-18	DWP EML					20221202
		6	Tu					DWP EML IMG					20221206
		7	We					DWP EML					Z22	20221207
				WP12-16	T48-4 SSC EML SPSE					20221207
		8	Th					WP14-18	DWP					Z22	20221208
		9	Fr					WP12-16	T48-4 SMS SPSE					20221209
		12	Mo					WP14-18	DWP					20221212
		16	Fr					WP13-18					20221216
		18	Su					WP14-15	DWP LIB					Z22	20221218
		19	Mo					DWP LBX					20221219
		22	Th					WP14-18	T48-3 DBT EML					20221222
		25	Su					WP12-16	T48-4 SPSE					V15		20221225
		28	We		12:00		14:00	WP13-18	T48-4 L18					20221228
2023	Jan	10	Tu					WP13-18	T48-4 LBX IMG SSC LIB					V15		20230110
		11	We					T48-4 PLN LIB					20230111
		12	Th					T48-4					20230112
		23	Mo					WP14-18	DWP EML					Z22	20230123
		29	Su					20230129
		30	Mo					WP13-18	T48-4 LBX SSC WP12					20230130
2023	Feb	8	We					WP14-15	T48-4 DBT EML WP12-13					20230208
		10	Fr					DWP					20230210
		11	Sa					DWP SSC					20230211
		12	Su					DWP LIB WP13					20230212
		13	Mo					DWP LIB					20230213
		14	Tu					DWP LBX					20230214
		15	We					DWP LIB					20230215
		16	Th					DWP SSC EML LBX WP16-18					20230216
		18	Sa					DWP LBX SSC DBD					20230218
		19	Su					20230219
		20	Mo					DWP					20230220
		21	Tu					20230221
		22	We					20230222
		23	Th					20230223
		24	Fr					20230224
		25	Sa					20230225
		26	Su					20230226
		27	Mo					20230227
		28	Tu					20230228
2023	Mar	1	We					20230301
		7	Tu					Assembly					20230307
		8	We					DWP MBTF SPSE MOU DKE BDC				BC13	S21			20230308
		9	Th					DWP MBTF					20230309
		10	Fr					DWP MBTF SPSE MOU DKE BDC				BC13	S21			20230310
		11	Sa					DWP DKE SPSE MOU LBX SSC LIB					20230311
		12	Su					DWP SSC LIB					20230312
		13	Mo					DWP LIB DKE	R&D					20230313
		14	Tu					DWP					20230314
		25	Sa					DWP DBD					20230325
	Apr	4	Tu					DWP EML					Z22	20230404
		5	We					DWP DBD					20230405
		12	We					DWP DBD SSC EML					Z22	20230412
		13	Th					DWP EML					20230413
		24	Mo					DWP LIB					20230424
	May	25	Th					DWP					20230525
		26	Fr					DWP					20230526
	Jun	2	Fr					DWP SSC WS					20230602

## WP16
WISPers: WP16	A					W150_6 ― 3rd Production Run ― To Be Determined

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D	L				V16
2022	Oct	9	Su					WP12-18	DWP T48-4 SSC L10 L14	R&D					20221009
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		14	Fr					WP11-16	T48-4 SPSE SSC EML					V16		20221014
		22	Sa					WP12-16	T48-4 SPSE EML MBTF					20221022
		24	Mo					WP12-18	DWP		L					20221024
		31	Mo					WP12-18					20221031
	Dec	2	Fr					WP14-18	DWP EML					20221202
		6	Tu					DWP EML IMG					20221206
		7	We					DWP EML					20221207
				WP12-16	T48-4 SSC EML SPSE					20221207
		8	Th					WP14-18	DWP					20221208
		9	Fr					WP12-16	T48-4 SMS SPSE					20221209
		12	Mo					WP14-18	DWP					20221212
		16	Fr					WP13-18					20221216
		22	Th					WP14-18	T48-3 DBT EML					20221222
		25	Su					WP12-16	T48-4 SPSE					V16		20221225
		28	We		12:00		14:00	WP13-18	T48-4 L18					20221228
2023	Jan	10	Tu					WP13-18	T48-4 LBX IMG SSC LIB					V16		20230110
		11	We					T48-4 PLN LIB					20230111
		12	Th					T48-4					20230112
		23	Mo					WP14-18	DWP EML					20230123
		29	Su					20230129
		30	Mo					WP13-18	T48-4 LBX SSC WP12					20230130
	Feb	16	Th					[WP16-18] TFTP W150 LVD (Low Voltage Disable): Possible/option/improvement for WP16 onwards; Can add to Meter/Output Assembly / Provides some discharge and freeze protection, SLA and FLA batteries can be prevented from discharging more than ~50%	DWP WP14-15					20230216

## WP17
WISPers: WP17	A					W150_7 ― 3rd Production Run ― To Be Determined

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D
2022	Oct	9	Su					WP12-18	DWP T48-4 SSC L10 L14	R&D					20221009
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		24	Mo					WP12-18	DWP					20221024
		31	Mo					WP12-18					20221031
	Dec	2	Fr					WP14-18	DWP EML					20221202
		6	Tu					DWP EML IMG					20221206
		7	We					DWP EML					20221207
		8	Th					WP14-18	DWP					20221208
		12	Mo					WP14-18					20221212
		16	Fr					WP13-18					20221216
		22	Th					WP14-18	T48-3 DBT EML					20221222
		28	We		12:00		14:00	WP13-18	T48-4 L18					20221228
2023	Jan	10	Tu					WP13-18	T48-4 LBX IMG SSC LIB					20230110
		11	We					T48-4 PLN LIB					20230111
		12	Th					T48-4					20230112
		23	Mo					WP14-18	DWP EML					20230123
		29	Su					20230129
		30	Mo					WP13-18	T48-4 LBX SSC WP12					20230130
	Feb	16	Th					WP16-18	DWP WP14-15					20230216

## WP18
WISPers: WP18	A					W150_8 ― 3rd Production Run ― To Be Determined

Date/Time CST/CDT					Description	Other Sources	Status	Location	Battery	Charger	Load Supply	DC-DC	Meter
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D
2022	Oct	9	Su					WP12-18	DWP T48-4 SSC L10 L14	R&D					20221009
		13	Th					WP11-18	T48-3 T48-4 SMS DWP SMS L17					20221013
		24	Mo					WP12-18	DWP					20221024
		31	Mo					WP12-18					20221031
	Dec	2	Fr					WP14-18	DWP EML					20221202
		6	Tu					DWP EML IMG					20221206
		7	We					DWP EML					20221207
		8	Th					WP14-18	DWP					20221208
		12	Mo					WP14-18					20221212
		16	Fr					WP13-18					20221216
		22	Th					WP14-18	T48-3 DBT EML					20221222
		28	We		12:00		14:00	WP13-18	T48-4 L18					20221228
2023	Jan	10	Tu					WP13-18	T48-4 LBX IMG SSC LIB					20230110
		11	We					T48-4 PLN LIB					20230111
		12	Th					T48-4					20230112
		23	Mo					WP14-18	DWP EML					20230123
		29	Su					20230129
		30	Mo					WP13-18	T48-4 LBX SSC WP12					20230130
	Feb	16	Th					WP16-18	DWP WP14-15					20230216

## Z0
Miscellaneous: Z0	A					E_1: Engel MT35F-U1

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L
2011	Aug	?					Download 'ENGELUSA2010Brochure'	LIB	Research		201108?
		29					Ordered from Engel, 900 Jupiter Park Drive, Jupiter, FL 33458; $868.00 + $51.00 S&H; Invoice in Library	EML LIB	On Order		20110829
	Sep	1					Approximate date received		Available	204 W 3rd ST	20110901
		26					I'm in Kansas, on my way to Colorado to see Dad; Engel is in the Honda, behind the driver's seat		Applied	MA1	20110926
		30					Honda and HAPS in Colorado: Dad rides in the Honda, probably for the first time; Engel cooler behind driver's seat (first known photo of Engel in use); Guanella Pass above Georgetown	IMG			20110930
	Oct	1					Honda and HAPS in Colorado: Campsite along the road from Ward to Brainard Lake; Engel cooler more clearly shown behind driver's seat				20111001
		4					Honda and HAPS in Colorado: Dad, about 4 miles West up Magnolia Road, which leaves the Boulder Canyon Highway 119 about 3-4 miles West of Canyon Boulevard, Boulder / The engine overheated and we stopped for lunch; Engel cooler				20111004
		5					Honda and HAPS in Colorado: Brainard Lake; Campsite near road below Brainard Lake; Engel just visible				20111005
		15					Honda and HAPS in Colorado: Lake Eldora ski resort. Engel just barely visible.				20111015
		17					Honda and HAPS in Colorado: Dad, Garden of the Gods; Engel behind driver's seat				20111017
		21					Honda and HAPS in Colorado: 4th of July trailhead; Engel behind driver's seat				20111021
	Nov	9					Honda and HAPS in Iowa: Pat McGrath dealership, Subaru purchased; Engel behind driver's seat				20111109
		10					Honda and HAPS in Iowa: Pat McGrath dealership, comparisons of Honda and Subaru (Honda was left parked there for several weeks until I returned with a tow dolly); Engel was transferred to the Subaru			MA2	20111110
2012	May	13					Photos: Removed rear seats from Subaru (5/13/12 to 5/17/12): I had begun designing the Subaru RV with an improved Auxiliary Power System. Engel cooler. Also spent a day looking at how to mount the batteries on the rear.				20120513
		17					Engel in rear of Subaru at finished of project to remove rear seats				20120517
	?	?					Built a wooden platform for the Engel in the Subaru, right side behind passenger seat (unknown exactly when, but after removing rear seats and before taking another road trip)				2012MM?
	Aug	29					Rayville Folk Dance Party photos from Janice Lee showing Engel cooler shipping box on gray rolling ladder	IMG			20120829
2013	Jan	20					House fire: Engel survived because it was either in the Subaru (in the garage) or in the main shop. Engel began to be used constantly for food storage in the main shop kitchen (except for when I went on a road trip in the Subaru).			L	20130120
	Mar					Left for Ukraine, while in Ukraine the Engel was in the Subaru parked at Gene and Robin's house at Carter Lake, Loveland, Colorado			MA2	20130320
2014	Dec	25					I return from Ukraine after spending about ten days in Colorado (approximate date). Engel was moved to kitchen bench in main shop whenever I wasn't on a road trip.			L	20141225
2015	Aug	28					Julia and Mark Hall in the kitchen (main shop) showing Engel on bench	IMG			20150828
	Oct	23					Wilcox Residence, Loveland, CO: Subaru, Engel plugged in			MA2	20151023
2016	Jan	8					Bryce Jones in kitchen (main shop) showing Engel on bench			L	20160108
		18					20160118
2017	Jun	27					Horizon Exercycle showing Engel on bench				20170627
2018	Mar	15					W100 Testing showing Engel on bench				20180315
	Jun	11		~	06:20	~	06:50	Trace "fit tested" on board above batteries (in front of space for Engel, ~$78 in ~2004)				20180611
		23		~	06:45	~	16:00	… Trace rewired with longer #4 battery connections (TS_1); 2x4s cut and installed to prop Engel board above battery tops				20180623
2019	Mar	15	Fr	~	08:00			Trace inverter in use almost constantly during trip to Iowa (seek mode, Engel cooler, laptop and phone chargers)			MA2	20190315
		17	Su	~		~	22:30	Inverter in constant on mode during Sibley to Rayville run; Returned from Iowa (Engel back on the kitchen bench)			L	20190317
	May	13					20190513 Owner's Guide + Invoice Scan_7pages.pdf (damaged in house fire, but very usable); Inventory sticker applied	LIB			20190513
		14					This history sheet completed to date				20190514
2020	May	23	Sa	~	13:00			Engel cleaned and installed in Subaru (camping trip, Marcus and Sharon)	BC1		MA2	20200523
2021	Nov	13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup / Engel was in Subaru for a long time, but was moved to the main shop a few weeks ago for use in stabilizing Schauer BTS	IMG Z18		L	20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)	IMG			20211114
	Dec	5	Su	~	20:45	~	21:35	Late night thoughts: See white sheet Engel Battery Enclosure: I can fit the T-105s in the Engel and get full temperature control, cooling and heating (probably the entire range of outdoor tower site conditions)	DRD WS			20211205
		6	Mo					Added notes/ideas to white sheet Engel Battery Enclosure for circulating fan(s); TODO "Order heat pads"				20211206
		7	Tu					Added notes/ideas to white sheet Engel Battery Enclosure for Dinico control (many of the ideas turned out later to be erroneous); Ordered (4) heating pads 3CDD2D 60W 6x2", Zoro.com, $73.34	DRD EML WS			20211207
				~	21:00	~	21:50	Late night thoughts: See white sheet Engel Battery Enclosure Dinico Controller & Relays; Mostly erroneous ideas (corrected Sa12/11)	DRD WS			20211207
		9	Th					I've been working on T-sensors for W10 (many problems with infant mortalities of ones rec'd from India a long time ago); TODO "Comparitive Study of T-Sensors & Calibration of Dinicos"; Rec'd heat pads from Zoro	DRD			20211209
		11	Sa					Still many problems with W10 T-sensors; TODO "Raised priority of finishing Engel Enclosure"; Dinico control setup simplification ideas; Erroneous ideas corrected on white sheet Engel Battery Enclosure Dinico Controller & Relays	DRD WS			20211211
		12	Su					Problems with W10 T-sensors continue; Fabricated wooden blocks to set batteries on (~1/4"); Installed and wired up (4) fans (IMG); Engel moved from kitchen floor to bench; (4) heat pads wired up; Tested heat to >60⁰C (OK with Variac 40 max ~52w total); Dinico and SPDT relay set up with clip leads (TODO make a better harness of this, it's fragile), regulating on Enclosure Air with T1; Duty cycle 45% @ 60⁰C (Variac 35, Engel OFF)	DRD IMG B70/71 BC3 O6 O7 O8 O9 Z19		L0	20211212
		13	Mo					Duty cycle 93% @ -20⁰C (Heat OFF) ...; Duty cycles 63/37% @ 22⁰C (Variac 30, Engel, cycle total ~2m); Duty cycles 59/41% @ 22⁰C (Variac 35, Engel, cycle total ~2m); Duty cycles 78/22% @ 22⁰C (Variac 20, Engel, cycle total ~3m) / Duty cycles 90/10% @ 22⁰C (Variac 10, Engel, cycle total ~5m); (To minimize Engel "wear and tear" best to keep cycle long)	DRD O6 O7 O8 O9			20211213
		14	Tu					Duty cycles 98/2% @ 60⁰C (Variac 25, Engel, cycle total ~27m); Duty cycles 70/30% @ 60⁰C (Variac 40, Engel, cycle total ~3m); Cool should not be used at high temperatures / Duty cycle 35% @ 60⁰C (Variac 40, Engel OFF, cycle total ~2'); Silver tape on heat pads is coming loose; Complete dissassembly, fans removed, heat harness removed, heaters carefully wrapped with aluminum foil (IMGs) / Reassembled and set 60⁰C to bake on the silver tape; Set -20⁰C, 5 hrs later stuck at -19.7⁰C dropping extremely slowly (ambient ~22.5⁰C); Revised thoughts on future test points (-15, -5, 5, 15, 25, 35, 45, 55⁰C; 5-131⁰F) / Thoughts on Engel $900+ ($1500?) investment "Don't run at high temperatures"; Duty cycle 84% @ -15⁰C (No heat, Engel, cycle total ~4'); W10 (5) T-sensors running w/o errors on Sensor Rack	DRD SSC IMG			20211214
		15	We					With set 25.0⁰C (Variac 10, Engel OFF) it will not regulate (ambient ~22.5⁰C) because the fans dissipate ~150mA@13.8v=~2w; Heat pads w/Variac on 10 are ~3.3w; When set just above ambient must use both heat and cool to regulate (or as found out later set 25.0⁰C can be maintained with cooling only due to internal heat of fans and charging battery); Problems with W10 T-sensors continue, ordered (7) more sensors from DigiKey	DRD			20211215
		16	Th					Many problems with W10 T-sensors; Further troubleshooting of T-sensors stopped by RCWT Emergency	TM21F L3			20211216
		17	Fr					B26 SLA from RCWT installed in Engel (25.0⁰C); Checked and corrected W50 Float; Started a series of W50 BTS Tests @ 5, 10, 15, 20, 25, 30⁰C ...	TM21F PLN B26 WP1 Z19			20211217
		19	Su					... W50 BTS Tests FINAL DATA; Began some Engel stability testing, regulating on air ...	TM21F PLN B26 WP1			20211219
		20	Mo					See TM21F for notes and CONCLUSIONS in testing temperature regulation on the Battery instead of the Enclosure Air; Regulating on the battery is the fastest way to reach a new temperature / The air temperature swings wide to drive the "lead brick" to the desired T; If close to ambient and using both heat and cool it uses a lot more energy (but can conserve by lowering the Variac heat setting) / Began work on a possible W10 algorithm to automate temperature regulation with two modes	TM21F PLN Z19			20211220
				Set up to use Engel Battery Enclosure for B26/W50 Autopsy (set 21.0⁰C); ITECH Battery Test started (regulated temperature very nice for this!)	TM21F PLN B26 WP1			20211220
		21	Tu					ITECH Battery Test Concluded; Thermal Balance Checks data, shop heat OFF then ON; B26/W50 Recovery started	TM21F PLN B26 WP1 IMG			20211221
		22	We					Recovery completed; Notes on learning how to reduce energy and Engel use at temperatures near ambient for long term regulation (reduce or eliminate heat for long cycle times)	TM21F PLN B26			20211222
		23	Th			~	15:32	Experiments with maintaining battery T near ambient with the least amount of Engel cool and heat (TM21F); Recommend Heat 5, Engel ON and set 25.2 when target is 25.0 (seems to be OK for shop heat ON during working hours and OFF at night, with low heat the Engel will overshoot, and the average s/b ~25.0) ...; Set -20⁰C (W50/B26) to explore the limits of the lowest possible temperature and how long it takes with a "lead-brick" in the enclosure ...				20211223
		25	Sa					The Engel ran for more than 2 days and it won't reach -20⁰C (but it might if I was willing to wait another day); Lowest seen -17.7/-18.5⁰C (battery/air) and this with no internal battery charge wattage (W50 off) / Cover air gaps filled with 1/4" shrink (Air T immediate drop); Set -15.0⁰C to use W50/B26 to D&R test with 75w load	TM21F PLN B26 WP1 W10			20211225
		26	Su					B26 Discharge started and Engel is struggling to maintain -15⁰C; ~7a discharge current is warming the battery significantly; Worst error seen -13.2/-14.4 (battery/air ⁰C) and warming up / Removed shrink tubing air gap fillers (Concerns about explosion hazard in Recovery, which will start automatically by Wattmon control after I've gone to sleep)				20211226
		27	Mo	~	02:30	~	02:40	B26 is in Recovery and the Engel is still struggling to maintain -15⁰C; ~7a charge current warmed the battery to higher than -9.0/-12.1 (battery/air ⁰C); Now 1.39aE charge and battery is cooling down slowly / CONCLUSION For any significant battery discharge or charge above ~1a the Engel cannot maintain regulation lower than ~-10⁰C	TM21F PLN B26 WP1			20211227
				~	09:30	~	10:00	Set 25.0⁰C, Engel OFF, Heat 40; (Engel has been running almost 100% of the time for ~4 days) ... / Removed air gap shrink tubing and set Heat 50 (I've never set it this high before, let's see what happens) (now warming up as rapidly as possible w/o opening cover)	TM21F PLN B26			20211227
				~	10:48	~	10:54	7.1/30.8 (battery/air ⁰C), Air is +23.7 above Battery; Opened cover ~2m to examine condensation (a pool in the bottom and some on B26) and heat pad temperatures are too hot to touch except briefly (100⁰C?) ... / 8.3/31.6, Air is +24.3 above Battery; Charge 0.52aE rising, if the battery was fully charged I would expect the charge rate to be dropping as the charge V drops (for higher BTS T), BUT it's rising / (this is probably due to better migration in the paste of the SLA, and this effect might also be seen with an FLA)				20211227
				~	15:10			25.5/28.4 (Battery T is staying high); Set 25.2, Heat 5, Engel ON; Although not yet completely stabilized, these settings s/b good for the night for the target 25.0⁰C battery (see Th12/23)				20211227
		28	Tu	~	05:31	~	06:39	Engel is stable, long cycle: Cool 4m (6%), Heat 64m (94%), Total 68m	TM21F PLN			20211228
				~	07:27			Heat and Engel OFF, cover opened, fans OFF [W50/B26 Testing Concluded until after catching up on invoicing and recordkeeping]	TM21F PLN B26 Z19			20211228
		29	We					Photos of Engel Battery Enclosure; Review of Heater Pad purchase on Zoro.com	DNT IMG B26			20211229
2022	Jan	1	Sa					SSC of approved review on Zoro.com	DNT SSC IMG	Available	L	20220101
2022	Feb	17	Th					WP1 removed from bench, B26 removed from Engel (placed under bench on maintenance charge); Engel rotated and moved left on bench / Engel used to run temperatures up/down for testing T-sensors	DRD SSC WP1 W10 Z19	Applied		20220217
		20	Su			~	07:15	Further troubleshooting of T-sensors stopped by ONWT Emergency; Engel OFF (was regulating -20⁰C)	DRD TM22 W10 Z19			20220220
				Failed attempt at spare Schauer preparation / (BTS in Engel @ 25.0⁰C)	TM22 TM48S L14 PLN	Available		20220220
2022	May	24	Tu					Powered up for Schauer BC7 Preparation; D2D_2 control, T1 Air, T2 bundled near Schauer BTS; Set 25.4⁰C, Heat 10, Engel ON	T48S PLN BC7	Applied		20220524
		26	Th					Instrumentation set up, T-105s in Engel with W10 current loops; Target 25.0⁰C ...; Arrived at PSP (Predicted Set Point) 25.5⁰C, Heat 10, Engel ON [These settings and PSP remained good for 2 days]	T48S PLN SSC IMG BC7			20220526
		28	Sa					T-105s: Engel continues stable at 25.0⁰C; T Range BTS Tests Started ...; New Target -10.0⁰C ...	T48S PLN SSC BC7			20220528
		31	Tu					T-105s: Engel is stable at -10.0⁰C; PSP -10.2⁰C, Heat OFF, Engel ON; NOTES on running Absorption Tests: Circulating fans OFF then gap Engel lid, Start Absorption tests when T=Target-0.1 ...; New Target 0.0⁰C ...	T48S PLN BC7			20220531
2022	Jun	2	Th					T-105s: Engel is stable at 0.0⁰C; PSP 0.0⁰C, Heat OFF, Engel ON; CONCLUSION for running Absorption Tests: As before, but chase wattage during test ...; New Target +10.0⁰C ...				20220602
		4	Sa					T-105s: Engel is stable at +10.0⁰C; PSP +10.0⁰C, Heat OFF, Engel ON ...; New Target +20.0⁰C ...				20220604
		6	Mo					T-105s: Engel is stable at +20.0⁰C; PSP +20.2⁰C, Heat 20, Engel ON ...; New Target +30.0⁰C ...				20220606
		9	Th					T-105s: Engel is stable at +30.0⁰C; PSP +31.0⁰C, Heat 20, Engel ON ...; New Target +40.0⁰C ...				20220609
		10	Fr					Discovered reversing T-comp problem with BC7: Unable to stabilize at +40⁰C without serious birddogging (explosion hazard, Engel cover must be gapped); T Range BTS Tests Abandoned/Concluded; New Target shop ambient				20220610
		11	Sa					BC7 Schauer BTS test setup broken down: Circulating fans OFF; Engel OFF; T-105s removed; Cleaned mold and stains in the bottom	T48S BC7	Available		20220611
				Assembled BC8 Schauer BTS test setup: Bundled BTS and Dinico sensor T2 together in center of enclosure in 3/4" electrical conduit 7.5" long (zinc steel pipe) / Stabilizing BTS to +25.0⁰C ...	T48S PLN BC8 IMG	Applied		20220611
		12	Su					BC8 Schauer BTS Tests Started: No battery; FTR has Duty Cycle Statistics / Target +25.0⁰C: PSP +25.1⁰C, Heat 25, Engel ON; [see Th6/16 for a better setting] / Target +30.0⁰C: PSP +30.2⁰C, Heat 40, Engel ON / Target +35.0⁰C: PSP +35.6⁰C, Heat 50, Engel ON / Target +40.0⁰C: PSP +41.1⁰C, Heat 50, Engel ON; If this Target is needed again, consider Lower Heat and Engel OFF (see FTR); ... New target +45.0⁰C ...	T48S PLN BC8			20220612
		13	Mo					Stabilization at +45.0⁰C was interrupted/delayed by troubleshooting and replacement of bad reversing relay on Dinico T control	T48S PLN BC8 Z19			20220613
		14	Tu					BC8 Schauer BTS Tests continued, see Su6/12 / Target +45.0⁰C: PSP +44.5⁰C, Heat 40, Engel OFF / Target +50.0⁰C: PSP +49.5⁰C, Heat 40, Engel OFF / Target -10.0⁰C: PSP -9.6⁰C, Heat OFF, Engel ON / Target -5.0⁰C: PSP -4.7⁰C, Heat OFF, Engel ON; ... New target 0.0⁰C ...	T48S PLN BC8			20220614
		15	We					BC8 Schauer BTS Tests continued, see Su6/12 / Target 0.0⁰C: PSP +0.2⁰C, Heat OFF, Engel ON / Target +5.0⁰C: PSP +5.1⁰C, Heat OFF, Engel ON / Target +10.0⁰C: PSP +10.1⁰C, Heat OFF, Engel ON / Target +15.0⁰C: PSP +15.1⁰C, Heat OFF, Engel ON; ... New target +20.0⁰C ...				20220615
		16	Th					BC8 Schauer BTS Tests continued, see Su6/12 / Target +20.0⁰C: PSP +19.8⁰C, Heat 20, Engel ON / Target +25.0⁰C: PSP +24.9⁰C, Heat 30, Engel ON; BC8 Schauer BTS Tests Completed; Heat OFF; Engel OFF; Cover open wide; Circulating fans OFF; Dinico OFF	T48S PLN BC8 IMG	Available		20220616
		20	Mo					Approximate date I started using the Engel/Dinico for a Precision Beer Cooler (PBC); Started with set 0.0⁰C but soon found out I could lower it (as the high alcohol content of the beer I drink lowers the freezing point)		Applied		20220620
		28	Tu					Beer removed for W50 Prep: Set 24.9⁰C, Heat 30, Engel ON (settings from Th6/16/22 T48S); W50 BTS bundled in conduit pipe with Dinico T2 ... / After completing this I went back to using the Engel as PBC, set -1.5⁰C	TM22 WP1			20220628
2022	Jul	3	Su	~	07:00			Beer removed; Engel OFF, Cover Open, Circulating Fans OFF (departed on trip to CO)		Available		20220703
		21	Th	~	12:55			Dinico/Engel/fans powered up, again for use as PBC: Set -2.5⁰C (as before trip to CO)	PLN	Applied		20220721
		23	Sa					Added Circulating Fans Cover Switch: Momentary pushbutton switch mounted inside with Velcro; If cover is opened more than ~1/2" it interrupts the circulating fans; Perfect for cooling beer, but also useful in bench testing	PLN IMG			20220723
		24	Su					Set -3.0⁰C (no beers are freezing)	PLN			20220724
		26	Tu					Many beers at -3.0⁰C and none of them frozen: Set -3.5⁰C [probable best setting for opened/capped beers, see Su8/14]				20220726
		29	Fr					Beers in box -3.1⁰C (not dropping quickly); No beers inside or outside of box show any signs of freezing; Set -4.0⁰C				20220729
		31	Su					Beers in box -3.3 to -3.4⁰C (not dropping); No beers show any signs of freezing; Set -4.5⁰C				20220731
2022	Aug	2	Tu					Beers in box -4.0, no freezing; Set -5.0⁰C				20220802
		4	Th					Beers in box -4.0, no freezing (inside or outside of box); Set -5.5⁰C [this was the lowest setting tried, but it freezes opened/capped beers]				20220804
		5	Fr					Beer in box -4.9 frozen (opened/capped, low pressure); All other beers OK; Set -5.0⁰C; NOTE The freezing point is also depressed by CO2 pressure (not just alcohol content)				20220805
		6	Sa					Beer not in box frozen (opened/capped, Heineken); Set -4.5⁰C				20220806
		10	We					Beer outside box frozen (opened/capped, St. Pauli); Set -4.0⁰C; NOTE I can also place partial beers in the box as they won't freeze as easily there				20220810
		13	Sa					Discovered that Engel was not running; Wiggled AC input plug and OK; NOTE It's a little loose and probably got knocked out a bit by kitchen cooking activity				20220813
		14	Su					Beer in box frozen (opened/capped, Heineken); Set -3.5⁰C; NOTE This is probably the ideal setting for use as PBC if I'm going to be putting opened/capped partial beers in it (put them inside box)				20220814
		15	Mo					Used for food from small fridges while defrosting: Set -1.0⁰C				20220815
				~	16:00	~	20:50	Dried and cleaned out: Engel OFF; Cover open; Set 25.0, Heat 10; Fans ON ...; Heat OFF; Fans OFF (cover open)		Available		20220815
		19	Fr					Prep of SCP-75-12 Chargers for LSWT: Adjusted BC9 and BC10 for Target of 13.500vI at 25.0⁰C (no battery, BTS metal pipe in Engel); PSP=+24.9, Heat 30, Engel ON (same as Th6/16 settings)	T48-3 PLN L17	Applied		20220819
		20	Sa					Dual Supply Bench Testing Setup Assembled: Z20 Dinico mounted on Wiegmann Back Plate, T2 sensor on battery negative post will be used to indicate battery temperature / Z19 Dinico for T1 Air regulation , T2 on top of 27TMX for comparison; Stabilizing towards +25.0⁰C				20220820
		21	Su					Stable at +25.0⁰C (Z20 T2); PSP=25.6, Heat 30, Engel ON (27TMX)				20220821
2022	Sep	5	Mo	~	06:15			Stable for a long time: Z20 T2 +24.9⁰C mostly 25.0⁰C after start of cooling (set is 25.7=PSP+0.1); 13.480-13.483vI through entire cycle (BC9 Float on 27TMX in Engel); Load 0.072aI, Net charge ~0.070aE (total ~142mA)	T48-3 PLN			20220905
		12	Mo					Very stable for a week now (set 25.7): New PSP for 27TMX target +25.0⁰C (Z20 T2); PSP=25.75, Heat 30, Engel ON; This could be achieved in testing by iPhone timer (10m set 25.8, 10m set 25.7)	T48-3 PLN WP11			20220912
		14	We					Tour of shop given to Geri and Drake: When I showed them the Engel it was not cooling (Z20 T2 ~35⁰C); Heat OFF, Cover opened (will tshoot later)	T48-3 PLN			20220914
		15	Th	~	06:30			Cooling "fixed": Again, probably by reseating AC input cord (contacts are "loose")	T48-3 PLN WP11			20220915
		17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917
		19	Mo					Indirect Comparison of Z19 T2 with Z20 T2, CONCLUSIONs: Z19 with Plastic Cap reads +0.35⁰C higher than Z20 / I confused the comparison somewhat by installing the Plastic Cap, which appears to drop the battery T readout by about -~0.25⁰C / I think it is safe to state that Z20 T2 reads ~-0.5 degC lower than Z19 T2 / Set changed from 25.7 to 25.4 new PSP, Z19 T2 negative post, plastic cap, Heat 30, Engel ON ... ~10 hours later the battery stabilized at 25.0⁰C	T48-3 PLN WP11			20220919
		20	Tu					Bench Setup Changes/Improvements: Moved Z19 T2 and Plastic Cap to Battery +; Rotated Battery (+ near the front); Installed new design Foam Block (Battery +) / CONCLUSIONs: Most of the difference between the (-) and (+) posts of the 27TMX is due to uneven heating and cooling effects within the Engel, the rear of the enclosure is warmer than the front / The new Foam Cap has made a dramatic difference: Readings are at least 1.3⁰C closer to the true internal battery T / There is more stratification and uneven heat/cool inside the Engel than I thought: The top is >3⁰C hotter than the bottom; The rear is >1⁰C hotter than the front	T48-3 PLN IMG WP11			20220920
		21	We					Bench Setup Changes/Improvements: Engel Heat/Cool Duty Cycle Changed (lower heat, longer cycle): / Total Duty Cycle was <2m with Heat 30 (Cool 34% of cycle); Total Duty Cycle now ~5.7m with Heat 15 (1/4 the power, Cool 9% of cycle, Target 25.0⁰C); PSP has been shifted down due to this change, will notate after stabilization / Rotated 27TMX: Installed Z19 T2 and Foam Cap on Battery Negative Post (front left); It's best to have the extra stuff (BTS and T2 if exterior site) on Battery Negative because it doesn't swell / Fabricated and Installed Another Foam Cap on 27TMX +: Best for safety and reducing effect of surrounding air on battery T	T48-3 PLN WP11			20220921
		25	Su					Engel Stable at +25.0⁰C (We9/21 changes/improvements): Found PSP=25.8, Heat 15, Engel ON (27TMX)	T48-3 PLN WP11 Z19			20220925
2022	Oct	1	Sa					Engel (+25⁰C Target): Found Relay Contacts Fused Closed; B58 ~34⁰C (BK float was ~180mA, set reduced to 13.38v); Cleaned relay contacts; Oiled pivot points and springs; Changed relay wiring (both poles for heat) / DO NOT LEAVE UNATTENDED AT HIGH HEAT; [Fr10/28 TFTP: We may be able to reduce the inductive kick of the Variac by placing a large resistive load which would absorb most of the kick]; Seeking PSP for Heat OFF ...	T48-3 PLN WP11 Z19			20221001
		2	Su					Engel Stable at +25.0⁰C: W150_1 at bench ambient, 27TMX and BTS in Engel / PSP 25.2-25.3, Heat OFF, Engel ON, 1.7% duty cycle, total cycle ~43m; Very close to not enough internal heat (circ. fans, float charge) to maintain ~2degC above shop ambient / PSP 25.4, Heat 5, Engel ON, 2.8% duty cycle, total cycle ~34m / 25⁰C tests completed, moving Engel to -15⁰C ...				20221002
		3	Mo					Bench Testing (-15⁰C): Stabilizing, looking for PSP; Circulating fans inop: Opened cover, fiddled, fixed (loose Velcro); Photo of W150_1 on bench next to Engel	T48-3 PLN IMG WP11 Z19			20221003
		4	Tu					Bench Testing (stable at -15⁰C): W150_1 at bench ambient, 27TMX and BTS in Engel; PSP -15.5, Heat OFF, Engel ON, 86% duty cycle, total cycle ~4.6m / -15⁰C tests completed, recovery while heating to +50⁰C: Relay stuck in heat (probably caused by white neutral clip leads pressing against pole on back side) ...; Relay contacts partially stuck at times ...	T48-3 PLN WP11 Z19			20221004
		5	We					Bench Testing (stable at +50⁰C): Woke to relay stuck in heat (wiggled and then OK); PSP +50.4, Heat 20, Engel OFF (W150_1 at bench ambient, 27TMX and BTS in Engel); Moving on to +25⁰C / W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 PLN IMG WP11 Z19			20221005
		6	Th					Bench Testing (~25⁰C): Bench Testing Finished / Heat OFF, Engel OFF, Cover open	T48-3 PLN WP11	Available		20221006
		25	Tu					PBC: T2 in conduit in box w/11 St. Paulis from garage; Set -3.5⁰C as per Su8/14; Cool is ~60% of total cycle	DNT PLN	Applied		20221025
		26	We					PBC: Cool is ~47% of total cycle ~3m				20221026
		29	Sa					PBC: Photos and video "$2,000 Precision Beer Cooler"	DNT PLN IMG			20221029
2022	Dec	13	Tu					End use as PBC; Rigged ~40w bulb on Heat before Variac; Hopefully, theoretically, this should reduce the inductive kick that is probably causing the relay contacts to stick; Started WP12 Configuration and Testing	T48-4 PLN WP12 Z19			20221213
		14	We					WP12 Configuration and Testing completed; Heat changed to conserve Engel until ready to Configure and Test WP13 (Heat 30->10, Engel OFF)	T48-4 PLN WP12			20221214
		15	Th	~	10:00	~	11:30	Engel ON ...; Heat 10->5 and Engel OFF	PLN L18			20221215
		16	Fr	~	07:30			All OFF: Cover open, Heat OFF; 40w bulb off (waiting for Configure and Test of WP13)	PLN			20221216
2023	Jan	7	Sa					Started Configuration and Testing of WP13: Target 25.0⁰C (BC11 BTS); 40w bulb ON, Heat 30; Engel ON	T48-4 PLN WP13			20230107
		8	Su			~	18:10	WP13 BTS testing completed; Heat OFF, 40w bulb OFF, BTS removed ...; Engel retasked as PBC; Set -3.5⁰C as per Tu10/25/22, but also set differential d=0.3 to lengthen duty cycle				20230108
		12	Th					PBC: Cool is ~50% of total cycle ~4m (d=0.3); Set d=1.0 to lengthen duty cycle even more (but it will also lower the average beer T) / Added 2nd old CSU timer to Heat; It is easier to obtain duty cycle stats with the old CSU timers (as opposed to using the iPhone); See PLN for examples of this	PLN			20230112
		13	Fr					PBC: Cool is 50.5% of total cycle 5.8m (d=1.0, T2 beers -2.8⁰C, HVAC heat set 70⁰F); Set d=2.0 to lengthen duty cycle even more (best for Engel if Rest between cools is >=5m)				20230113
				R&D TODO: W150 Full Environmental Testing (WP13); Measure Engel Effective Cooling Power	DWP WP13			20230113
		14	Sa					PBC: Cool is ~52% of total cycle ~8.4m (d=2.0, T2 beers -3.4⁰C stable, HVAC heat set 70⁰F); Rest between cools ~4m (and this morning when it was cool in the shop it was 5m); Agreement between T2 beer (-3.4) and set (-3.5)	PLN			20230114
		15	Su	~	08:30			PBC: (HVAC Heat OFF at 62⁰F, d=2.0, T2 beers -2.6⁰C); Cool is ~40% of total cycle ~11.2m; Rest between cools ~6.7m				20230115
		27	Fr					PBC: Divider box fabricated; Corona Extra 24-pack case box cut down, 1/2" feet, silver tape; Holds 20 beers; No more rattles; Easy to load (when down to only 8 beers left transfer a 12 pack); Better air circulation (faster cooling)				20230127

## Z1
Miscellaneous: Z1	A					CP_1: CradlePoint MBR95

Date/Time CST/CDT					Description	Other Sources	Status	Location	Backup
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	L	cp_config_20220701_0806.bin
2013	Feb	20					Ordered from 3Gstore.com / Downloads to Library	EML CPSN LIB	On Order			20130220
		25					Received	CPSN	Available	L		20130225
	Mar	3					Joseph Fowler unpacked and set up, but I told him not to change the configuration at all					20130303
		22					Joseph Fowler configured (Skype call from Ukraine); Problems (see CPSN), we were trying to set it up bridged somehow to current shop router					20130322
?	?	?					Mark Hall took the router to his house (while I was in Ukraine)			Hall Residence		?MM?
2015	Feb	4					Retrieved router from Mark Hall (after return from Ukraine)	CPSN		L0		20150204
		5					Downloaded 20150205 MBR95_Manual_3.6.3.pdf to Library; Installed for use with Pantech UML290VW Modem; Reset to factory defaults; Firmware Update 4.2.0 -> 5.0.4; Backup / Physically installed in rear room with VW modem in North East-side window on USB extender and LAN1 connected to 8-port Gigabit switch	LIB CPSN	Applied		cp_config_20150205_0904.bin	20150205
		6					Configuration; Backup	CPSN		L	cp_config_20150206_1350.bin	20150206
	Mar	5					Setup WiFi as WAN with AndroidHotspot3365, password 1269e2c5979b; Backup				cp_config_20150305_1922.bin	20150305
		8					Reenabled WAN Interface for Pantech UML290 (I had disabled it a few days ago because I had run out of data allowance with VW); Backup				cp_config_20150308_0805.bin	20150308
	Apr	15					Reserved IP 90.0.0.4 for JAK2					20150415
		19					Reserved IPs modified for JAK2; Backup				cp_config_20150419_1000.bin	20150419
		23					Reserved IP for JAK2 corrected; Backup				cp_config_20150423_1515.bin	20150423
		30					TurboNet Installed; Backup				cp_config_20150430_1623.bin	20150430
	May	16					Set up Device Alerts; Backup				cp_config_20150516_0745.bin	20150516
	Jun	29					Network Settings / Firewall Configuration, Port Forwarding Rules (VNC T400s); Not working yet (still don't have a fixed IP from TurboNet)					20150629
	Jul	1					Email from Keith Jones "static ip" (for Data Vision Services): 12.133.21.140, 255.255.255.128, 12.133.21.129, 199.59.192.66, 8.8.8.8	EML				20150701
		2					Turbonet Static IP; Port Forwarding Rules; Backup	CPSN			cp_config_20150702_1049.bin	20150702
	Sep	19					Emails to and from Keith Jones "Re: IP Addresses": This is what I have now: 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon) / Keith responds with "You can use .147 if you need another one"	EML				20150919
	Oct	9					Reserved IP 90.0.0.99 for Sasha-Laptop; Modified Port Forwarding Rules for VNC to Sasha-Laptop	CPSN				20151009
2016	Feb	24					Email to Keith Jones "Re: Ip's for Jeff Klute" which summarizes static IPs: 12.133.21.140 (DVS), 12.133.21.146 (RW Wattmon), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.157 (RW WebRelay)	EML				20160224
	May	20					Port Forwarding Rule added for JAK2 CrashPlan Listen	CPSN				20160520
		22					Backup				cp_config_20160522_2202.bin	20160522
		24					Port Forwarding Rule Added for T400s CrashPlan Listen; Backup				cp_config_20160524_0617.bin	20160524
	Jun	26					Port Forwarding Rules modified for T400s and JAK2 CrashPlan Listen					20160626
		27					Backup				cp_config_20160627_0120.bin	20160627
	Jul	7					Temporary changes (CPSN says "see Alternative Energy.doc" but on 6/20/18 I couldn't find anything there about this) …					20160707
		8					Temporary changes end					20160708
		16					“Extra” TurboNet public fixed IP set: 12.133.21.147 (JAK2 is yet on it’s own subnet and USG 100 router)					20160716
	Dec	21					Port 80 forwarded to NAS (Web Server)					20161221
		22					Backup				cp_config_20161222_1021.bin	20161222
		25					Photos of Website Hosting Hardware (shared with Yevgeniya)	IMG				20161225
2017	Jan	6					Network Settings / DNS Configuration / Known Hosts Configuration (for websites); Backup	CPSN			cp_config_20170106_0545.bin	20170106
		31					Email to Mark & Keith "Static IPs: conflicts? Known Hosts?": List of IP addresses not using DHCP 12.133.21.146 (RW Wattmon), 12.133.21.157 (RW WebRelay), 12.133.21.141 (RN Wattmon), 12.133.21.143 (RN WebRelay), 12.133.21.147 (DVS WAN #1), 12.133.21.140 (DVS WAN #2), all 255.255.255.128, 12.133.21.129 / Also inquired about the possibility of adding those addresses to his router's Known Hosts table; 5/7/19 I have not yet to receive a response to these inquiries	EML				20170131
	Mar	4					Removed port forwarding for JAK2 CrashPlan; Removed port forwarding for VNC SASHA-LAPTOP; Backup	CPSN			cp_config_20170304_0757.bin	20170304
		8					Email to Mark & Keith "Re: Static IPs: conflicts? Known Hosts?": I've heard nothing about this since over a month ago; 5/7/19 I have not yet to receive a response to these inquiries	EML				20170308
	Apr	14					DHCP Reservations for Wattmon_9 and Wattmon_10	CPSN				20170414
	May	26					DHCP Reservation for T450s; Firewall configuration Port Forwarding Rules for T450s incoming VNC connections to LAC and WNC; Reserved IP 90.0.0.18, EPSON3323CA, 44:d2:44:33:23:ca					20170526
		30					Backup				cp_config_20180530_1340.bin	20170530
2018	Jun	20					This history sheet created; Inventory Sticker applied					20180620
	Aug	15					DHCP Reservation for Wattmon_8: 90.0.0.108, d8-80-39-0c-a9-a7, d8:80:39:0c:a9:a7; Backup	CPSN			cp_config_20180815_0406.bin	20180815
2019	Mar	10					Internet / WiFi as WAN > Wireless Scan Settings: Scan Interval: 60 -> 5 (seconds); This doesn’t seem to (but may) help the cradlepoint connect to the Android Hotspot faster; Backup				cp_config_20190310_0320.bin	20190310
	Apr	6					DHCP Reservation for HikVision Camera 1 of 5: 90.0.0.51, c4-2f-90-42-d6-05, c4:2f:90:42:d6:05; Backup				cp_config_20190406_0520.bin	20190406
		13					Port Forwarding Rule added for T400s BlueIris Web Server: Port 81 --> 90.0.0.10:81; Backup				cp_config_20190413_2045.bin	20190413
		17			07:31			Disabled Port Forwarding for NAS Web Server (Temporary): Did not update Current Configuration					20190417
		18					13:13	Enabled Port Forwarding for NAS Web Server					20190418
		29	Mo		12:50		14:05	Rayville still down (since Su4/28 15:58, lightning destroyed unit at RCWT) but Mark says they see my unit; Rebooted CradlePoint; Restarted Ubiquiti; No service / Static IP 207.229.103.164 (255.255.255.248, 207.229.103.161, 8.8.8.8, 8.8.4.4); CradlePoint Static --> DHCP (rec'd 10.0.100.202); 13:32 we are up but without incoming services that need fixed IP / No backup of Current Settings; We’re hoping to be able to go back to the static IP as soon as Mark/Keith get the unit replaced in a couple of days	CPSN SMS				20190429
		30	Tu		11:33			Email from Mark originally from Keith "Jeff Klute Static IP address" which I could use on current subnet: / 207.229.103.54 (255.255.255.252, 207.229.103.53, 1.1.1.1, 8.8.8.8) [not used, I'm hoping they'll get us back to our original static IP]	EML CPSN				20190430
	May	1			12:29		12:56	No internet; Mark advises me to switch back to my fixed IP (unit has been replaced) … / CradlePoint set for previous fixed IP (207.229.103.164); Internet Restored (outage 26 mins 18 s); No backup of Current Settings (nothing has changed since 4/13/19)	SMS CPSN				20190501
		12					These notes caught up since 6/20/18 when I started this sheet, which will be the primary place for notes on the CradlePoint Setup, with extreme details and the Current Configuration in CPSN	CPSN				20190512
	Jun	14	Fr	~	23:30	~	00:53	Very poor internet, pings are 450-650ms; NetWorx Speed Meter on T450s has stopped working; Unable to get a test with Speedtest.exe or .net; CradlePoint wouldn't connect to hot spot / Rebooted CradlePoint, still wouldn't connect; Manually disabled Ethernet in CradlePoint; 00:12 Established internet for about 40 mins until 00:53 when I Enabled Ethernet on CradlePoint and turned off WiFi Hotspot					20190614
		27					TurboNet down until tower is repainted; At some point after I switched to using Consumer Cellular and phone hotspot I disabled Ethernet Blue					20190627
	Jul	25	Th					DHCP Reservation for Ricoh SP C261SFNw All-in-One Color Laser Printer: 90.0.0.19				cp_config_20190725_0400.bin	20190725
	Sep	6	Fr	~	14:33	~	14:57	Ubiquiti NanoStation plugged in; Samsung phone WiFi hotspot OFF; Enabled "Ethernet: Blue"; TurboNet is up; Fixed IP is correct (207.229.103.164)	CPSN			cp_config_20190907_0400.bin	20190906
		25	We	~	04:00	~	04:20	Discovered that slow download speeds are fixed by CP_1 reboot (see RW) / Internet / Connection Manager > WAN Interfaces > WiFi: AndroidHotspot3365 > Disable (this may or may not help, problem shows up after a day or two) / System Settings / Managed Services > WiPipe Central Services > Disable (this may or may not help, just shooting blindly now to find something that makes a difference)	L1				20190925
		27	Fr		02:29		05:10	NetWorx Speed Meter tests (02:29 and 03:29), speeds have dropped again; Rebooted CP_1 (04:05); System Settings / Administration > System Logging > Logging Level: Info->Debug; Clear Log / Speeds have not substantially improved (04:12); Rebooted CP_1, but speeds have not improved; Powered down and restarted entire network, but speeds have not improved, in fact, they are worse; T450s rebooted / NetWorx Speed Meter stopped working; Speedtest.exe 6.6/9.4 Mbps down/up; NetWorx Speed Meter on T400s 976 Kbps down; T450s direct to TurboNet PoE injector, speedtest.exe 3/6 Mbps down/up / To Keith and Mark	EML L1				20190927
				~	12:00			Mark and Brandon stopped by to test: Their laptop direct to PoE injector at first showed reasonably good speeds (32/12 Mbps down/up); T450s direct to PoE injector poor speeds, multiple speedtest.exe, 2-6 Mbps / Then Brandon's laptop again and poor speeds (2-6 Mbps, some long pings); They went on the roof and aimed the antenna up a bit; No improvement; But these tests confirm it isn't in my network or the CradlePoint / Problem is most likely either cabling issues (run to the roof) or the tree in the way really does matter; TODO "Drop the tree or move the antenna to the S end of the shop roof (requires new cable)"	L1 WS			cp_config_20190928_0325.bin	20190927
	Oct	24	Th	~	09:50	~	13:50	Very poor internet speeds for 5 days (Kbps); Rebooted CP_1 immediate improvement (Mbps) …; Tested again, poor speeds (Kbps)					20191024
		30	We					Very poor speeds lately; Rebooting CP_1 sometimes helps slightly, but poorest on windy days					20191030
	Nov	2					Again, slight improvement with CP_1 reboot					20191102
		7	Th					I discovered part of the problem with poor speeds (since September): Ubiquiti Tough Switch stopped working and internet lost entirely until I restarted it (see notes on white sheet stored with Ubiquiti) / Removed Ubiquiti entirely (I don't need it or something like it until and if I get all 5 security cameras installed); Tested internet speeds with SpeedTest.exe and immediately saw 16ms pings and 48/59 Mbps down/up (wow!) / The tree might still be an issue, but for now all looks good					20191107
				~	07:00			Re-enabled WiFi AndroidHotspot3365, tested failover and connects if phone hotspot is turned on				cp_config_20191107_0700.bin	20191107
2020	Jun	25	Th					From Keith “Here is your new ip address, This work is being done to provide a fiber failover in case of a fiber cut. Please put this in your router by July 6 2020! These are active” / 137.83.25.169/30; Ip=137.83.25.170; Sn=255.255.255.252; Gw=137.83.25.169	EML TW6-10 L1				20200625
		27	Sa		10:02			To Keith “I’ll update my router and DNS sometime in the next few days …” with questions about failover that as of Th7/2 have not been answered					20200627
	Jul	1	We		15:38		18:27	Internet down …; To Keith and Mark “… Any known issue?”; Immediate answer from Mark “Reset your router. You’re up” [I went back to sleep]	SMS L1				20200701
		2	Th		00:55	~	02:15	Rebooted CP_1 (still no internet); Internet > Connection Manager > Ethernet: Blue > Edit > General Settings > Failure Check > Monitor while connected: Active Ping to 207.229.103.161 (Gw) / [I’ve never noticed this setting before]; Dashboard status went immediately to State “Disconnected” then “Connecting” / Internet > Connection Manager > Ethernet: Blue > Edit > Ethernet Settings > addresses changed as per email from Keith 6/25/20; Also disabled Active Ping; State shows as “Connected” but no internet / Powered off/on TurboNet PoE and CP_1, yet no internet; Set for DHCP and rec’d IP 10.0.103.58 (now we have internet) / NetWorx Speed Meter says my IP address is 207.229.103.164 [sic] but shows 21.4/13.8 Mbps down/up; Reset to fixed IP as per Keith (no internet, screenshot); Reset to DHCP (10.0.103.58); Email to Keith and Mark; TODO	SSC EML TW6-10 L1				20200702
				~	18:00	~	20:00	I noticed that internet was down since 08:13; Set static IP as per Keith’s EML of Th6/25 and internet is up [as of yet no response to my email]; DNS registration changed (Network Solutions); Email from Keith 18:32 / Reply to Keith 18:56; Tested browsing to DataVisionServices.com (iPhone, Cellular Data, must wait); EML printouts filed; NetWorx Connection Monitor logs cleared and Speed Meter tests (T450s, T400s, JAK2)	L1 EML WSN SSC CPSN TW6-10				20200702
		3	Fr	~	06:20	~	10:00	DNS to DataVisionServices.com is working (iPhone, Cellular); Network Settings > Firewall Configuration > Port Forwarding Rules > deleted VNC SERVANT2, VNC T450s LAC, VNC T450s WNC, T400s CrashPlan Listen / VNC Address Books Modified T450s, T400s and JAK2 / Internet > Connection Manager > WAN Interfaces > Ethernet > Edit > General Settings > Failure Check > Idle Check Interval 60 seconds, Monitor while connected Active Ping, 216.58.192.142 (google.com) / Tested by disconnecting rooftop TurboNet (OK); Set up iPhone Personal Hotspot	T450s T400s JAK2				20200703
		4	Sa	~	05:30	~	12:00	Set up and tested iPhone WiFi as WAN with automatic failover from TurboNet to iPhone; This did not work as expected, mystified why it won’t connect to iPhone / iPhone is changing the BSSID (deleted BSSID from Saved Profile); iPhone shuts down WiFi broadcasting to save battery power, so if it isn’t being used CP_1 thinks it is “Unplugged” / THEREFORE, if we lose TurboNet use Settings > Personal Hotspot (Control Center can also make it discoverable) / Tests, iPhone will sustain connection while locked and for a long time (I tested for >30 mins), 90 seconds after TurboNet is restored and CP stops using iPhone, the iPhone will stop broadcasting / Notes on research in CPSN “Is there any way to keep the iPhone Discoverable even when Hotspot is not being used?” / (I’m not going to pursue this now, as it doesn’t look very promising and I’d rather stick to a “manual ON” situation until cellular data is “less expensive”); TODO	Z13 CPSN				20200704
		5	Su	~	06:45	~	09:00	System Settings > Device Alerts: SMTP notifications sent to Jeff@DataVisionServices.com for WAN Device Status Change; MailCOPA filters; Testing	Z13 CPSN			cp_config_20200705_0835.bin	20200705
				~	09:00	~	11:15	Internet > Data Usage Management and Alerts: CC iPhone Hotspot setup and tested / Work flow “If TurboNet goes down and I have to use the iPhone Hotspot” adjust the Assigned Usage and Percent of Usage and update the Historical Data to reflect the current iPhone Cellular measurements / (which I reset on the 21st of each month)				cp_config_20200705_1115.bin	20200705
				~	11:15	~	11:30	See CPSN for “Automatic Failback from iPhone to TurboNet (Notes from TODO)”					20200705
		20	Mo	~	03:00			SMTP notifications are not being sent for “short” (2-10 min) internet failures; NetWorx Connection Monitor sees them, but CP is not sending the emails; Reviewed settings; I’m not sure why, I’ll keep an eye on it / [NOTE ADDED 7/26 It could be that the failure check is not done if the iPhone connection is not available]					20200720
		23	Th	~	08:15			Internet > Data Usage > Add > TurboNet; Assigned Usage in MB 409600 (400GB, 500000MB is maximum allowed); Cycle Type Monthly; Cycle Start Date 7/1/20; Send alert on Cap; Custom Alert / Percent of Usage 50 (200GB); Added 60769 MB x 2 dated 7/22/20 (current usage as per NetWorx) / The alerts are somewhat meaningless, as I have unlimited data with TurboNet, but the tally should show me how much the iPhone is using (when compared with NetWorx tally for JAK2, T400s and T450s); Saved Backup; (R)				cp_config_20200723_0840.bin	20200723
	Nov	23	Mo	~	05:40			Internet > Data Usage > TurboNet > Edit > Do NOT Send Alert on Cap and Do NOT Custom Alert; Saved Backup				cp_config_20201123_0540.bin	20201123
2021	Aug	5	Th					Yesterday @ 16:46 we lost internet at the shop, see RW for initial details; M&K at TurboNet traced this to RCWT being down, see RCWT for details; This morning I went onsite at RCWT with M&K and service was restored / But when I returned to the shop I still did not have internet on T450s and T400s / Rebooted CP, repowered everything, called Keith, switched CP to DHCP (was fixed IP 137.83.25.170), CP is getting WAN 10.10.11.244 BUT "Connecting" and no internet T400s/T450s, rebooted, cycled power / Laptop direct to TurboNet adapter does get internet; Switched CP back to static IP; CP clock is not correct; System Settings / Administration > Local Management > Disabled Internet bounce pages / ALL THE EFFORTS DID NOT RESTORE INTERNET TO T400s/T450s; Decided CP_1 is probably defective and will replace with 2nd unit I bought for the SAPS (CP_2); SSCs of CP configuration/status pages / Reviewed and corrected Current Configuration in CPSN (some changes were applied for things I no longer use); Saved Backup (but I think I'll just manually set up CP_2) / I removed CP_1 from service by the end of the day - it's on the bench waiting testing, because I want to be sure it is defective before I throw it out, as a spare is a good idea!	L1 Z2 CPSN	Defective?	L0	cp_config_20210805_1230.bin	20210805
		15	Su					Tested CP_1; Reset and Configured with cp_config_20210806_2110.bin (which is from CP_2 on 8/6/21); Everything is 100% AOK (diagnosis: configuration was corrupted); In service again; Saved backup	Z2 CPSN	Applied	L	cp_config_20210815_1510.bin	20210815
2022	Jul	1	Fr					Since 8/6/21 I've been using DHCP for the WAN interface; In preparations for trip to Colorado I set fixed IP 137.83.25.170 as per CPSN MASTER CONFIGURATION / Configured port forwarding for incoming VNC connections to T400s and JAK2 as per CPSN MASTER CONFIGURATION; Saved backup	CPSN			cp_config_20220701_0806.bin	20220701

## Z2
Miscellaneous: Z2	A					CP_2: CradlePoint MBR95

Date/Time CST/CDT					Description	Other Sources	Status	Location	Backup
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L	cp_config_20210806_2110.bin
2015	Aug	16					Ordered from eBay	EML SSRP	On Order			20150816
		20					Received: Very poorly packed, loose in box, no static or water wrapping	SSRP	Available	L		20150820
2018	Jun	15		~	17:45	~	18:00	Bench test of PS_3 (V6): CradlePoint 4w @ startup, 3w continuous			L0		20180615
		21					This history sheet created; Inventory Sticker applied		Assembly	MA2		20180621
2020	May	30					Bench cleaned and parts for assembly boxed with labels “MA2”	MA2				20200530
2021	Aug	5					Started setup to replace CP_1 for Shop LAN: CP_1 crapped out and may be defective; See CPSN for extreme details of process and helpful notes on the "state of the system"	L1 Z1 CPSN	Applied	L	cp_config_20210805_1610.bin	20210805
		6					Completed setup; Flawless operation; Also see CPSN "Attempted Test of iPhone Backup Internet"	CPSN			cp_config_20210806_2110.bin	20210806
		15	Su					Tested CP_1 which was found to be 100% AOK after reset and restoration of configuration from cp_config_20210806_2110.bin; CP_2 Bagged as Spare	Z1 CPSN	Available			20210815

## Z3
Miscellaneous: Z3	A					TEC_1: TE Connectivity V23130-C2021-A412

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	16					[Z3-4] Downloads to Library / Ordered from DigiKey / Ordered 4 position plug assemblies for these latching relays from Mouser	LIB EML SSRP DKE MOU	On Order		20150816
		19					[Z3-4] Received; Slated for SAPS		Available	L	20150819
2018	Mar	10					[Z3-4] More downloads to Library	LIB			20180310
	Jun	21					[Z3-4] This history sheet created; Inventory Sticker applied				20180621
		29					[Z3-4] Bench testing using BK_1, PS_3 (V6), I8O8_1 and TEC_1; Works OK, contact resistance is less than 0.1 ohms (Fluke 8000A); Cut flange from around connector and soldered wire to pins (TEC_1/2) / Coil power is 30-35w, not to be provided by PS_3 (V6), because relay specifications state they should make/break at 6v coil		Assembly	MA2	20180629
2020	May	30					[Z3-4] Bench cleaned and parts for assembly boxed with labels “MA2”	MA2			20200530

## Z4
Miscellaneous: Z4	A					TEC_2: TE Connectivity V23130-C2021-A412

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	16					Z3-4	LIB EML SSRP DKE MOU	On Order		20150816
		19					Available	L	20150819
2018	Mar	10					LIB			20180310
	Jun	21					20180621
		29					Assembly	MA2	20180629
2020	May	30					MA2			20200530

## Z5
Miscellaneous: Z5	A					MS_1: Murata 3020-01101-0

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					[Z5-10] Downloads to Library / Ordered from Mouser	LIB EML SSRP MOU	On Order		20150819
		22					[Z5-10] Received		Available	L	20150822
	Sep					Installed in 6x6x4" box on bumper of Subaru			MA2	20150922
2018	Jun	21					[Z5-10] This history sheet created; Inventory Sticker applied				20180621
	Jul	4					Removed from 6x6x4" box on bumper of Subaru in order to install in SAPS Equipment Box		Assembly		20180704
2020	May	30					[Z5-10] Bench cleaned and parts for assembly boxed with labels “MA2”	MA2			20200530

## Z6
Miscellaneous: Z6	A					MS_2: Murata 3020-01101-0

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					Z5-10	LIB EML SSRP MOU	On Order		20150819
		22					Available	L	20150822
2018	Jun	21					Z5-10				20180621
	Jul	4					Installed in SAPS Equipment Box		Assembly	MA2	20180704
2020	May	30					Z5-10	MA2			20200530

## Z7
Miscellaneous: Z7	A					MA_1: Murata DCA5-20PC-6-DC4-RL-C

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					Z5-10	LIB EML SSRP MOU	On Order		20150819
		22					Available	L	20150822
2018	Mar	9					[Z7-10] Meters tested on the bench for a few days (1 ammeter and 1 voltmeter, not sure which ones exactly, approximate date)				20180309
	Jun	21					Z5-10		Assembly	MA2	20180621
2020	May	30					Z5-10	MA2			20200530

## Z8
Miscellaneous: Z8	A					MA_2: Murata DCA5-20PC-6-DC4-RL-C

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					Z5-10	LIB EML SSRP MOU	On Order		20150819
		22					Available	L	20150822
2018	Mar	9					Z7-10				20180309
	Jun	21					Z5-10		Assembly	MA2	20180621
2020	May	30					MA2			20200530

## Z9
Miscellaneous: Z9	A					MV_1: Murata DMS-20PC-0-DCM-B-C

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					Z5-10	LIB EML SSRP MOU	On Order		20150819
		22					Available	L	20150822
2018	Mar	9					Z7-10				20180309
	Jun	21					Z5-10		Assembly	MA2	20180621
2020	May	30					MA2			20200530

## Z10
Miscellaneous: Z10	A					MV_2: Murata DMS-20PC-0-DCM-B-C

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Assembly	MA2
2015	Aug	19					Z5-10	LIB EML SSRP MOU	On Order		20150819
		22					Available	L	20150822
2018	Mar	9					Z7-10				20180309
	Jun	21					Z5-10		Assembly	MA2	20180621
2020	May	30					MA2			20200530

## Z11
Miscellaneous: Z11	A					DI_1: Dwyer Instruments PLVT1

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2015	Sep	8					Ordered from Amazon.com	EML SSRP	On Order		20150908
		10					Received		Available	L	20150910
2018	Jun	22					This history sheet created; Inventory Stickers applied; Battery stickers applied (as per ones in shop)				20180622
		29					Bench test on PS_4 (I1)	Slated for SAPS		L0	20180629
	Jul	1					Decision made not to use in SAPS project (MA2): stored near center door with stuff for hot water heater control		Available	L	20180701

## Z12
Miscellaneous: Z12	A					VC_1: Vag Com KKL 409.1

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Applied	MA2
2018	May	22					Ordered from eBay seller ndbdsch: For use with FreeSSM software to diagnose and repair problems with Subaru and for further abilities to interface with the SAPS Wattmon system	EML SSRP	On Order		20180522
		25	Fr		10:53			Received in mailbox		Available	L	20180525
		26	Sa					Inventory stickers applied			L0	20180526
		29	Tu	~	04:00			T450s, being used to diagnose Subaru problems		Applied		20180529
		30	We					Semi-permanently installed in Subaru			MA2	20180530

## Z13
Miscellaneous: Z13	A					Ai11: Apple iPhone 11 Pro Max

Date/Time CST/CDT					Description	Other Sources	Hours	Total Hours	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				228	Active	L
2020	Jun	7	Su					I dropped my Samsung phone in the MO river; I immediately began looking at phones to buy; #1 priority is one with a good camera / Reviews always come up with Apple iPhone 11 Pro being the phone with the best camera		2.00	2.00	Research		20200607
		8	Mo					Chat with Consumer Cellular support (transcript EML); Ordered a replacement SIM Card (free)	EML CC	1.00	3.00			20200608
		13	Sa					Rec’d SIM Card	CC	0.05	3.05			20200613
		17	We	~	06:00	~	10:00	Created Summary entry and History sheet; Serious now about this iPhone purchase because yesterday TurboNet paid me $1450 for (3) W100s; Final research before ordering / Display brightness (800 to 1200 cd/m2 typical) and color accuracy are rated very highly according to review at DisplayMate.com / (see Library, this technically accurate analysis of the display gives the highest ratings for display quality of ANY smartphone yet reviewed) / Samsung i9300 Galaxy S3 was <250 cd/m2 brightness (some reviews say <200 cd/m2); Some Otter Box case research, but more research needed there yet; Apple Store, placed order #W964202191 / Created Apple ID Jeff@DataVisionServices.com, JKlute2020	EML LIB SSC	4.00	7.05	On Order		20200617
				Invoice received	Ai11P	0.05	7.10			20200617
		18	Th	~	04:00	~	09:30	20200618 Wikipedia iPhone 11 Pro.pdf; Case research; RokForm order and questions prepared (CA, not open yet) / 20200618 Apple iPhone User Guide.url; 20200618 Safety, Warranty and Regulatory Information – iphone-11-pro-max-info.pdf; TODO	LIB	5.50	12.60			20200618
				~	10:00	~	11:45	Call to RokForm (and chat recommended that is what I should do); The issue with the “extra hand needed to hold the charger to the dash mount while removing the phone” is more or less resolved as “I will gum up the works on the RokLock on the charger that attaches to the dash mount so that it is tighter than the phone’s RokLok”; The tripod mount has been discontinued due to “lack of sales” and “lots of people don’t use a tripod anymore”; I urged them to reconsider and NOT drop this accessory from their line; They don’t know when they will, if ever, remanufacture the tripod mount; TODO Try to find a tripod mount from a distributor that has stock (eBay? Anywhere in the world); Shipping is same day if ordered before 3pm CA time; Shipping is free on orders >$100 (USPS priority mail, 1-3 business days); Chat messages with RokForm (gum up the works, tripod mount); Order placed with RokForm; I earned 980 “points” and signed up for customer account (34157934); More research (mostly iCloud, but general phone browsing)	Viber EML Ai11P SSC	1.75	14.35			20200618
				15:17		17:30	Apple iPhone received …; Unboxed (but not turned on, I was not feeling well)	Ai11P	2.22	16.57	Available	L	20200618
		19	Fr	~	01:30	~	03:15	iPhone first time setup: Press and hold side button; Swipe up; English > United States; Set Up Manually; MBR95, abig2304; “… activate …”; Face ID setup; Passcode 3415; Don’t Transfer Apps & Data (I’m going to have to do ths manually later on); It did not accept what I though was my Apple ID (Jeff@DataVisionServices.com, JKlute2020, “Incorrect Apple ID or Password”); Visited https://appleid.apple.com on T450s and verified ID (that had not been done yet, 06/11/1956, What was the first thing you learned to cook? Pudding; What was the model of your first car? Oldsmobile; What is the name of the street where you grew up; Cureton); Successfully entered Apple ID jeff@datavisionservices.com (lower case), JKlute2020; Terms and Conditions sent by email (4); Welcome to iCloud EML; Express Settings > Customize; Keep Your iPhone Up to Date > Install Updates Manually; Location Services > Enable; Pay >Set up later in Wallet; Siri > Initial voice recognition; Improve Siri & Dictation > Not Now; Screen Time (weekly report, parental controls) > Set Up Later in Settings (don’t bother) / Analytics > Don’t Share; True Tone Display > No option to change anything here, it’s probably on; Appearance > Dark; Display Zoom > Zoomed	EML	1.75	18.32	Setup	L0	20200619
				~	03:15	~	03:45	Settings: Display & Brightness > Auto-Lock 30 Seconds → 5 Minutes; Text Size > Up one notch from center; True Tone > OFF; Night Shift is already OFF		0.50	18.82			20200619
				~	03:45	~	04:30	Installed CC Nano-SIM: User’s Guide does not say to turn the phone off 1st; Installed SIM; CC site says to repower phone, so rebooted; CC website Activation; Step 3 Test Call failed (2x); Phone restarted; Test OK / *#06# Device Info EID 89049032005008882600047691323829, IMEI 352844110577587, IMEI2 352844110601064, MEID 35284411057758; CC site Step 4 IMEI 352844110577587, Jeff@DataVisionServices.com / Text messages rec’d; CC site Finish Activation; But setup is not complete (see printout in CC); TODO call CC when support is open at 07:00 CDT (05:00 PDT)	SSC	0.75	19.57			20200619
				~	04:30	~	05:45	TODO concerning DWL-7200AP which is inop; CradlePoint DHCP Reservation 90.0.0.15, Jeffreys-iPhone, 88:a4:79:ee:5d:d7 / RokForm case order not to be received until Mo6/22 (so being VERY CAREFUL as I don’t want another Pirosmani Hotel Experience)	CPSN	1.25	20.82			20200619
				~	05:45	~	06:15	Added iPhone User Guide to Books; I’m not sure it’s downloaded, but it should be; TODO try accessing User Guide when no internet		0.50	21.32			20200619
				~	06:15	~	07:00	Played with Compass app but failed to find out how to access it w/o Siri (could not find on Home screen); TODO after case is rec’d calibrate and setup Compass app		0.75	22.07			20200619
				~	07:00	~	08:15	Called CC to finish setup … FaceTime enabled; Test MMS not rec’d; Must hang up and reset network settings; Settings > General > Reset > Reset Network Settings / I should get test MMS from them, if I don’t call them back; After 20’ no MMS rec’d; Called Marcus, he called me back OK; Asked him to send me an MMS; Rec’d and replied (picture of truck)	CC MMS	1.25	23.32			20200619
				~	08:15	~	11:15	Constantly experimenting with new iPhone; The feature that has now improved my productivity the most is Siri / “Hey Siri, set a timer for 47 minutes” (very, very useful) and “Hey Sir, go away” is good also (although can swipe up) / Retrieved Voice Mail, oldest Th6/11; Two factor identification setup for iCloud; Email account created jeffreyklute@icloud.com	EML	3.00	26.32			20200619
		20	Sa	~	01:30	~	09:00	Researched various and sundry means to restore the Android content to the iPhone, Cloud transfer of photos and video, ongoing backups and management of files via Win7, Photo Steam, iCloud for Windows, Coolmuster iOS Assistant, s/b able to use Windows Explorer (or XY) to DCIM, AnyTrans, etc… / Manually transfering phone contacts by reference to 20200404 Contacts.html (backup made with Coolmuster) and adding them on iCloud.com (which updates the phone immediately) as they need cleaning up and labeling anyway (>200, decided not to add country codes to US numbers, although if in Ukraine I may have to edit them) …	SSC	7.50	33.82			20200620
				~	12:00	~	16:45	Continued iCloud.com Contacts updates from 20200404 Contacts.html: Groups USA (no country code) and Not USA (w/country codes) / This project did not take as long as is recorded here, because as I worked on the Contacts list all sorts of questions came up, which I would research / (Who are they? When and where did I meet them? Do I have other links to these people, such as FaceBook and websites, etc.?); Any dead or no longer useful contact was skipped; Finished with 177 Contacts (was 220)		4.75	38.57			20200620
		21	Su	~	03:00	~	06:15			3.25	41.82			20200621
				~	05:15	~	09:30	Tested via USB on T450s: God is My Provider; I had not bought a USB-C adapter, so I thought there was no way to connect using the older larger USB ports; BUT on the day I was boating with Marcus and dropped my phone in the river I found an Apple Lightning to USB cable at the boat dock on the ground; I took it home and hung it up with the other USB cable stuff in the main shop (I kept it even though at the time I thought I had no use for it); That cable was exactly what I needed, and God gave it to me on the day my old phone was lost; SMS to Marcus; Can browse DCIM on Apple iPhone using Windows Explorer or XY (empty, I haven’t used the camera yet); Cannot create files or folders in DCIM; Files can be added using iCloud Photos, but they don’t go into DCIM, they must be organized into Albums or Folders, and “Only files in JPEG format can be uploaded” / First images INCREDIBLY SHARP, including the video, using only natural lighting (I did not turn on any extra lights), and no need to shoot duplicates to be sure I get a sharp one!; Settings > Photos > Download and Keep Originals (do NOT Optimize iPhone Storage, which can replace the photos on the phone with reduced size files and makes the originals only available from iCloud); Photos shot at 07:30 were available on Icloud Photos in 11 minutes (phone charged and connected to WiFi, although iOS 13 s/b able to use Mobile data to upload them); I could not use XY to copy the files from DCIM (“Error Copying File or Folder, A device attached to the system is not functioning.”); Tried again after reconnecting phone via USB and managed to get IMG_0001.JPG and .MOV; Restarted but same error; Downloaded from iCloud Photos OK (interesting that it changed the file type IMG_0002.MOV to .MP4); On T450s all the files are useable (.MOV QuickTime Movie opens with WMP, .MP4 opens with VLC) / Research “Is it possible to change iPhone photo naming conventions?” - NO (biggest disappointment with iPhone I’ve yet encountered) / TODO Play with BFR (Better File Rename); TODO More research on finding software for Win7 to change iPhone picture file names to include date and time	SMS IMG	4.25	46.07			20200621
		22	Mo	~	04:30	~	06:00	FaceTime call I made yesterday used about 10MB cellular data (and about 15MB WiFi); Cellular data usage since 1st time setup on Fr6/19 102 MB (at that average I’ll be going over my CC Connect Plan of 500MB) / Reset statistics; Set monthly reminder starting 7/21/20 11:55 PM “Consumer Cellular cycle end”; Set AutoLock to NEVER (easier when working with phone which is easy to lock with side button)		1.50	47.57			20200622
				~	06:00	~	07:00	Turned off notifications for Apple Wallet and Apple Pay (Settings > Notifications > Wallet > Allow Notifications OFF / Settings > Wallet & Apple Pay > Apple Cash and Double-Click Side Button OFF; Settings > Safari > Check for Apple Pay OFF; Finish Settings Up your iPhone > Set Up Apply Pay > Cancel)		1.00	48.57			20200622
				~	07:00	~	08:00	Updated iOS 13.3.1 → 13.5.1; iOS Automatic Updates are OFF (that was done during 1st time setup) but there appears to be no way to disable the automatic download of a new iOS (which probably doesn’t occur on mobile data); iTunes & App Store > App Updates OFF (all other AUTOMATIC DOWNLOADS are already OFF), CELLULAR DATA App Downloads > Always Ask		1.00	49.57			20200622
				~	08:00	~	09:45	Experiment: Settings > General > iPhone Storage > GarageBand (1.7GB) > Offload App; Leaves icon on the Home screen but puts a Cloud Download icon next to it; Pressing it takes you to the info on the App but I could find no way to install it; General > iPhone Storage > GarageBand (now way down the list) > Reinstall App same message “Unable to Install ‘GarageBand’ You must purchase this app to install it.” > View in App Store and no download button, but a circle with a square; Research that square is the download progress bar, tapping it stops the download; After an hour nothing much has happened, but it could be downloading in the background / GarageBand is free for all iOS devices; Settings > General > iPhone Storage > GarageBand (549 KB) > Delete App (gone from the Home Screen); App Store > Search > GarageBand for iPhone > GET / Shows downloading in AppStore and on the 2nd Home screen Icon with “Loading…”		1.75	51.32			20200622
				~	09:45	~	10:00	Rearranged Home screens: Unused and less important Apps on 2nd Home screen (which is now full) and I only have 12 Apps on the 1st Home screen		0.25	51.57			20200622
				~	10:00	~	10:45	Accessibility > Voice Control > Set up Voice Control (download); Can now speak “Lock Screen”, “Reboot Device”, and while editing text there are some helpful voice commands / There are hundreds of voice commands, say “What can I say” or “Show Commands”; Also discovered method of moving the cursor into the middle of a word (press once, then long press again)		0.75	52.32			20200622
				~	10:45	~	11:15	Accessibility > Touch > Assistive Touch > Devices > Bluetooth Devices: Paired spare Bluetooth mouse from leather bag and turned on Assistive Touch		0.50	52.82			20200622
				~	11:15	~	11:30	Discovered the best way to edit text with the keyboard: / Press and hold the spacebar and the whole keyboard becomes a trackpoint, which makes moving the cursor accurately very easy, as you can see exactly where it is as it isn’t covered up by your finger		0.25	53.07			20200622
				~	11:30	~	12:15	Signed up for Apple TV+ Free Year: USB $4.99/month after 6/21/21; Some initial trials, but I don’t have time to watch now	EML SPF	0.75	53.82			20200622
				~	12:15	~	14:30	RokForm case and accessories arrived; Installed in case and applied screen protector; I have a small bubble probably caused by dust particle, will wait and see if it improves; Protector is crooked; I’m not real happy but each one is $30; Installed wireless charger in Subaru; Settings > Display & Brightness > Raise to Wake OFF (I don’t want the phone coming on when I move it around); Lanyard causes it to rock when placed on a flat surface		2.25	56.07			20200622
				~	14:30	~	15:00	Google Maps App installed; Settings > Privacy > Location Services > Google Maps > Always		0.50	56.57			20200622
				~	15:00	~	16:30	Viber App installed; T450s required scan of QR code (OK); Stuck on “Rakuten Viber, Loading…” for a long time; Reboot device and was able to finish activation; Auto Backup Daily (text messages only) / Chat History and images are still on T450s, but iPhone has no history at all; Sent test message to Gem; Learned how to take screenshots (IMGs)	SMS IMG	1.50	58.07			20200622
		23	Tu	~	10:45	~	13:30	Feedback to info@rokform.com; Email reply “please call”; Called 855-765-3676, 3x NA, did not leave a message …; 4th call LMVM	EML	2.75	60.82			20200623
				~	15:00	~	15:25	Experiments with BFR on photos downloaded from iCloud.com …		0.42	61.23			20200623
				~	15:25	~	15:35	Rec’d call from RokForm, but after explaining that it was them that called me she went away to review the email and then we lost the connection [note added later: they haven’t called back yet as of Mo6/29 01:00]		0.17	61.40			20200623
				~	15:35	~	17:20	… Continued experiments with photos downloaded from iCloud.com Su6/21; Using BFR to rename them after downloading them from iCloud turned out to be a big pain (I’ve already got TODO for looking for better software); The Date Taken dates and times are recorded in UTC (probably an aspect of the AFS); XY can show previews of JPEG, MOV and MP4 files, but can’t decode the HEIC or Unmodified Original MOV; JPEGs can be opened with Windows Photo Viewer; MOVs except “Unmodified Original” open with WMP; VLC opens the MP4s; HEICs can’t be opened with anything I have on T400s; Suggest that from now on if downloading from iCloud.com “Unmodified Original” is also saved in Photos Backup, but not in the culled set, as for now all of those can’t be previewed or opened from XY on T400s; Culled by deleting “Unmodified Original” files; ViewNX2 previews only the JPEG files and show that they are only 2048x1536 (Android JPG were 3264x2448); Adobe Photo Shop Elements opens the JPEG files (but I didn’t try to edit them); Research; Camera > Formats > Most Compatible; This will take more storage space but preserve compatibility with different programs or platforms (Windows); As far as I can tell, the newer HEIF formats are useable only on Macs and the phone or iCloud make attempts at converting this to JPG; I’d rather have the original be a JPEG than use the newer formats which aren’t compatible with all of my programs and platforms; Reviewed Camera > Record Video settings and left them at default (1080p at 30fps, Slo-Mo at 720p and 240fps)		1.75	63.15			20200623
				~	17:20	~	19:30	Shot another series of photos and videos; Fill flash didn’t work very well for the plants in the window, but the natural light ones were very good (HDR); All photos handheld, very sharp and no duplicates needed; Used all 3 lenses 0.5x (super wide angle), 1x (normal), 2x (telephoto); Photos were available on iCloud starting within minutes and by 18:04 when I checked they were all available (less than 30 minutes, phone on WiFi but not locked); Photos and videos on iCloud are now 289MB; Direct USB connection to T450s, but again same error “A device attached to the system is not functioning” and was able to get only some of them (35 to transfer, managed only 11); Photos > Cellular Data > Unlimited Updates ON (unlimited use of cellular data to upload and download to iCloud Photos when not connected to WiFi); Settings > Photos > TRANSFER TO MAC OR PC is already set to Automatic (not Keep Originals); All xfers from iCloud do not include MP4 files (MOV); Screenshots in Most Compatible are JPG but the same screenshots in Unmodified Originals are PNG (this is a good reason to save both the Most Compatible and Unmodified Originals in Photos Backup); "Hey Siri, please marry me" (IMGs)	IMG	2.17	65.32			20200623
		24	We	~	07:00	~	07:15	Photos shot of Marcus and Boom Truck; Culled on the phone		0.25	65.57			20200624
		25	Th	~	05:40	~	06:45	Revisited Settings > Photos > Cellular Data: Unlimited Updates is available only if Cellular Data is ON (research reveals that if Unlimited Updates is OFF the phone will use a maximum of 150MB per day or somehow other throttle data use); Left Unlimited Updates ON and turned OFF Cellular Data / If I am ever in a situation where immediate sync is needed and I’m not worried about the data plan then use Cellular Data ON and Unlimited Updates ON		1.08	66.65			20200625
				~	06:45	~	08:30	Settings > Photos > TRANSFER TO MAC OR PC, Automatic → Keep Originals; Tested Direct USB connection to T450s again, no more errors; Worked on Images … All 3 methods of retrieving the photos from the iPhone are identical for the latest set from 6/24 (Marcus and Boom Truck); Direct USB to T450s (Originals) = iCloud Photos Most Compatible Including Edits = iCloud Photos Unmodified Originals		1.75	68.40			20200625
				~	08:30	~	13:00	Worked on 1st 3 sets of Images to test ORCTPM; BFR droplets created (JPG/JPEG requires local time, MOV requires UTC time, screenshots and photos edited on iPhone have no Date Taken information and must be manually renamed by context or reference to Photos on phone or iCloud); Some problems with XY fixed; Noticed that latest image sizes are now 4032x3024 (test set 1 was 2048x1536)	SSC IMG	4.50	72.90			20200625
		26	Fr	~	02:00	~	06:30	T400s Xyplorer, BFR Droplets on Desktop added to XY Catalog; More browsing on transferring photos and videos back and forth to iPhone; Tested Windows Import Pictures and Videos T400s / Noticed that IMG_0029.MOV (Marcus and Boom Truck) cannot be opened with Movie Maker (T400s) / Tested using Settings > Photos > TRANSFER TO MAC OR PC, Automatic with Windows Import Pictures and Videos T400s; Same error as before but there was an option to continue / Movie Maker still can’t open IMG_0029.MOV; Restored Settings > Photos > TRANSFER TO MAC OR PC, Keep Originals / Decided what to do with DCIM originals on iPhone (delete them after they’ve been properly transferred, uploads of ORCTPM organized photos and videos to iCloud Drive, pay Apple what they want for enough storage to shoot a whole bunch of photos and videos and delay getting them transferred) / TODO on shooting another test set; Started images for update of XY to latest version	T400s	4.50	77.40			20200626
				~	21:00	~	22:05	Examined Windows Import and noticed that Windows is setting the Created and Modified datetimes correctly to the Date Taken datetime even for files that don’t have a visible Date Taken / This means that if I use Windows Import BFR can rename all of the files in one pass from the Created datetime / However, I’m not so sure that Apple didn’t modify the Created datetimes this morning for some reason (background processing); There’s a lot of confusion going on, I’m going to have to run another test set / Looking at first 3 sets directly in DCIM they all have correct Created datetimes; Evidently iCloud Photos transfers are also getting the correct datetimes, I don’t know		1.08	78.48			20200626
				~	22:05	~	23:45	Sorted Windows Import files into Photos Backup and Images for first three sets 6/21, 6/23 and 6/24; Deleted DCIM files; ORC finished for first 3 sets		1.67	80.15			20200626
		27	Sa	~	00:15	~	00:30	Camera > Live Photos OFF; In general I don’t want this ON, as it consumes more memory and creates .MOV files I end up deleting; Also research shows it can interfere with low light photos, as the camera has to continue shooting video and can’t use a long series of photos to create the image; Note that Settings > Camera > Preserve Settings > Live photo s/b ON to preserve the Live Photo setting		0.25	80.40			20200627
				~	07:30	~	08:30	T400s Xyplorer updated to latest version (it makes no difference to previews of MOV files)		1.00	81.40			20200627
				~	08:30	~	09:10	Noticed that iCloud backup had not occurred since 4 days ago; Phone must be attached to power, on WiFi and Locked in order for automatic backups to occur every 24 hrs / A missed backup should run as soon as conditions are met; Manual backup OK (Back Up Now @ 08:38) / The only reason I can think of as to why it isn’t backing up every day is that I’ve been running the phone a lot without letting it sleep (lock) and at night I’ve not been charging it (using it next to bed) / Settings > Display & Brightness > Auto-Lock 5 Minutes		0.67	82.07			20200627
				~	09:10	~	11:00	Installed iCloud for Windows on T400s; Tested screenshot on iPhone, it showed up on T400s within 30 seconds; Renamed that file and copied it into Uploads, SysTray shows that iCloud Photos was updated, but I can’t find it on iPhone or iCloud.com Photos; DCIM shows only the original IMG_0031.PNG; Search on iPhone Files cannot find “2020” or a bunch of other searches for that Upload; Moved 20200627 2253 IMG_0031.PNG to C:\Users\Jeff\ICloudDrive, SysTray shows that iCloud Drive was updated, iPhone Files > iCloud Drive shows it; iCloud.com shows it after Refresh Page; Further tests and configuration, see T400s and JAK2 Setup Notes	SSC LIB T400s JAK2 IMG	1.83	83.90			20200627
				~	20:00	~	02:30			6.50	90.40			20200627
		28	Su	~	09:15	~	10:30			1.25	91.65			20200628
				~	10:30	~	13:45	Worked on seeing if there is a fix for XY Preview of MOV files; K-Lite Codec Pack Downloaded and Installed on T400s; XY now previews and creates thumbnails for .MOV / Windows Explorer now shows thumbnails for .MOV; I like the included MPC-HC (Media Player Classic Home Cinema) which is now the default association for all video files / Can’t preview or open HEIC files, see T400s Setup Notes for some quick research on opening HEIF files; Movie Maker now opens .MOV / Changes to T400s replicated to T450s and JAK2 as much as possible (XY, iCloud, K-Lite) …	SSC LIB T400s T450s JAK2	3.25	94.90			20200628
		29	Mo	~	01:00	~	05:00			4.00	98.90			20200629
				~	05:40	~	06:00			0.33	99.23			20200629
		30	Tu	~	02:30	~	08:10			5.67	104.90			20200630
				~	07:00	~	07:15	Accessibility > Voice Control > Attention Aware ON; This keeps it from entering text or executing commands from nearby music or conversations / Commands that work with this include “Wake Up” and “Go to sleep” which overrides and changes whether or not it is ON		0.25	105.15			20200630
				~	13:00	~	17:00	… Tests of iCloud for Windows on T450s reveals that I should reconfigure the systems on T400s and T450s; TODO Move G:\iCloud\Photos to G:\Photos Backup\iCloudPhotos (Downloads, Shared, Uploads); TODO Rename G:\iCloud\Drive as iCloudDrive; TODO T400s and JAK2 AWS sync G:\iCloud changed to iCloudDrive; TODO T450s CrashPlan inclusion for G:\iCloud modified to iCloudDrive; Work flow notes in T450s Setup Notes “If we don’t have WiFi, or don’t want to use Mobile data for iPhone or T450s, then use Windows Transfer (Photos Backup). Otherwise, copy the downloaded photos to Images and go from there. When copied and backed up, delete the photos on iPhone or iCloud.com.”; T450s iCloud reconfiguration and image; T400s iCloud reconfiguration; T400s and JAK2 AWS reconfiguration; …	T450s T400s IMG	4.00	109.15			20200630
2020	Jul	1	We	~	02:45	~	04:15			1.50	110.65			20200701
				~	08:00	~	08:30			0.50	111.15			20200701
				~	10:30	~	12:40			2.17	113.32			20200701
		3	Fr	~	08:15	~	10:00	Cellular > Set Up Personal Hotspot > “To enable personal hotspot on this account, contact CC at 611 or visit http://www.consumercellular.com/myaccount”; Nothing found on website, called 611, 0733 … Kimberly, tethering was turned off, she turned it on; (R) and now there is Settings > Personal Hotspot; Allow Others to Join YES (devices signed into iCloud do not need the password) / WiFi Password 4jhebtjz6tyrr → 34157934; Unlike Samsung phone it is always on even if iPhone is connected to WiFi; Settings > Personal Hotspot > Allow Others to Join > On/Off to control it		1.75	115.07			20200703
		4	Sa	~	05:30	~	12:00	Setup WiFi as WAN on CP_1 (partially completed, more TODO); If we lose TurboNet use Settings > Personal Hotspot to make iPhone discoverable by CP; Notes on research in CPSN “Is there any way to keep the iPhone Discoverable even when Hotspot is not being used?” (I’m not going to pursue this now, as it doesn’t look very promising and I’d rather stick to a “manual ON” situation until cellular data is “less expensive”)	Z1 CPSN IMG	6.50	121.57			20200704
		5	Su	~	06:15	~	06:45	I discovered the reason why I’ve been missing calls and text messages: The Ring / Silent switch was on Silent (orange bar); Research, did not find a visible notification app		0.50	122.07			20200705
				~	06:45	~	11:30	Continued configuration of CP_1: SMTP notifications/alerts to Jeff@DataVisionServices.com for WAN Device Status Changes and Data Usage	Z1 CPSN	4.75	126.82			20200705
		6	Mo	~	03:30	~	07:15	Setup/tested iPhone Personal Hotspot on T450s using WiFi and Bluetooth; Research into how to tether with USB; TODO Install selected files from iTunes as per TDCatTech; Started Image of T450s	T450s	3.75	130.57			20200706
		9	Th	~	00:00	~	03:15	K-Lite Codec Pack installed on T450s: XY .MOV thumbnails and previews are not rotated as per sensor data, but Windows Explorer thumbnails are OK / Other than these rotation problems T450s is identical to T400s in behaviour		3.25	133.82			20200709
				~	03:15	~	03:50	Added columns Hours and Total Hours to this History sheet as I’d really like to have an idea how long it takes to setup and maintain the iPhone and associated systems on the network		0.58	134.40			20200709
				~	03:50	~	05:30	Replicated changes needed on T400s and T450s to JAK2 (XY, BFR, K-Lite Codec Pack) / Hey Siri 'what date is 45 days from now', iPhone screenshot	JAK2 IMG	1.67	136.07			20200709
				~	18:05	~	20:15			1.67	137.73			20200709
		10	Fr	~	06:00	~	08:50	Setup and tested Personal Hotspot connected via USB to T450s; Works fine except when T450s is reboot it must be reset (WiFi would automatically connect after a reboot) / It interferes with ability to browse to DCIM or use Windows Import; Uninstalled Apple Mobile Device Support; Configured Windows Import (I had used it before on T400s)	T450s	2.83	140.57			20200710
				~	09:10	~	10:20	Better File Rename updated to latest version I’m entitled to / No problems with T400s and T450s, but JAK2 is only partially operational (BFS and BFR don’t work, and I haven’t tested BFA)	T400s T450s JAK2	1.17	141.73			20200710
		11	Sa	~	05:15	~	06:40			1.42	143.15			20200711
				~	07:15	~	09:00			1.75	144.90			20200711
		12	Su	~	03:10	~	07:30			4.33	149.23			20200712
				~	23:30	~	03:45	ScreenShot Captor (SSC): / Updates to latest version / Troubleshooting of “Bogus Metadata added to .JPGs” and other issues / DonationCoder.com Forum posts “JPG Bogus Metadata Replication to Subsequent Captures” and “Request JPG Caption Metadata CR_LF not just LF” / EML 20200716.9 Forum Donation Credit Claim Link doesn't work.pdf	T400s T450s JAK2 LIB EML	4.25	153.48			20200712
		13	Mo	~	15:15	~	19:00			3.75	157.23			20200713
		14	Tu	~	02:20	~	06:20			4.00	161.23			20200714
				~	16:00	~	00:00			8.00	169.23			20200714
		15	We	~	07:45	~	08:45			1.00	170.23			20200715
		16	Th	~	02:55	~	04:00			1.08	171.32			20200716
				~	05:45	~	06:45			1.00	172.32			20200716
				~	07:30	~	08:00			0.50	172.82			20200716
				~	15:30	~	18:45			3.25	176.07			20200716
				~	18:45	~	20:30	Better File Tools Series: Problems on JAK2 addressed	JAK2	1.75	177.82			20200716
		17	Fr	~	14:00	~	18:00	Researched “How to stop iPhone Files from modifying a LAN file when it is opened?”; Google search could find nothing about this; Marked all files in “G:\AV\Other Audio\Grey, Zane - The Forlorn River - Jack Sondericker, Books In Motion, 9 CDs” as Read-only, played 1st track with iPhone Files, when I moved to the 2nd track Files locked up and a few minutes later Files had to be restarted; I think the problem only applies to .mp3 files (it may be trying to write some obscure tag such as last played date/time); Tested again, and no problems (the iPhone Files lockup/restart could have been due to something else); Testing with .mp3 files that are not Read-only shows that the modification occurs when the file starts to play; The iPhone places a lock on the file until it is restarted; The Read-only attribute is copied with the file when AWS syncs it, but if applied after the sync AWS does not think the file has been modified and so doesn’t sync it; I want the ability to play music files on the iPhone from the LAN, and marking my entire music collection Read-only on (4) computers (including the NAS) just doesn’t appeal to me; Removed Read-only from files I had marked that way; Installed and tested iPhone app Flacbox (it was the first app I came to that talked up front about directly accessing files on computer or NAS with SMB); Flacbox works great for what I need; Connected quickly and perfectly with NAS; Does not modify .mp3s that are played; Skip time buttons; Controllable when iPhone is locked; Plays all in a folder (no need to create a playlist); Settings > Audio Player > General > Audio player buttons on the main lock screens > Skip time 10 seconds; Music library > Album covers > DO NOT Download automatically (it gets them wrong) / Interface > Number of items per page > All		4.00	181.82			20200717
		20	Mo	~	05:00	~	06:55	Research into methods to retrieve a COPY of SMS/MMS/iMessages in a form that I can use with other applications: I found two products both from imobie.com; Phone Rescue accesses the iCloud backup to extract and manipulate data from it, and can also add messages to iPhone (1st choice for now); AnyTrans does it directly from the phone with a USB/Lightning cable; Both products come with $ attached, and they aren’t “up front” about “Free Trial” limitations; Further research is needed, but I don’t need either tool until I need to copy and paste a lot of messages from the iPhone to other applications on the network / Uninstalled Coolmuster Android software from T450s	T450s	1.92	183.73			20200720
		23	Th	~	09:15	~	12:30	Chat with Consumer Cellular support (transcript EML); WiFi calling feature turned OFF on their end; Test call to Gem OK (was NOT required to reenter the entire phone number manually); Cellular > Wi-Fi Calling is OFF / Further research into how to format and store phone numbers in Contacts; "Always use +"; "For most compatibility always add the + prefix. It doesn’t matter where you are (i.e. which carrier is hosting your connection) it’s understood that what follows the + is a complete dialing instruction including country code, area code (if applicable), and local number"; "If international calling is something you're going to be doing, ALWAYS use the +(country code) format"; Further research (how to accomplish all this with iCloud and iPhone Contacts); It is not clear what Dial Assist does, exactly, and it may be a problem in my case; Phone > Dial Assist OFF; You would think that if I get all of Contacts to use International Dialing format (+CountryCode AreaCode Number) that this setting would make no difference, but I need to also see if incoming phone numbers can be saved to Contacts with the CountryCode; Cellular > Wi-Fi Assist is ON by default (Automatically use cellular data when Wi-Fi connectivity is poor, not changed); "What are the disadvantages of WiFi Calling?" answer "Restrictions on international calls"; TODO Convert all Contacts to "fully qualified" International Format with out extraneous spaces	EML 3/7/22 3/15/22	3.25	186.98			20200723
		24	Fr	~	03:40	~	08:50	iCloud.com Contacts Group USA "Empty Group"; But OK on iPhone; (R) iPhone same problem; Signed out of iCloud on iPhone and then back in, "your data stored in Safari and Contacts will be uploaded to iCloud - merge" and "Messages don't match"; iCloud Messages ON; iCloud Keychain ON; Photos > Download and Keep Originals (this was changed by signing out and back in to iCloud); iCloud > Backup > Back Up Now (04:18); iCloud > Contacts OFF (Keep on My iPhone), (R), (iCloud.com Contacts as before), iCloud > Contacts ON (Existing Local Contacts > Merge); Yet not showing USA Contacts on iCloud.com; (R) T450s, same problem; iCloud.com Contacts > Preferences > DO NOT Automatically format phone numbers; Changes made in iCloud.com Contacts do not always replicate to phone "as is" (removing spaces from Ukraine phone numbers OK in iCloud.com but not on iPhone, adding +1 to US numbers does work); iCloud.com Contacts used to recreate USA Group (when I started this process it cleared the USA Group on the iPhone); Added +1 to all US numbers; Removed incorrect formatting (not all of which replicates to iPhone); iCloud.com Contacts formatting USA "+1 (AreaCode) xxx-xxxx", Ukraine "+380 (CarrierCode2digits) xxx xxxx" (unfortunately spaces will be added by iPhone Contacts, but unless contact is edited there they will be retained in iCloud.com Contacts); iCloud.com Contacts s/b used to edit Contacts list, as it is the easiest and formatting changes work there (although not all replicated to iPhone Contacts); NOTE If a Group disappears on iCloud.com try editing a contact in that Group on the iPhone which might recreate all of them on iCloud.com; Added Group International for contacts that s/b in both USA and Not USA; NOTE Total of All Contacts should equal totals of International, Not USA and USA on both on iCloud.com and iPhone; NOTE Groups cannot be managed on iPhone (adding, changing, modifying) it must be done on iCloud.com Contacts (and so adding a new contact on the iPhone will NOT assign it to a group); NOTE It is possible to add a contact to more than one group, but in my current management system I would like to avoid this; iCloud.com All Contacts 181, International 1, Not USA 65, USA 113 (total subgroups 179, missing two); In search for missing two I realized that the Group feature is not well enough integrated into the iPhone such that management will be a nightmare (adding a new contact on iPhone does NOT assign it to a group); Used iCloud.com to delete all Groups (perhaps I'll find another use for Group features such as to send text messages to more than one recipient, i.e. "TurboNet"); Ended up with 180 contacts all with fully qualified international phone numbers; I could not find an app or a way to automatically add +CountryCode to all new contacts, it must be done manually; iPhone Screenshots	IMG	5.17	192.15			20200724
		25	Sa	~	03:30	~	05:30			2.00	194.15			20200725
				~	06:30	~	07:15		IMG	0.75	194.90			20200725
				~	05:30	~	06:30	Viber crashes upon opening a Chat: Open Viber > Choose a Chat > Viber shows the Chat thread for about 1 second then disappears; Research shows many other users are experiencing the problem, but most reports from 7/10/20 (15 days ago); Forced close of Viber and (R) iPhone (problem remains); Viber app is up to date as per App Store > Today > Profile > Viber Messenger (no update available, last updated 7/20/20); Reinstalled Viber via General > iPhone Storage > Viber > Offload App ... (long wait, 10-15 mins) ... (R) ... Reinstall app ... (long wait) ... exited and reentered Settings (app has been reinstalled), but Viber still crashes; I'm going to wait this one out, as Viber will probably fix the problem on their end within a few days, weeks or months, and I don't use Viber on the phone very much; 7/10/20 "In a tweet, Viber said that such technical issue is being experienced worldwide" and "The instant messaging software application advised its users to wait while they fix the glitch"; Further research reveals that the problem may well be the Facebook SDK that many app developers are relying on (1/2 dozen apps all started crashing at the same time); It's been more than two weeks since the problem was 1st reported and there is no solution yet; Either Viber can't easily remove the SDK features, or Facebook can't fix the SDK version that broke the previously written apps; Affects only iPhone		1.00	195.90			20200725
		26	Su	~	05:30	~	05:40	CC invoice shows 467.5 MB and iPhone recorded it as 494 MB (period ending 7/21/20); At least for now the iPhone totals are ~95% of the CC totals		0.17	196.07			20200726
		29	We	~	12:50	~	13:00	ScreenShot Captor (SSC): 02:14 Jesse on DonationCoder.com Forum topic "Request JPG Caption Metadata CR_LF not just LF”, "Try 4.39.0 BETA"; Imaged T400s to test; Installed and tested; Replies to Forum / $25 donation; $23.97 donated to Jesse (mouser); Considered new topic concerning embedded color space/profile, fascinating research on Jeffrey Friedl's site, but in the end decided it was not time for me to bring this up with SSC, the forum or mouser; Jeffrey Friedl's Image Metadata Viewer reveals that currently produced iPhone images (IMG_0189.JPG example) use an unrecognized embedded ICC color space profile 'Display P3', so if I want to post those images to the web I would need to convert to sRGB and imbed the sRGB profile	EML T400s LIB	0.17	196.23			20200729
		30	Th	~	06:00	~	11:00			5.00	201.23			20200730
2020	Aug	5	We	~	14:40	~	14:55	Installed App Store update for Viber released 8/1/20 (see Sa7/25 "Viber crashes upon opening a chat"); Viber no longer crashes when opening a chat; It took them almost a month to fix this problem on iPhone		0.25	201.48			20200805
		9	Su	~	13:20	~	14:05	Researched AppleCare+ (8 days remaining): With Theft and Loss it is $14.99/mo ($359.76) or $299 (both for 24 months); There's deductibles and limits on everything that might happen (Theft and Loss $269) / It's not worth it, decided to pass (I'll self-insure)		0.75	202.23			20200809
		13	Th	~	01:05	~	01:35	Installed Murphy Drive Rewards		0.50	202.73			20200813
		16	Su	~	18:30	~	19:15	2nd RokForm order placed / (I received an email for a "one day only" 20% off code AUGUST2020, savings $48.99)	EML Ai11P	0.75	203.48			20200816
		17	Mo	~	08:35	~	08:50		USB/SPF	0.25	203.73			20200817
		23	Su	~	06:25	~	08:00	RokForm order was rec'd Fr8/21: Unpacked; Battery pack wireless phone charger set up at computer (issue, stops charging when iPhone is full); G-ROK Speaker tested/charging / Email to info@rokform.com inquiring about how to use the SD card; Installed Viber update released 8/16/20	Ai11P EML	1.58	205.32			20200823
		24	Mo	~	03:00	~	06:30	Researched wireless charging stand for at main station; Ordered 'Belkin BOOST CHARGE Wireless Charging Stand - Special Edition' from Apple; Cleaned bench (iPhone 11/RokForm box) / Updated iOS 13.5.1 to 13.6.1 "includes bug fixes"; 13.6 "Adds a new setting to choose if updates automatically download to your device when on Wi-Fi" / General > Software Update > Customize Automatic Updates > Do NOT Install iOS Updates and Do NOT Download iOS Updates; Installed Viber update released 8/23/20		3.50	208.82			20200824
		26	We	~	08:10	~	08:25	Notifications > AMBER Alerts OFF; Updated iMovie to 2.2.10 released 8/25/20: General > iPhone Storage > iTunes U > Delete App		0.25	209.07			20200826
		27	Th	~	07:30	~	08:10	Apple Belkin Charging Stand rec'd We8/26: Unpacked, plugged it in, and it works; Simple, elegant, nice heavy base, perfect design for what I need at the main computer station! / Updated Google Maps; $63.98 added to summary total cost; Product registered on Belkin site	Ai11P	0.67	209.73			20200827
		31	Mo	~	06:30	~	06:40	Updated Viber to 13.7.0 released 8/30/20 "Control who can add you to groups-- everyone or saved contacts only. Go to More > Settings > Privacy"		0.17	209.90			20200831
2020	Sep	6	Su	~	14:20	~	15:05	ScreenShot Captor (SSC) JAK2/T450s: Updated to 4.39.0b (nothing new from Mouser in a long time, might as well run with BETA, which creates the jpg metadata correctly, especially for ViewNX 2) / Configured to Check for Updates		0.75	210.65			20200906
		20	Su	~	20:50	~	20:55	Updated Viber to 13.8 released 9/15/20		0.08	210.73			20200920
2020	Oct	31	Sa	~	17:35	~	17:40	Facebook and Messenger installed		0.08	210.82	Active	L	20201031
2020	Nov	26	Th	~	11:45	~	13:00	Fabricated tripod mount: 2x2x3.5" angle iron with 1/4-20 tapped thread; Works great with Rokform magnetic case		1.25	212.07			20201126
2020	Dec	22	Tu	~	08:00	~	08:30	Problems with CC not connecting me to Andrew Wommack Ministries Europe in England: Called CC for support; Ultimately what fixed it was to disable LTE (Settings > Cellular > Cellular Data Options > Disable LTE)	3/15/22	0.50	212.57			20201222
2021	Apr	1	Th	~	13:30	~	15:00	Hyperlapse from Instagram is totally free with a rating of 3.8/5; Skyflow by Andrey Kovalyov is $2.99 for the full version with a rating of 4.7/5; Decided to install Skyflow; Although it looks like it can shoot a portrait mode video, the interface is landscape only; 1st tests; Even though there appeared to be an option to rotate the video, it did not come out in Portrait (as viewed on T400s in Downloads)	IMG	1.50	214.07			20210401
		2	Fr	~	13:30	~	13:45	Not completely satisfied with how SkyFlow works I installed Hyperlapse from Instagram; But very, very simplistic, no obvious camera controls and "12x" is as slow as it goes / So it looks like I'm stuck with SkyFlow, for which I need to pay $2.99 for further testing		0.25	214.32			20210402
				~	14:20	~	15:00	Apple ID password change required; JKlute2020->JaK@2021; Paid $2.99 for SkyFlow Full Version; Testing with 1080p (tomato starts in window), 10 secs per frame, 240 frames total / (Video made yesterday Skyflow ~ 2021.04.01 14-40 540p 25fps.mov opens just fine with WMM)	IMG	0.67	214.98			20210402
		4	Sa	~	10:05	~	11:40	iCloud.com 5GB is almost full, available space 0.5 GB, clean up: Deleted SkyFlow Projects and FlacBox files that are not needed; Backup was 1.9GB, now 1.2GB / Tried to delete items from Docs=iCloudDrive (1.33 GB) but nothing found I don't want / Photos and Videos can always be deleted as soon as they have propogated to T450S where they propogate to CrashPlan (was 0.4 GB now 0.02 GB); I do not want to delete any Messages (0.8 GB) / Available space now 1.6 GB; Note I'm probably eventually going to have to pay Apple for more iCloud storage (1st plan is $0.99 for 50 GB)	SSC	1.58	216.57			20210404
		26	Mo	~	06:45	~	07:40	Increased iCloud storage 5 GB -> 50 GB; $0.99 per month; USB	SPF	0.92	217.48			20210426
2021	Aug	12	Th	~	14:30	~	15:30	Deleted Downloaded Video "Pilot" (~800MB) / Uninstalled GarageBand (1.57GB), Keynote (473.2 MB), Numbers (477 MB), Pages (467.2MB) [these are all free apps and I've never used them, and they constantly want updates] / Updated Facebook, Messenger, Viber, Apple Store, Google Maps, Murphy Drive, Flacbox; Installed Ubiquiti WiFiman, 4.7/5 rating, v0.14.1, 7/22/21, maybe of some use		1.00	218.48			20210812
2022	Mar	3	Th	~	08:15	~	08:45	Received email We3/2/22 from Consumer Cellular: "NETWORK UPDATE WILL AFFECT YOUR PHONE SERVICE"; Advised to change Settings > Cellular > Cellular Data Options > Enable LTE for Voice & Data / But the option there on my iPhone only says "Enable LTE" (see iPhone screenshot); Setting not changed	IMG Ai11P	0.50	218.98			20220303
				~	08:45	~	08:55	Currently using iOS 13.6.1; iOS 15.3.1 available; (7) App Store updates to do		0.17	219.15			20220303
				~	08:55	~	09:40	iOS 15.3.1 "About this Update": Affected changes/additions include FaceTime, Messages and Memoji, Focus, Notifications, Maps, Safari, Wallet, Live Text, Spotlight, Photos, Health, Weather, Siri, Privacy, iCloud+, Accessibility and "other features and improvements"; New features available with iOS 15; Notables for me: There appears to be a Messages search; Photos sent via Messages automatically appear in Photos app; "Easily save photos" in Messages conversation (new save button); Focus to control and filter notifications, including while driving; Notifications improved (summary for the day, mute, etc.); Maps, many improvements; Safari has a new Bottom Tab Bar to swipe left or right to move between tabs, Tab Groups, Customizable Start Page, Voice Search; Spotlight has Photos Search by locations, things in the photo or Messages contact name (pull down from the Lock Screen or Notification Center to open Spotlight); Siri "On-device speech processing" adds "Offline support" (requires A12 Bionic and later and download of speech models, my iPhone is A13 Bionic), also "Maintaining context" between Siri requests; Camera "Zoom in QuickTake video" swipe up or down while taking video to zoom in or out; Keyboard "Magnification loupe for text cursor and selection"; "Drag and drop" across apps; Reminders improvements; Translate "System-wide translation" (select and tap Translate); Live Text in photos (OCR) with context sensitive menus (for example, Camera photo of phone number, tap "call"; Per-App Text Size (Control Center); Photos can manually set the time, date and location of a photo and obtain more information; iOS 15 was first released to the public in September 2021		0.75	219.90			20220303
				~	09:40	~	09:50	Updated iOS 13.6.1 → 15.3.1; Terms and Conditions sent by Email; ... "About 3 hours remaining" (CradlePoint shows 2-4 Mbps download) ...	EML	0.17	220.07			20220303
				~	09:50	~	10:30	... Thought about the implications of this major change; Studied WikiPedia "iOS 15"; Download continues at 2~4 Mbps ...		0.67	220.73			20220303
				~	11:45	~	12:15	... Downloading has stopped ...; Status "About 1 hour remaining" ...		0.05	220.78			20220303
				~	12:20	~	12:45	... Downloading started again ...; Status "About 41 minutes remaining" ...		0.05	220.83			20220303
				~	13:22	~	13:25	... "Downloading..." and "About 5 minutes remaining" ...; Downloading has stopped, now "Preparing Update..." ...		0.10	220.93			20220303
				~	13:50			... it's installing the update (blank screen with apple and progress bar)		0.05	220.98			20220303
				~	14:00	~	14:15	... I heard it beep, and briefly saw "Primary: Your SIM sent a text message" (or some such); "Software Update Complete, Your iPhone has been updated to iOS 15.3.1"; Apple Pay "Add cards" > Set Up Later in Wallet / iPhone Analytics "Help Apple" > Don't Share; Welcome to iPhone (home page); Carrier Settings Update, New settings are available > Update / Settings > Finish Setting Up Your iPhone > More for Your iPhone > Set Up Apple Pay ... Set Up Later in Wallet / App Store (9) > What's New on the App Store > Continue > Personalized Ads > Turn Off Personalized Ads > Location Services (sharing location with App Store) > when I finally arrived in App Store the (9) updates were no longer being notified or shown	3/15/22	0.25	221.23			20220303
		4	Fr	~	04:05	~	07:30	General review of settings and testing of new features in iOS 15.3.1: Settings > Cellular > Cellular Data Options > Enable LTE for Voice & Data does not exist (see iPhone screenshot) / Checked operation of Personal Hotspot, Allow Others to Join OFF->ON (OK) / Personal Hotspot is persistant now, seems to stay on even if I'm not in Settings > Personal Hotspot (do not generally leave it on so that if TurboNet goes down we'll have CradlePoint automatic switchover to iPhone cellular, as this will increase mobile data usage) / App Store > (8) Updates (Google Maps, Messenger, Apple Store, Ubiquiti WiFiman, Murphy Drive Rewards, Flacbox FLAC Player Equalizer, Clips, iMove) > Update All / Siri is much faster now (on device speech processing and offline support); New Translate app looks to be very useful (moved to home screen); System-wide translation is working (tested with Viber, Siri is amazing) / Settings > Messages > Filter Unknown Senders; Now have Messages Filters "All Messages", "Known Senders" and "Unknown Senders", and this is a WOW! feature / Settings > Accessibility > Voice Control > Customize Commands > Dictation > <phrase> OFF (I had turned this on at some time in the past so that I could always speak text to write, but it isn't needed in Messages as there is a Microphone button there, and it has a nasty tendency to write everything it hears when I'm looking at the phone)	IMG	3.42	224.65			20220304
		7	Mo	~	11:20	~	11:40	Reviewed Settings > Phone: Dial Assist OFF; Decided to leave it OFF as I saw this in search "However, if you save international numbers with prefixes in their [your] contacts, the Dial Assist Feature can accidentally cause problems."; I considered this once before, see Th7/23/20)	7/23/20	0.33	224.98			20220307
		15	Tu	~	10:40	~	11:45	Can no longer dial Ukraine phone numbers; This might have started Th3/3/22 when I updated the iOS and the SIM card received an update; Dialed 611 (4) customer service, agent, 0733 ... on hold for ~20m then silence ... (Robert had problems with his headset) ... on hold while he contacted technical support (now 30m) ... Antionette in Tech Support advised me that AT&T is having unresolved problems with international dialing (many others have reported it), AT&T is working on the problem, for now can dial 1-201-490-2159 then at the prompt enter 380 50 729 0906 (example for Gem); 45m support call; I called Gem, it works / Antionette called back and I reported to her that this method works, and I'll be waiting to see if AT&T fixes the problem	3/3/22 12/22/20 7/23/20	1.08	226.07			20220315
2022	Apr	6	We					Incoming calls not ringing: Gem tried to call me 6 times in a row and was sent to VM every time; Others in the USA called me but no notification or ring / I only found out by talking with these people by call, Viber or SMS that they had tried to reach me, but nothing in Recent call list / 611 (4) 0733 ... Anica advised to Reset Network settings; Settings > General > Transfer or Reset iPhone > Reset Network / MBR95 password (and probably all WiFi passwords) were dumped (restored manually from T450s networking records); Personal Hotspot is no longer setup / FIXED: Incoming calls are ringing but I have setup work to redo		1.00	227.07			20220406
		8	Fr	~	07:25	~	07:50	Settings > Personal Hotspot > Allow Others to Join (Wi-Fi Password 34157934); Tested by unplugging TurboNet's PoE connection; Flawless (NetWorx CM never saw the outage, CP showed it all working as it should) / WiFi password re-entered: MBR95-Public Speak Russian		0.42	227.48			20220408
		10	Su	~	05:15	~	05:30	Settings > Siri & Search: Siri Responses, SPOKEN RESPONSES > When Silent Mode is Off --> Always; Always Show Siri Captions; Always Show Speech		0.25	227.73			20220410
				~	07:05	~	07:15	Settings > Siri & Search: Listen for "Hey Siri" > ON --> OFF (wait 10s) --> ON and rerecorded (function is improved, both with speakerphone and headset)		0.17	227.90			20220410
	May	18	We					Problems receiving direct phone calls from Gem continue: Today rebooting the iPhone helped, but it is still intermittent		0.20	228.10			20220518
2023	May	31	We					Installed Ace Rewards (Apple ID for Jeff@DataVisionServices.com is still JaK@2021); I did this primarily to obtain $5 bonus for downloading the app and linking my Ace Rewards membership		0.10	228.20			20230531

## Z14
Miscellaneous: Z14	A					MV_3: Murata DMS-20PC-8-DCM-C

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L5
2020	Dec	29					Ordered from Mouser	EML MOU	On Order		20201229
2021	Jan	1					Received	MOU L5	Available	L0	20210101
		19	Tu					Attached to battery bank for TurboNet/RHS (Richmond High School) while bench testing, using clip leads; Reads ~0.15v lower than Fluke (76.15v Fluke, 76.0v Murata)	L5	Applied		20210119
		27	We					Difference between the Murata and Fluke is now about -0.25v	L5			20210127
2021	Feb	24	We	~	12:15	~	17:00	Travel and onsite at RHS: Boost charger mounted to RHS fabricated battery box, which looks great; Photos	IMG TA2	Sold	L5	20210224

## Z15
Miscellaneous: Z15	A					IRT_1: Fluke 62 MAX+

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Aug	31					20210831.0 TODO Infrared Thermometer Replacement Notes.doc; 20210831.1 Fluke 62 MAX+ Infrared Thermometer User Manual - 62max-62maxplus_manual.pdf / Ordered from Test Equipment Depot 20210831.2 Web Order Test Equipment Depot Scan.jpg (also ordered TEC25 Branded EVA Case for Two Meters - will use for IRT_1 and Micronta) / 20210831.3 Test Equipment Depot Order Confirmation Email SSC.jpg	LIB EML SPF WMBS SSC	On Order		20210831
	Sep	1					20210901.0 Emissivity Table, ThermoWorks.pdf	LIB			20210901
		2					Invoice Received 20210902 Invoice Test Equipment Depot Scan.jpg	LIB EML SPF WMBS			20210902
		8					Received; 20210908 Fluke 62 MAX+ Initial Test & Review.docx	LIB WMBS	Available	L	20210908
		13					Review submitted to ResellerRatings.com	EML			20210913
	Oct	24	Su					Video sent to Pavel via Viber	IMG			20211024
	Nov	13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup				20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)				20211114
2022	Sep	17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917

## Z16
Miscellaneous: Z16	A					EX_1: Extech 380947

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Sep	25					Ordered from Test Equipment Depot / 20210925.0 Extech Mini DC-AC Clamp Meters Datasheet - 380941_380942_380947_DS-en.pdf / 20210925.1 Extech User Guide 380947 Revision A - 380947A_UM-en.pdf / 20210925.2 Extech 380947, Test Equipment Depot, Order Confirmation Scan.jpg	LIB EML SPF	On Order		20210925
	Oct	1					Invoice Received 20211001 Extech 380947, Test Equipment Depot, Invoice Scan.jpg				20211001
		4					Received		Available	L	20211004
		5					Stickers added; This sheet created	LIB WMBS			20211005
		24	Su					Video sent to Pavel via Viber	IMG			20211024
	Nov	13	Sa					Overview and detail photos of TurboNet MikroTik 48v project test setup: Schauer #1, Traco #1, T-105s, Wattmon, APC load setup				20211113
		14	Su	~	00:13	~	00:22	Two moving videos of TurboNet MikroTik 48v project test setup; While in recovery from deep discharge; Overhead lights off (dark)				20211114
2022	Apr	17	Su					Stickers added for polarity on the jaws (something I’ve been confused about many times now, I should have done this when I first purchased it); Positive current flow is into the loop from the “top” or display side / I also noticed that the BK and the Extech agree to within 5mA at 1 amp (Extech’s least significant digit agrees with BK which has more resolution); Extraordinary agreement and stability / Extech 380947 + IN +.lbx; Extech 380947 Positive current flow is into the loop from the top or display side.lbx	LBX			20220417
	Sep	17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917
	Oct	5	We					W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 IMG WP11			20221005

## Z17
Miscellaneous: Z17	A					IT_1: ITECH IT8512A+

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Available	L
2021	Aug	22					As part of the TurboNet MikroTik 48v Systems Project I began to look for a suitable Electronic Load / Began by studying the Rigol DL3021 ($518 delivered) 200W/150V/40A	DBT LIB T48P	Research		20210822
	Sep	5					Further shopping research: Siglent SDL1020X-E (entry level ~$500) 200W/150V/30A (nice detailed display with waveform logging and color if spend higher $); East Tester ET5410 ($269.78) 400W (too cheap) / Multicomp PRO MP710259 US ($399) 300W/120V/30A (too cheap); Quick look at Hanchen	DBT LIB			20210905
		22					Lexington meeting with Keith and Mark: Rec'd $2600 advance on MikroTik Pilot Project (out of which I'll buy an Electronic Load)	DBT T48P TPC1 TEDS TOI			20210922
		26					Research: Discovered ITECH 8500 series, in-depth study; Datasheet, YouTube Video, User Manual and eevblog.com discussion to Library; IT8512A+ 300W/150V/30A (perfect range for my work) / Looked for IT E122 USB Communication Module, $50.40 w/USB cable @ tequipment.net, $35 Amazon (wait to order until we become familiar with IT8512A+) / Studied other "knock-offs" of this basic design (Maynuo original designer, BK); ITECH is owned by BK Precision (but BK "knock-offs" are too pricy) / Exhaustive source research, places with stock in the USA high $, tried to order from AliExpress ($435) but eventual response "not available"	DBT LIB			20210926
		27					Further source research: Mouser and DigiKey do not list man'f ITECH; eBay is the only listings below $600 (but ships from China) / Called Circuit Specialists, Maria, 480-464-2485 (480-285-1415 direct), ordered online $600.51, estimated ship date 10/8/21	DBT LIB DRD	On Order		20210927
	Nov	30					Circuit Specialists changed the estimated ship date several times, and I called Maria several times, but finally received Invoice with Shipping Confirmation & Tracking	LIB DRD			20211130
	Dec	3	Fr					Received, initial tests AOK: Agrees very well with BK, Amps readouts agree 0.000 to +0.001 Amps (last digit) in the 0-5a range / The ITECH will be my laboratory current standard from now on (planning on using it to calibrate the Wattmon current loops, as on a suitable power supply/battery can go 0-30A w/o extra wire loops) / Inventory stickers; Notated invoice copied		Available	L0	20211203
		4	Sa					Fabricated Remote Sense cable: 6ft Belden 88760 (TurboNet tower Power Cable "sample" I saved, twisted pair shielded 18awg); Red and Black clip leads with ~20" spread, tinned leads for ITECH rear panel Sense	DRD			20211204
				Careful spot calibration comparisons, Fluke, BK and ITECH (6-19v, 0-5a); The ITECH is now my main laboratory standard for accuracy and precision, because the comparisons are all very good / For voltage the Fluke reads only very slightly higher than the BK and the ITECH, and the ITECH has more resolution, especially below 10v; For current the BK generally reads slightly lower, but only 1-3 mA / I noticed some drift in the ITECH which is probably from internal temperature rises at the higher wattages, and also may be from different input voltages (CC mode); For details and the data see FTR	DRD IMG			20211204
				Experiments with B0 (BK being used to boost charge/current available): / Set 30.000a, power limited to readback of 299.97w (~25a); Set 300.0w, readback is 299.92-299.98w; Set 11.70v, saw 25.7a max and shift to regulation once it was no longer power limited	DRD B0			20211204
				Attempted B0 Battery Test @ 3w (but manual is wrong, can't do CW Battery Test)	DRD			20211204
				16:30	Setup Battery Test: RANGE=30.000A, CURRENT=11.250A, STOP VOLT=10.000V, STOP CAP=999.999AH, STOP TIMER=99999S, SAVE BATT FILE 1; Also monitoring and logging with W10 ...; Started discharge	DRD B70-71			20211204
		5	Su	~	09:09			Battery Test concluded; ITECH performed flawlessly; Very good agreement with Wattmon			L	20211205
		20	Mo					Setup Battery Test: RANGE=3.333A, CURRENT=3.333A, STOP VOLT=9.600V, STOP CAP=999.999AH, STOP TIMER=28800S, SAVE BATT FILE 2; Also monitoring and logging with W10 ...; Started discharge	TM21F WP1			20211220
		21	Tu					Battery Test concluded; ITECH performed flawlessly	TM21F WP1 IMG			20211221
		22	We	~	08:04	~	11:58	ITECH was extremely useful in determining the high power limits of the W50 (PS1 fuse blown)	TM21F WP1 SSC IMG			20211222
2022	Jan	5					SureCall Cellphone Booster Power Supply Adapter Replaced; ITECH very useful and quick to test replacement at full load	IMG WMBS			20220105
	Feb	20	Su					Failed attempt at spare Schauer preparation	TM22 TM48S L14			20220220
	Apr	14	Th					Tracos Stock Fabrication: ITECH used to verify outputs of TP_2 and TP_3	T48S V10 V11 IMG			20220414
	May	24	Tu					Started "BC7 Schauer Preparation" (T-105s)	T48S BC7	Applied		20220524
	Jun	11	Sa					Started "BC8 Schauer BTS Tests" (no battery): BK in parallel to ITECH input (Schauer output), set 12v/5.1a; 2wI, Schauer ON; Could not get Schauer to remain stable with only 2w load; Tried CC but no better / Starts reliably to stable voltage at 17.00wI (but can't get anywhere near 100-200mA Float charge range); Added capacitance, (6) 47uF @ 35v (assembly that was used on APC load) / This is much better, 0.500aI is stable through startup (to 13.450vI, 6.69wI), close enough to minimum charge current when battery is fully charged that it won't matter for the purposes of this test, / which is to determine BTS T-Comp at -15 to 50⁰C	T48S BC8			20220611
		16	Th					Proof of Principle tests of Traco and ~54v power supply on output; 20220616 1714 IMG_2597 PSE.jpg	T48-3 IMG L17			20220616
		20	Su					Experiments with ITECH Von and S13; ITECH now set Von > Living > 10v; S13 burn-in at 165w load ...; Load OFF	T48-3 L17			20220620
	Sep	17	Sa					Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917
	Oct	5	We					W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 IMG WP11			20221005
		6	Th					Bench Testing (~25⁰C): Bench Testing Finished / ITECH disconnected and OFF	T48-3 PLN WP11	Available		20221006
2023	Jan	13	Fr					R&D TODO: Voltage Reference Calibrations; W150 Full Environmental Testing (WP13)	DWP WP13			20230113
	Feb	5	Su					PentaRef:ITECH Spot Calibration Checks: Comparisons from 0.2 to 10v; Worst error is 3.5mV low at 10.0000vP (0.035% low); CONCLUSION The ITECH can be trusted to have an accuracy better than ±0.05% in the range 0.2 to 10v	DRD			20230205
		6	Mo					Completed ITECH/Fluke/BK/Micronta Cross Calibration Checks: 20230205 ITECH-Fluke-BK-Micronta Cross Calibration Checks.ods sheet 20230206 Analysis / Labels applied to Fluke, BK and Micronta; Micronta graph printed for field meter case	DRD DBD LBX SSC S2			20230206

## Z18
Miscellaneous: Z18	A					D2D_1: Dinico DIN-S-CF

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L14
2021	Oct	8	Fr					Mark and Keith confirmed again that they want a new enclosure for ONWT and I desired to incorporate active fan cooling to keep the batteries as cool as possible; Researched differential fan controls; I found they are available in $50-$100 range (Amazon, ThermoMart.com, Dinico); These types of controllers are most often used for solar hot water heating systems, to turn the pump on when the panel temperature is higher than the internal tank temperature, but they could be adapted to our application; The relay outputs are NO only, so the lower end cutoff (~50 degF) would have to be obtained by a reversing relay (or separate thermostat) to OPEN when temperature is low; Abandoned idea (at the time I thought the cost of installation would be too high for the benefits received and I tabled it); Later on this day I discovered the Meir BW-136FC enclosures with fan cooling (NEMA 3R, see printout)	TEDS L14	Research		20211008
		12	Tu					After several days considering suitable NEMA 3R enclosures I came back to the differential fan control idea and the Meir BW-136FC enclosures; It's not just battery life that's improved, it's also reduced maintenance, as the batteries use a lot more water when they are hot, even if they aren't in Absorption; A differential T fan controller system would save on maintenance costs, AND increase the useful life of the batteries; I took a closer look at the Dinico DIN-S-CF from ThermoMart.com in Ontario, Canada; 20211012 ThermoMart.com DIN-S-CF Manual (last version).pdf; I made plans to incorporate the Dinico for active fan cooling at ONWT (low temperature "floor" by a reversing relay or a separate snap disk or reed thermostat); It all "clicked" at this time; I recommended to Mark that we buy the Meir enclosure for ONWT (after he had already ordered a Wiegmann); Mark ordered the Meir	TEDS LIB SMS EML	Design		20211012
		15	Fr					Mark also authorized buying what it takes to retrofit the Wiegmann enclosure that he had on order; Found Integra fan kits, shrouds, filters so that the Dinico can be used in the Weigmann as well as the preferred Meir enclosure / Ordered Integra fan kit (Southern Electronics); Decided to try using a snap thermostat for the fan control system "floor" instead of a reversing relay, as it seemed easier at the time	TEDS EML			20211015
		17	Su					Ordered Dinico from ThermoMart.com; Planned mounting for DIN-S-CF controller; Ordered snap disk thermostat and Integra fan shroud from DigiKey / 20211017.0 ThermoMart.com DIN-S-CF SSC.jpg; 20211017.1 Dinico Global Inc. (ThermoMart) - Order Invoice EML SSC.jpg; 20211017.2 ThermoMart Order Invoice EML SSC Annotated Scan.jpg	TEDS TMD DKE EML LIB	On Order		20211017
		21	Th					Quick test of DigiKey Cantherm snap-disk (received We10/20); Reconsidered reversing relay for fan control "floor" as snap-disk ON and OFF temperatures are extremely sloppy; Ordered reversing relay from DigiKey	TEDS DKE EML			20211021
		22	Fr					Received Dinico (approximate date); Fan control shown on 20211022 Mier BW-136FC Enclosure 24x36x12, Drawing Scan.jpg / 20211022 DigiKey Invoice Reversing Relay Scan.jpg	TMD TEDS DKE DBT LIB	Available	L	20211022
		27	We					Initial tests AOK; Setup for use in regulating the temperature of the Schauer BTS in the QED (Quick Easy Defroster) in the Engel on the floor; Dinico and Engel in 20211027 1310 IMG_2134.MOV / Reversing relay received from DigiKey	TOI T48P IMG DKE	Applied	L0	20211027
		30	Sa					Began series of Schauer BTS tests with Dinico control of the QED in the Engel on the floor	T48P			20211030
		31	Su					BTS tests concluded (data was obtained for 25, 20 and 10⁰C); Priorities rearranged (we will need temperature stabilization with Engel and Dinico, but testing should wait until ITECH Electronic Load is received)				20211031
	Nov	2	Tu					Began adjustments of Schauer #1 for ONWT, with BTS sensor in QED in Engel on the floor and Dinico control; 20211102 0828 IMG_2146.MOV	T48P IMG			20211102
		5	Fr					A suitable metal plate was found that can be fabricated into a mounting bracket for the Dinico at ONWT; Mark here for "show and tell" (discussed Mier enclosure plans and I showed him the Dinico on the bench)	TOI SMS			20211105
		9	Tu					Dinico #1 and Engel in 20211109 1209 IMG_2148.MOV	IMG			20211109
		12	Fr					Mier enclosure delivered to the shop by Dakota and Brandon (will be used at ONWT instead of the Wiegmann)	TOI SMS			20211112
		13	Sa					General Bench Testing Photos; Schauer #1, Traco #1, Dinico #1; 20211113 1318 IMG_2167.JPG (Dinico #1)	T48P IMG Z0			20211113
		14	Su					20211114 0013 IMG_2174.MOV; 20211114 0021 IMG_2175.MOV	T48P IMG			20211114
		19	Fr					Proposal sent to Keith, Mark and Brad for "Odessa North Remote Monitoring" / Proposal included monitoring of battery/outside air temperatures and enclosure fan operation (to determine the effectiveness of the active fan cooling system) / 20211119 Email to Keith, Mark & Brad 'Odessa North Remote Monitoring'.pdf / [DORM project abandoned Su10/23/22]	TOI DORM EML DBT			20211119
		20	Sa					Fabricated mounting bracket and assembled with relay	TOI	Assembly		20211120
		21	Su					Marked, drilled and tapped all mounting holes in the Meir back plate (test fit all) including Dinico fan control assembly				20211121
		22	Mo					Fan Control System Schematic Working Draft and Unit Assembly; Dinico programmed (Set Point 0.0⁰C, Ld 1.0⁰C, Hd 1.1⁰C) / Labels: Dinico Sensor T1 Outside - Wire Label 0.5 in.lbx; Dinico Sensor T2 Battery - Wire Label 0.5 in.lbx; Dinico AC Power Plug Cooling Fan - Wire Label 0.5 in.lbx; Dinico DIN-S-CF Settings.lbx; Dinico Caution! 120 VAC.lbx; Spare Fuse.lbx / Mark/Keith Scheduling arrangements for Tu11/23 ONWT installation; Assembly closeup photos TurboNet Dinico #1 (ONWT)	TOI IMG LBX SMS IMG			20211122
		23	Tu					Fan Control System Installed in Mier, wired to door switch and fan, tested (garage floor, working copy of Fr10/22 Mier BW-136FC layout plan) / 20211022,1123 Mier BW-136FC Enclosure 24x36x12, Assembly Working Copy (ONWT), Drawing Scan.jpg; Mark and Keith picked up the partially assembled Mier to deliver to ONWT	TOI SMS DBT	Ready	Mark/Keith	20211123
				~	12:20	~	15:40	Onsite installation at ONWT: Fan control system tested but I forgot to put the outside T-sensor under the box (I left it dangling below the fan control system)	TOI	Installed	L14	20211123
		29	Mo					20211129 Fan Cooling System, Enclosures Design Specifications, Schematic Scan.jpg; As assembled for ONWT showing Dinico, Reversing Relay, Door Switch and Fan; Copied to eventually place in Mier brochure slot	TEDS DBT TOI			20211129
		30	Tu					20211130.1 Invoice - Enclosures Design Specifications & Procurement.pdf / 20211130.2 Email to Mark, Keith & Brad 'Invoice - Enclosures Design Specifications & Procurement'.pdf	TEDS DBT EML	Sold		20211130
	Dec	3	Fr					Schematic drafts, physical connections planned: White sheet "ONWT Remote Monitoring"; Notated copy of 11/29/21 "Fan Cooling System" Schematic; Plans to use Wattmon to monitor fan control system (AC voltages from Dinico)	DORM WS			20211203
		4	Sa					ONWT Remote Monitoring plans modified to control fan system power with Wattmon RL5 (instead of controlling Schauer power) [DORM project abandoned Su10/23/22]	DORM			20211204
		5	Su					TODO for ONWT installation (capacity vs. temperature concerns): Reprogram Dinico for 10⁰C "floor"; This realization came after I analyzed the data from a T-105 dicharge capacity test and studied Trojan's specifications	DRD			20211205
		31	Fr					20211231.1 Invoice - Odessa North Installation (ONWT).pdf	TOI DBT			20211231
2022	Jan	1	Sa					20220101 Email to Mark, Keith and Brad 'Invoice - Odessa North Installation' (ONWT).pdf				20220101
		4	Tu					20220104.2 TurboNet Statement.pdf; 20220104.3 Email to Mark & Keith 'TurboNet Statement'.pdf; Politics, Mark: "What's the $1,195 Cabinet charge? I purchased the cabinets.."	EML TEDS DNT			20220104
		5	We					Politics, Mark: Emails to Mark and Keith / "Yes, you did purchase the Wiegmann and Mier enclosures. But I performed the research, design, planning and engineering work. I gave you the specifications, drawings and schematics. I also made numerous initial phone calls to suppliers. Also on this invoice are the amounts I spent to buy the fan control components for the Mier at ON and the Integra fan/filter/shrouds for the Wiegmann. As for the hours spent I gave you a 50% discount from my normal rates." / Sticker shock 20220105 Email from Mark 'TurboNet Statement'.pdf (maybe will respond later)	EML TEDS DNT DBT			20220105
	Feb	19	Sa					Mimosas stopped working; Keith onsite; Strange reports from Keith that "power was off" and that he had to cycle power to the fan control system	TM22 SMS		L14	20220219
		21	Mo	~	09:45	~	11:10	Onsite at ONWT with Keith and Dakota: Strange reports from Sa2/19 continue in careful questions/answers with Keith (fan control system off until power cycled, then ~3⁰C)	TM22		L14	20220221
				~	11:10	~	14:00	Onsite Alone (after Keith departed): Fan control system T-sensor placed under the box; Reprogrammed Dinico for 10⁰C "floor": Tested and adjusted Meir enclosure door switch (it was too "loose"); Many photos	TM22 IMG			20220221
	Mar	12	Sa					Dinico Inventory Sticker 0.375.lbx; One applied to ThermoMart invoice, but the unit's sticker should be applied the next time I go to ONWT; / Notated invoices for Dinicos/Relays (ThermoMart, DigiKey and Mouser) scanned and organized in Library\ThermoMart (Dinico)	T48S LBX LIB			20220312
		27	Su					Labels prepared for T-sensors and reversing relay (to be applied on the next visit to ONWT): Wire Label, Dinico Sensor.lbx; TurboNet Reversing Relay For Dinico.lbx; Dinico prep is finished	T48S LBX			20220327
	Sep	19	Mo					TODO for ONWT: W150 BTS and Z18 T2 in lug s/b on T-105 negative post under Plastic [Foam] Cap [We9/21 Decided to install these under a Cap on the +6v negative post of a T-105]	T48-3 PLN		L14	20220919

## Z19
Miscellaneous: Z19	A					D2D_2: Dinico DIN-S-CF

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L
2021	Nov	11	Th					[Z19-20] Keith here to finalize ONWT Power Cable Assembly Plans: / Verbal order for Schauer and Traco spares (and at the time I thought we should also order spare Dinicos and Reversing Relays)	TOI SMS T48S L14	Sales		20211111
		15	Mo					[Z19-20] 20211115 Quote - Spare Parts for ONWT and Future.pdf; (2) Schauers, (2) Tracos, (2) Dinicos and Reversing Relays, $1,720; Emailed to Mark, Keith and Brad; Mark "I can get you a check tomorrow for the 1720"	T48S DBT EML SMS L14			20211115
		16	Tu					[Z19-20] Mark and Keith at shop to pickup the Power Cable Assembly for ONWT / Received $1,720 TurboNet check for spares	TOI SMS T48s	Advanced		20211116
		17	We					[Z19-20] Orders (Schauers, Tracos, Relays, Dinicos) / 20211117.0 Dinico Global Inc. (ThermoMart) - Order Invoice EML SSC.jpg; 20211117.1 ThermoMart Order Invoice EML SSC Annotated Scan.jpg / DigiKey had no stock on Reversing Relays; 20211117.2 Mouser Invoice Reversing Relays Scan.jpg	T48S EML TMD MOU LIB DKE	On Order		20211117
		19	Fr					[Z19-20] Reversing Relays (and Tracos) received	T48S MOU DKE			20211119
		22	Mo					[Z19-20] Dinicos received	T48S TMD	Available	L	20211122
	Dec	5	Su					White sheet "Engel Battery Enclosure": Plans begin to utilize a Dinico controller; D2D_2 slated for this project	DRD WS			20211205
		7	Tu					Late night thoughts continue for the design of the Engel Enclosure with Dinico control: White sheets "Engel Battery Enclosure" and "Engel Battery Enclosure - Dinico Controllers & Relays" [some Dinico ideas abandoned Sa12/11]				20211207
		10	Fr					[Z19-20] (Schauer chargers and Schauer invoice received); All the spares have been received; TurboNet Invoice Date (although spares have not been prepared yet); [Invoice completed and emailed Su1/2/22]	T48S DBT	Prep		20211210
		11	Sa					Dinico control setup simplification ideas; KISS notes on Tu12/7 white sheet "Engel Battery Enclosure - Dinico Controllers & Relays"; Continued design hopes and plans	DRD WS			20211211
		12	Su					Dinico #2 and SPDT Reversing Relay set up on the left end of the bench for control of the Engel cooling and the heat pads [ongoing R&D]	DRD Z0	Applied	L0	20211212
		14	Tu					Engel Battery Enclosure Assembly ... Dinico #2	IMG DRD		L	20211214
		17	Fr					Dinico #2 in use for B26 and W50 testing (RCWT Emergency) [ongoing through Tu12/28/21]	TM21F WP1 Z0			20211217
		19	Su					Dinico Station Adjusting Notes (B26, WP1, BTS Tests); Kept for help developing a Wattmon algorithm to automate targeting desired battery temperature set points	PLN			20211219
		20	Mo					Physically swapped sensors to regulate on Battery instead of Air (Engel); Dinico Station Adjusting Notes (W50 Autopsy)	TM21F PLN Z0			20211220
		21	Tu					Dinico Station Adjusting Notes (W50 Autopsy, WP1/B26) [ongoing through Tu12/28/21]; W50 Testing (WISPer Prototype #1 from RCWT)	PLN IMG			20211221
		28	Tu					Dinico Station Adjusting Notes (W50 Autopsy, WP1/B26); Testing concluded, heat and Engel OFF, cover opened, fans OFF	PLN WP1 Z0			20211228
		29	We					Engel Battery Enclosure Assembly ... Dinico #2; Photos used for zoro.com review of heat pads	IMG DNT			20211229
2022	Jan	2	Su					[Z19-20] 20211210 Invoice - Spare Parts for ONWT and Future.pdf; 20220102 Email to Mark, Keith & Brad 'Invoice - Spare Parts for ON & Future (MikroTik 48v Systems)'.pdf / The invoice total was increased by $60 to $1780 mainly because of the extra procurement time caused by the Reversing Relays not being in stock at DigiKey We11/17/21	TM48S DBT EML L14			20220102
	Feb	17	Th					Engel and Dinico #2 used to run temperatures up/down for testing T-sensors on W10	DRD Z0			20220217
		20	Su					Further troubleshooting of T-sensors stopped by ONWT Emergency	DRD TM22 W10 Z0			20220220
				Set up and attempted configuration of spare Schauer (stabilizing BTS @ 25⁰C); Physically swapped sensors to regulate on Air instead of Battery (Engel); This move puts them back to factory; Dinico Station Adjusting Notes	TM22 TM48S L14 PLN			20220220
	Mar	12	Sa					[Z19-20] Printed and applied Dinico Inventory Sticker 0.375.lbx / Notated invoices for Dinicos/Relays (ThermoMart, DigiKey and Mouser) scanned and organized in Library\ThermoMart (Dinico)	T48S LBX LIB			20220312
		27	Su					[Z19-20] Labels applied to T-sensors and reversing relays: Wire Label, Dinico Sensor.lbx; TurboNet Reversing Relay For Dinico.lbx; Dinico prep is finished (Z19 still on the bench)	T48S LBX	Sold		20220327
	May	24	Tu					Powered up for Schauer BC7 Preparation; Engel, T1 Air, T2 bundled near Schauer BTS; Set 25.4⁰C, heat 10, Engel ON	T48S PLN BC7			20220524
	Jun	13	Mo					During BC8 Schauer BTS test run I discovered that the Reversing Relay had sticky contacts; Removed and labeled as "Defective: Intermittent Sticking of NO Contacts"; Replaced with Potter & Brumfield "Clacker"; Replacement on order	T48S PLN BC8 Z0			20220613
		16	Th					BC8 Schauer BTS Tests Completed; Heat OFF; Engel OFF; Cover open wide; Circulating fans OFF; Dinico OFF	T48S PLN BC8 IMG			20220616
		27	Mo					Ordered replacement Reversing Relay (see Mo6/13)	T48-3 DKE			20220627
		29	We					Received replacement Reversing Relay				20220629
	Jul	27	We					Labeled replacement Reversing Relay; TurboNet Reversing Relay For Dinico.lbx	T48S LBX DKE			20220727
	Aug	9	Tu					[Z19-20] Finished fabrication of two brackets for Dinico Fan Controller Assemblies; Ordered epoxy (Amazon) and fuse holders (DigiKey); Z19 Reversing relay attached to bracket; Z19 remains in service on bench on Engel	T48-3 EML DKE L17		L0	20220809
		17	We					[Z19-20] (2) Dinico Fan Controller Assemblies completed (photos); Reprinted and applied inventory label (zip ties are covering up the originals); Dinico Inventory Sticker 0.375.lbx / Dinico AC Power Plug Cooling Fan - Wire Label 0.5 in.lbx / [Z19] Removed from Engel control system; Epoxied to bracket made Tu8/9; Integrated back into Engel control system (bench)	T48-3 IMG LBX L17		L	20220817
	Sep	17	Sa					[Z19-20] Photos of bench setup: Dual Supply on Wiegmann backplate for LSWT; Before disassembly for W150_1 prototype fabrication	T48-3 IMG			20220917
		18	Su					T2 Sensor Epoxied into 5/16" Battery Connector with Two Layers of Shrink: It will still be useable for T-105s and for insertion into metal pipe for BTS tests / Installed on 27TMX negative post in Engel; Plastic Cap on Negative Post; Indirect Comparisons of Z19 T2 with Z20 T2 (known stable 24.9-25.0⁰C from earlier testing with Z20 T2) ...	T48-3 PLN IMG WP11			20220918
		19	Mo					[Z19-20] Indirect Comparison of Z19 T2 with Z20 T2, CONCLUSIONs: I think it is safe to state that Z20 T2 reads ~-0.5 degC lower than Z19 T2	T48-3 PLN WP11			20220919
		20	Tu					Bench Setup Changes/Improvements: Moved Z19 T2 and Plastic Cap to Battery +; Rotated Battery (+ near the front); Installed new design Foam Block (Battery +); CONCLUSIONs (T48-3 and Z0)	T48-3 PLN IMG WP11			20220920
		21	We					Bench Setup Changes/Improvements: Engel Heat/Cool Duty Cycle Changed (lower heat, longer cycle); Rotated 27TMX: Installed Z19 T2 and Foam Cap on Battery Negative Post (front left)	T48-3 PLN WP11			20220921
		25	Su					Engel Stable at +25.0⁰C: PSP found for We9/21 changes/improvements	T48-3 PLN Z0			20220925
	Oct	1	Sa					Engel (+25⁰C Target): Found Relay Contacts Fused Closed; Cleaned relay contacts; Oiled pivot points and springs; Changed relay wiring (both poles for heat); DO NOT LEAVE UNATTENDED AT HIGH HEAT; Seeking PSP for Heat OFF ...				20221001
		2	Su					Engel Stable at +25.0⁰C: Found PSPs for Heat OFF and Heat 5 (W150_1 testing)				20221002
		3	Mo					Bench Testing (-15⁰C): Stabilizing, looking for PSP; Circulating fans inop: Opened cover, fiddled, fixed				20221003
		4	Tu					Bench Testing (stable at -15⁰C): PSP and duty cycle; More problems with relay contacts stuck in heat				20221004
		5	We					Bench Testing (stable at +50⁰C): Woke to relay stuck in heat (wiggled and then OK); PSP; [Z19-20] W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 PLN IMG Z0			20221005
		28	Fr					[Z19-20] 20221011 Report, Photos & Invoice - Wiegmann and Power Cable Assemblies for LSWT.pdf: Emailed to Keith and Mark; Z19 photo in Report (next to Z20 on We8/17)	T48-3 DBT EML L17			20221028
	Dec	13	Tu					Rigged ~40w bulb on Heat before Variac; Hopefully, theoretically, this should reduce the inductive kick that is probably causing the relay contacts to stick	T48-4 PLN Z0			20221213

## Z20
Miscellaneous: Z20	A					D2D_3: Dinico DIN-S-CF

Date/Time CST/CDT					Description	Other Sources	Status	Location
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				Sold	L17
2021	Nov	11	Th					Z19-20	TOI SMS T48S L14	Sales		20211111
		15	Mo					T48S DBT EML SMS L14			20211115
		16	Tu					TOI SMS T48s	Advanced		20211116
		17	We					T48S EML TMD MOU LIB DKE	On Order		20211117
		19	Fr					T48S MOU DKE			20211119
		22	Mo					T48S TMD	Available	L	20211122

	Dec	10	Fr					Z19-20	T48S DBT	Prep		20211210

2022	Jan	2	Su					Z19-20	TM48S DBT EML L14			20220102
	Mar	12	Sa					Z19-20	T48S LBX LIB			20220312
		27	Su					T48S LBX	Sold		20220327
	Aug	9	Tu					Z19-20; Z20 and reversing relay mounted on bracket	T48-3 EML DKE L17		L0	20220809
		17	We					Z19-20; Z20 Tested and Programmed; Epoxied T2 sensor into 5/16" ring connector (for attachment to 27TMX negative post) [Note added Su8/21: I should have covered it with shrink!] / Dinico DIN-S-CF Settings.lbx; Dinico Caution! 120 VAC.lbx	T48-3 IMG LBX L17		L	20220817
		20	Sa					Dual Supply Bench Testing Setup Assembled: Z20 Dinico mounted on Wiegmann Back Plate, T2 sensor on battery negative post will be used to indicate battery temperature	T48-3 PLN L17 IMG			20220820
		21	Su					Test setup dissasembled briefly, added shrink to Z20 T2 (2 layers) and BC9 BTS (+1 layer)	T48-3 PLN L17			20220821
	Sep	17	Sa					Z19-20	T48-3 IMG			20220917
		18	Su					Disassembled Bench Test Setup and Wiegmann Backplate: Moved Wiegmann Backplate to garage (with Z20 Assembly still attached, it will be used at LSWT but not needed for further W150_1 setup and testing) [see Su10/2] / Indirect Comparisons of Z19 T2 with Z20 T2 ...	T48-3 PLN IMG WP11			20220918
		19	Mo					Indirect Comparison of Z19 T2 with Z20 T2, CONCLUSIONs: I think it is safe to state that Z20 T2 reads ~-0.5 degC lower than Z19 T2	T48-3 PLN WP11			20220919
	Oct	2	Su					W150_1 Bench Testing Started (+25⁰C): Z20 Assembly moved from Wiegmann backplate to bench test setup to use to monitor W150 backplate temperatures / T1 between supplies above contactor (silver tape); T2 on 1/4"-20 foot bolt near label area (5/16" lug)	T48-3 PLN WP11			20221002
		5	We					W150_1 Bench Test Setup photos and video (A Hard Day's Night)	T48-3 PLN IMG WP11			20221005
		6	Th					Bench Testing (~25⁰C): Bench Testing Finished; Disconnected and OFF (T1 and T2 removed from W150 backplate)	T48-3 PLN WP11			20221006
		10	Mo					Wiegmann Prep for LSWT: Photos; Installed Z20 Dinico and intake fan assembly, tested; Applied labels Dinico DIN-S-CF Settings.lbx and Dinico Caution! 120 VAC.lbx; B58 battery spacers, right side of battery centered on the fan	T48-3 IMG LBX L17			20221010
		11	Tu					Brandon and Dakota Here: Wiegmann (with Z20), Mounting Bolts and Power Cable Assembly picked up (to be taken to LSWT)	T48-3		L17	20221011
		21	Fr					Onsite at LSWT: Windy but warm; T1 sensor silver taped through 1/4" hole; Fan control system plugged in and tested; Installed WP11; Connected B58, BTS and Z20 T2 on negative post, foam caps, battery terminal spray	T48-3 IMG		L17	20221021
		28	Fr					Z19-20; Z20 photos in Report, We8/17 (next to Z19, and on the Wiegmann back panel), Mo10/10 (on the garage bench, and inside the Wiegmann)	T48-3 DBT EML		L17	20221028

## Z21
Miscellaneous: Z21	A					MV_3: Murata DMR20-10-DCM-R-C

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D	L	WP14
2022	Oct	31	Mo					[Z21-22] TFTP (3) Voltmeters, Traco Disable Input: Aborted idea of using an output LED indicator light in favor of a small digital voltmeter / Small switches and voltmeter(s) all mount in backplate which eliminates the Power Cable Switch Assembly alltogether	DWP WP12	R&D			20221031
	Nov	21	Mo					[Z21-22] Design Changes for 1st Production Run, Voltmeter Modules Availability Research, CONCLUSIONs: / Voltmeter will not mount directly on backplate, the Meter Assembly s/b built on C-Channel; Murata DMR20-10-DCM-R-C looks good, but I need time for more R&D, requested sample / I don't have time now to introduce metering in the 1st Production Run, further development postponed until after WP13 Spare is ready	DWP WP12	Requested			20221121
		22	Tu					[Z21-22] Other Design Changes for 1st Production Run: Minor changes only (R&D postponed on Meter Assembly and Traco Disable Switch)					20221122
		23	We					[Z21-22] We may get a sample for the Meter Assembly for the 2nd Production Run with the help of Bill Beets EMLs, MO Murata Rep / I shared further info on the W150s including 20221008 0956 IMG_3305 PSE PSE.jpg (W150_1)	DWP EML WP12				20221123
		24	Th					[Z21-22] Bill Beets is trying to get me a sample; Murata confirmed to him that DigiKey and TTI are first in the queue to receive stock in early January; I shared further information on W150/12 and W150/24 voltages (7-57v)	DWP EML				20221124
		25	Fr					[Z21-22] Bill Beets will keep me informed on the sample status					20221125
	Dec	2	Fr					[Z21-22] Bill Beets EML Th12/1: "Murata was able to locate 1 pc of DMR20-10-DCM-R-C in engineering. This will be shipped directly to you within the next day or two."; Fedex overnight (tracking) / Free Meter Sample Received: Slated for WP14; Planning on incorporating these into the Meter Assemblies for the 2nd Production Run onwards / EML to Bill Beets (with CC to Sue Irvin, both at M2S Tech): "I'm impressed ..."; Attachment 20210207 1446 IMG_1259 PSE.jpg (RHS Boost Box w/Murata meter); "... I'll test the sample"		Available	L	WP14	20221202
		6	Tu					[Z21-22] EML from Bill Beets, who wanted to confirm that I had received the sample / Z21 tested on BK and ITECH, photos; EML to Bill Beets with photos	DWP EML IMG	R&D			20221206
		7	We					[Z21-22] Bill informed me that a 2nd Sample was being shipped to me (Z22 slated for WP15)	DWP EML				20221207
		8	Th					[Z21-22] 2nd Free Meter Sample Received: Delivered by UPS, opened and inspected (Z22 slated for WP15)	DWP			WP14	20221208
		18	Su					[Z21-22] Murata Meters WP14-15A Procurement Recordkeeping: Murata > 20221218 Datasheet DMR20-10-DCM-R-C - dmr20-10-dcm.pdf; Summary and History sheets created beginning with Mo10/31	DWP LIB			WP14	20221218
		19	Mo					[Z21-22] Murata Meters WP14-15A Procurement Recordkeeping: Designed, printed and applied W150 Meter Inventory Sticker 0.23.lbx; History sheets filled out	DWP LBX				20221219
		22	Th					[Z21-22] 20221021 Report, Photos & Invoice - LSWT Installation.pdf: Emailed to Keith and Mark; Murata meters and displayed voltages (13.5, 13.7 and 52.8v) mentioned in report with photo of Tu12/6 testing of Z21	T48-3 DBT EML				20221222
		23	Mo					[Z21-22] EML from Bill Beets: "Did you end up approving DMR20-10-DCM-R-C for use in your product?"	DWP EML			WP14	20221223
		29	Su					[Z21-22] EML reply to Bill Beets: / "Two prototypes are being built with the two meters we received. It may be a while before the final decision is made for production, but it looks good for now."					20221229
2023	Apr	4	Tu					[Z21-22] EML Rec'd from Bill Beets (Murata rep): "Was DMR20-10-DCM-R-C approved?"				WP14	20230404
		12	We					[Z21-22] Reply to Bill Beets: Mentioned how I was planning on doing the meter holes (will not use $$$ punch tool, 1-3/16" hole saw received from Amazon.com); Attached SSC of the meter area of the Meter Plate drawing	DWP SSC EML			WP14	20230412
		13	Th					[Z21-22] Hole Saw Examined [1-3/16" rec'd yesterday]: I'm curious as to how this will cut, as the best measurement I can make of the teeth OD is 1.1185"; EML from Bill Beets "I appreciate the update"	DWP EML				20230413
		24	Mo					[WP14-15] Mill Jigs (Postponed/Abandoned): The Meter Plates can be milled by starting with aligning and clamping them in the small 90⁰ vise; THEREFORE will move on to preparing to resume Assembly without any new jigs	DWP LIB				20230424

## Z22
Miscellaneous: Z22	A					MV_4: Murata DMR20-10-DCM-R-C

Date/Time CST/CDT					Description	Other Sources	Status	Location	WISPer
YYYY	Mmm	DD	Dw	~ ><	HH:MM	~ ><	HH:MM
				R&D	L	WP15
2022	Oct	31	Mo					Z21-22	DWP WP12	R&D			20221031
	Nov	21	Mo					Requested			20221121
		22	Tu					20221122
		23	We					DWP EML WP12				20221123
		24	Th					DWP EML				20221124
		25	Fr					20221125
	Dec	2	Fr					20221202
		6	Tu					DWP EML IMG				20221206
		7	We					DWP EML			WP15	20221207
		8	Th					DWP	Available	L	WP15	20221208
		18	Su					DWP LIB	R&D		WP15	20221218
		19	Mo					DWP LBX				20221219
		22	Th					T48-3 DBT EML				20221222
		23	Mo					DWP EML			WP15	20221223
		29	Su					20221229
2023	Apr	4	Tu					WP15	20230404
		12	We					DWP SSC EML			WP15	20230412
		13	Th					DWP EML				20230413
		24	Mo					DWP LIB				20230424

## WP1A
WISPers: WP1A	D		PARTS and ASSEMBLY LABOR	Quantity:		1	WP1		W50

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	2	Each	Power Supply/Charger: 75w/13.8v; Tcompensation function with external probe; 2 year warranty; Universal AC input 85-264VAC; Protections for short circuit, overload, over voltage, battery polarity (by fuse); DC output voltage detection signal (can be used for monitoring AC)	7/28/17	Mean Well	SCP-75-12	MOU	709-SCP75-12	BC4_5	$23.93	$47.86		$7.99	Ordering (all non-stock items except Battery); PS1 solder thermistor wire to board	3.00
BT Comp	1	Each	100Kohm NTC thermistor	8/10/17	Vishay / BC Components	NTCLE100E3104HB0	MOU	594-NTCLE100E3104HB0		$0.30	$0.30			Solder, shrink tube assembly	1.00
BT Comp	5	Feet	20-24 guage dual stranded wire, black, 4 feet extending + 1 foot internal							$0.10	$0.50	Estimate
BT Comp	1.5	Inches	1/8" shrink tube (to insulate between)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.18	8/2/18
BT Comp	1.75	Inches	3/16" shrink tube (first layer to cover both)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.22	8/2/18
BT Comp	2	Inches	1/4" shrink tube (outer layer)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.09	$0.19	8/2/18
Enclosure	1	Each	Aluminum Chassis Box, 8x10x2.5"	8/10/17	Hammond	1444-10825	MOU	546-1444-10825		$19.69	$19.69		$7.99	Enclosure prep total, mark, drill all holes, physical assembly (before wiring)	6.00
	1	Each	Aluminum Chassis Box "bottom" cover [not used]	8/10/17	Hammond	1434-108	MOU	546-1434-108			$0.00
	4	Each	Cover screws, #6x3/8" sheet metal screws [not needed]				BDC	2472			$0.00	7/30/18
	1	Each	Wire exit strain relief, 1/2" electrical "Romex clamp" with shrink tubing							$1.00	$1.00	Estimate
	2	Inches	1/2" Shrink Tube (wire exit strain relief)	5/30/15	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.19	$0.38	8/2/18
	10	Each	Button head allens wrench M3, L=5mm, initial order (100), also ordered Allen insert bit, 2mm ($1.79) but won't need to order this again if built again (hardware to mount power supplies)	8/11/17			BDC	18787		$0.03	$0.29		$4.95
	4	Each	Rubber feet, self adhesive (what I had in stock was ~1/4" diameter x 1/8" tall)							$0.25	$1.00	Estimate
Supply	1	Each	Power Cord: AC Input, cutoff from ones I have here, >3 feet extending + 1 foot internal							$3.00	$3.00	Estimate		Cut, tin and label colors (if needed)	0.50
	1	Each	Schottky Diode	8/10/17	Vishay	VS-STPS20L15D-N3	MOU	78-VS-STPS20L15D-N3		$3.43	$3.43
	1	Set	Schottky diode mounting hardware; Thermal pad or mica, screw, screw insulator, nut, lock washer, silver tape (to immobilize incoming wires), solder, silicone (to immobilize incoming wires)							$2.00	$2.00	Estimate
	1	Each	Fuse: 10A, PS1, "Battery, overload or reverse polarity" (one comes with each power supply, this is a spare)							$0.50	$0.50	Estimate
	4	Feet	Battery Cable: Red/Black zip pair, 3 feet extending + 1 foot internal, 16 gauge	8/11/17			bulkwire.com or powerwerx.com	Wire-RB-16-25		$1.72	$6.87		$12.05	Cut, tin ends	0.50
	4	Feet	Load Cable: Red/Black zip pair, 3 feet extending + 1 foot internal, 16 gauge	8/11/17			bulkwire.com or powerwerx.com	Wire-RB-16-25		$1.72	$6.87			Cut, tin ends	0.50
Misc.	6	Inches	Wire Labels: "Battery" and "Load", 3/8" Brother Tape	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.01	$0.07	8/2/18		Print and apply labels	0.50
	1	Each	Hook up wire, shrink tube, solder							$1.00	$1.00	Estimate		Wiring, soldering, shrinking (all internal connections)	2.00
	11	Inches	18 AWG Black Hookup Wire (stranded, AC PS1 to PS2)		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.32	8/2/18
	11	Inches	18 AWG White Hookup Wire (stranded, AC PS1 to PS2)		CNC Tech	1569-18-1-0500-002-1-TS	DKE	CN549W-25-ND	https://www.digikey.com/product-detail/en/cnc-tech/1569-18-1-0500-002-1-TS/CN549W-25-ND/7065847	$0.03	$0.32	7/30/18
	2	Inches	1/4" shrink tube (2x1" PS1 to battery cable)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.09	$0.19	8/2/18
	1.75	Inches	1/8" shrink tube (stagger cut unused wires PS1)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.21	8/2/18
	1.75	Inches	3/16" shrink tube (stagger cut unused wires PS1)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.22	8/2/18
	4	Each	Zip Ties, 4"		Belden	DT-04-18-GY-C	DKE	BEL8882-ND	https://www.digikey.com/products/en?keywords=BEL8882-ND	$0.03	$0.10	8/2/18		Bench test and adjustment of charge voltage	1.00

TOTALS:											$96.70		$32.98		15.00

Battery	1	Each	12 Volt 100 AH SLA (AGM), NB terminals (5/16" bolts, nuts and washers included)	7/14/17	SigmasTek	SP12-100	batterysharks.com	12V-100AH_B12-100	B26	$131.99	$131.99		$45.00	Ordering, Unpack, Initial Test and Charge	1.00

## WP2A
WISPers: WP2A	D		PARTS and ASSEMBLY LABOR	Quantity:		1	WP2		W100_1

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	1	Each	Power Supply	3/5/18	Delta Electronics	PMT-24V200W1AM	MOU	108-PMT-24V200W1AM	S4	$35.88	$35.88		$7.99	Order; Rec'v; Unpack	0.50
	1	Each	AC Power Cord: Input, >3 feet							$3.00	$3.00	Estimate		Cut, tin and label colors; Attach and test Power Supply	0.50
Genasun	1	Each	Genasun 10.5A MPPT, 12V Lead Acid	8/16/15	Genasun	GV-10-Pb-12V	alteEstore.com	GESGV-10-PB-12V	C4	$89.00	$89.00	8/2/18	$13.43	Order; Rec'v; Unpack; Remove cover; Bend LED out	0.50
	2	Each	6-32x1/4" Slotted round head machine screw, Zinc plated steel				BDC	1708	https://www.boltdepot.com/Product-Details.aspx?product=1708	$0.01	$0.03	8/2/18		Mount Genasun on Power Supply	0.50
Fan	1	Each	120vac 80x80x25mm [43 cfm, leftover from a long time ago]		Qualtek	FAA1-08025NBHW31	DKE	Q560-ND	https://www.digikey.com/products/en?keywords=Q560-ND	$14.03	$14.03	8/2/18
	1	Each	Fan guard, metal [leftover from a long time ago]		Qualtek	09325-F/30	DKE	CR212-ND	https://www.digikey.com/products/en?keywords=CR212-ND	$1.53	$1.53	8/2/18		Order; Rec'v; Unpack (fan and guard/filter)	0.50
	4	Each	6-32x2-15/16" Slotted round head machine screw, Zinc plated steel [from toggle bolts I had in stock]				BDC	1719	https://www.boltdepot.com/Product-Details.aspx?product=1719	$0.04	$0.15	8/2/18		Mount Fan on Power Supply	1.50
	12	Each	#6 SAE flat washers, Zinc plated steel				BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	$0.01	$0.15	8/2/18
	12	Each	#6 split lock washers, Zinc plated steel				BDC	3022	https://www.boltdepot.com/Product-Details.aspx?product=3022	$0.01	$0.14	8/2/18
	12	Each	6-32 Hex machine screw nuts, Zinc plated steel				BDC	2643	https://www.boltdepot.com/Product-Details.aspx?product=2643	$0.01	$0.17	8/2/18
	6	Inches	1/8" Shrink tubing (for leads)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.71	8/2/18
	1	Each	4" zip tie (to hold fan wire leads to #6 riser bolt)		Belden	DT-04-18-GY-C	DKE	BEL8882-ND	https://www.digikey.com/products/en?keywords=BEL8882-ND	$0.03	$0.03	8/2/18
Supply	36	Inches	#22 Stranded Red (Power Supply to Genasun Positive)		CNC Tech	1569-22-1-0500-004-1-TS	DKE	CN531R-25-ND	https://www.digikey.com/products/en?keywords=CN531R-25-ND	$0.02	$0.75	8/2/18		Cut, tin and wire Genasun to Power Supply	1.00
	2	Each	4" zip ties (to hold #22 loops to Power Supply)		Belden	DT-04-18-GY-C	DKE	BEL8882-ND	https://www.digikey.com/products/en?keywords=BEL8882-ND	$0.03	$0.05	8/2/18
	4	Inches	#18 Stranded Black (Power Supply to Genasun Negative)		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.12	8/2/18
Harness	4	Feet	#10 Stranded Red (Battery Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.03	DKE	C76832R-50-ND	https://www.digikey.com/products/en?keywords=C76832R-50-ND	$0.80	$3.18	8/3/18
	4	Feet	#10 Stranded Black (Battery Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	$0.80	$3.18	8/3/18
	2	Each	Ring connectors #10 - 5/16" (Battery) [Scott's Bargain Barn]		3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.22	$0.45	8/3/18
	28	Inches	#12 Stranded Red (Load Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.03	DKE	C76822R-50-ND	https://www.digikey.com/products/en?keywords=C76822R-50-ND	$0.05	$1.30	8/3/18
	36	Inches	#12 Stranded Black (Load Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.01	DKE	C76822B-50-ND	https://www.digikey.com/products/en?keywords=C76822B-50-ND	$0.05	$1.67	8/3/18
	6	Inches	#22 Solid (stripped, for 2x inline splices)		SparkFun Electronics	PRT-08023	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	$0.01	$0.05	8/3/18
	1	Each	#12 Inline ATM fuse holder	5/5/18	Eaton/Bussman	BP/HHM-RP	Scott's Bargain Barn			$2.09	$2.09		$3.78	Drive to SBB; Procure (based on buying 2 sets)	0.50
	2	Inches	3/16" Shrink tubing (for inline fuse butt splice)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.25	8/2/18
	2	Each	ATM fuses 20A (1 spare)	5/5/18	Couper/Bussman	BP/ATM-20-RP	Scott's Bargain Barn			$0.46	$0.92		$0.07
	2	Inches	Silver tape (spare fuse) [Fasson, from an HVAC supply house]		Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		$0.01	$0.02	8/1/18
	5	Inches	1/4" Shrink tubing (for 2x inline splices)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.09	$0.47	8/2/18
	3	Inches	1/2" Shrink tubing (for 2x battery ring connectors)	5/30/15	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.19	$0.57	8/2/18
	10	Grams	"44" Rosin Core Solder .050"	~2004	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	$0.10	$1.01	8/3/18
	2	Each	Wire nuts (protect Load ends from accidental short in installation) [Ideal #30-451J]				DKE			$0.10	$0.20	8/1/18
	1	Each	6" wire tie (to secure harness to power supply)	~2015			NAPA Auto Store	770-9204	https://www.napaonline.com/en/p/BK_7709204	$0.05	$0.05	8/1/18		Assemble and install harness; Test	2.75
Labels	12	Inches	3/8" .lbx: W100 Battery+, W100 Battery-, W100 Load+, W100 Load-, W100 34V MAX 12V	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.03	$0.36	8/3/18		Print and apply labels; Ready for delivery	1.00
	2	Inches	1/2" .lbx: W100 Power Supply Status	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.08	8/3/18
	9	Inches	3/4" .lbx: W100 Fan, W100 Status LED, W100 Battery Type, W100 Load Ratings	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.39	8/3/18
	2	Inches	1" yellow .lbx: W100 CAUTION!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.07	$0.14	8/3/18
	5	Inches	1-1/2" .lbx: W100 SN Man'f	~2010	Brother	TZe-261	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZe-261&rh=i%3Aaps%2Ck%3Abrother+TZe-261	$0.06	$0.28	8/3/18

TOTALS:									TOTALS:		$162.37		$25.27		9.25

Battery	2	Each	6 Volt 225 AH Flooded Deep Cycle, ELPT Terminals (5/16" nuts included)	4/21/16	Trojan	T-105	BFMS (Bill's Floor Machine Service), Kansas City MO		B9_10	$144.00	$288.00	~2018	$21.06	Drive to BFMS; Purchase; Initial Test and Charge	1.50
	12	Inches	#10 Stranded Green (Battery interconnection) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.06	DKE	C76832G-50-ND	https://www.digikey.com/product-detail/en/general-cable-carol-brand/76832.18.06/C76832G-50-ND/5452575	$0.07	$0.80	8/4/18		Assemble Battery interconnection	1.00
	2	Each	Ring connectors #10 - 5/16" (Battery interconnection) [Scott's Bargain Barn]		3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.22	$0.45	8/3/18
	3	Inches	1/2" Shrink tubing (for 2x battery ring connectors)	5/30/15	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.19	$0.57	8/2/18

TOTALS:									TOTALS:		$289.81		$21.06		2.50

## WP3A
WISPers: WP3A	D		PARTS and ASSEMBLY LABOR	Quantity:		1	WP3		W100_2

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor		Assembled
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	1	Each	Power Supply [Mouser 108-PMT-24V200W1AM $35.88 but this one was free]	3/9/18	Delta Electronics	PMT-24V200W1AM	DKE	1145-1076-ND	S5	$34.07	$34.07	8/4/18		Order; Rec'v; Unpack (all DigiKey items)	1.00
	1	Each	AC Power Cord: Input, >3 feet							$3.00	$3.00	Estimate		Cut, tin and label colors; Attach and test Power Supply	0.25
	1	Each	4" zip tie, Black (AC Line)		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	8/5/18
	1	Each	4" zip tie, White (AC Neutral)		Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	$0.03	$0.03	8/5/18
Genasun	1	Each	Genasun 10.5A MPPT, 12V Lead Acid	9/10/15	Genasun	GV-10-Pb-12V	alteEstore.com	GESGV-10-PB-12V	C6	$89.00	$89.00	8/2/18	$7.31	Order; Rec'v; Unpack; Remove cover	0.50
	2	Each	6-32x5/16" phillips pan head machine screw, Zinc plated steel Dad's stock]				BDC	9226	https://www.boltdepot.com/Product-Details.aspx?product=9226	$0.01	$0.03	8/5/18		Mount Genasun on Power Supply	0.25
Fan	1	Each	120vac 80x80x25mm 21 cfm	7/25/18	Qualtek	FAA1-08025NBHW31	DKE	Q560-ND	https://www.digikey.com/products/en?keywords=Q560-ND	$14.03	$14.03		$8.75	Mount Fan over Genasun (bend LED out); Cut (5.5" beyond fan), shrink, strip and tin fan leads; Remount cover on power supply; Attach fan to L & N; Test	2.00
	1	Each	Fan guard, plastic with filter	7/25/18	Qualtek	09325-F/30	DKE	CR212-ND	https://www.digikey.com/products/en?keywords=CR212-ND	$1.53	$1.53
	4	Each	6-32x3" Phillips flat head machine screws, SS 18-8 (2-3/4" is the ideal length, 3" must be cut to keep them out of the power supply components, or the fan must be mounted higher than necessary) [2-15/16" slotted round head zinc plated steel, from toggle bolts I had in stock]				BDC	1246	https://www.boltdepot.com/Product-Details.aspx?product=1246	$0.14	$0.55	8/8/18
	8	Each	#6 SAE flat washers, Zinc plated steel				BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	$0.01	$0.10	8/2/18
	8	Each	#6 split lock washers, Zinc plated steel				BDC	3022	https://www.boltdepot.com/Product-Details.aspx?product=3022	$0.01	$0.09	8/2/18
	12	Each	6-32 Hex machine screw nuts, Zinc plated steel				BDC	2643	https://www.boltdepot.com/Product-Details.aspx?product=2643	$0.01	$0.17	8/2/18
	5.5	Inches	1/8" Shrink tubing (for leads)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.65	8/2/18
	1	Each	4" zip tie, Black (to hold fan wire leads to #6 riser bolt)		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	8/5/18
Supply	36	Inches	#22 Stranded Red (Power Supply to Genasun Positive)		CNC Tech	1569-22-1-0500-004-1-TS	DKE	CN531R-25-ND	https://www.digikey.com/products/en?keywords=CN531R-25-ND	$0.02	$0.75	8/2/18		Cut, tin and wire Genasun to Power Supply	0.50
	3	Each	4" zip ties, Red (to hold #22 loops to Power Supply)		Belden	DT-04-18-RE-C	DKE	BEL8885-ND	https://www.digikey.com/products/en/cables-wires-management/cable-ties-and-cable-lacing/482?k=&pkeyword=&pv37=1&FV=fffc0087%2C24200199%2Cffe001e2&quantity=0&ColumnSort=0&page=1&stock=1&pageSize=25	$0.03	$0.08	8/5/18
	4	Inches	#18 Stranded Black (Power Supply to Genasun Negative)		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.12	8/2/18
Harness	4	Feet	#10 Stranded Red (Battery Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.03	DKE	C76832R-50-ND	https://www.digikey.com/products/en?keywords=C76832R-50-ND	$0.80	$3.18	8/3/18
	4	Feet	#10 Stranded Black (Battery Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	$0.80	$3.18	8/3/18
	2	Each	Ring connectors #10 - 5/16" (Battery) [Scott's Bargain Barn]		3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.22	$0.45	8/3/18
	28	Inches	#12 Stranded Red (Load Positive) [36", 1st harness made, Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.03	DKE	C76822R-50-ND	https://www.digikey.com/products/en?keywords=C76822R-50-ND	$0.05	$1.30	8/3/18
	36	Inches	#12 Stranded Black (Load Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.01	DKE	C76822B-50-ND	https://www.digikey.com/products/en?keywords=C76822B-50-ND	$0.05	$1.67	8/3/18
	6	Inches	#22 Solid (stripped, for 2x inline splices)		SparkFun Electronics	PRT-08023	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	$0.01	$0.05	8/3/18
	1	Each	#12 Inline ATM fuse holder	5/5/18	Eaton/Bussman	BP/HHM-RP	Scott's Bargain Barn			$2.09	$2.09		$3.78	Drive to SBB; Procure (based on buying 2 sets)	0.50
	2	Inches	3/16" Shrink tubing (for inline fuse butt splice)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.25	8/2/18
	2	Each	ATM fuses 20A (1 spare)	5/5/18	Couper/Bussman	BP/ATM-20-RP	Scott's Bargain Barn			$0.46	$0.92		$0.07
	1	Inch	Silver tape (spare fuse) [Fasson, from an HVAC supply house]		Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		$0.01	$0.01	8/1/18
	5	Inches	1/4" Shrink tubing (for 2x inline splices)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.09	$0.47	8/2/18
	3	Inches	1/2" Shrink tubing (for 2x battery ring connectors)	5/30/15	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.19	$0.57	8/2/18
	10	Grams	6" zip tie (to secure harness to power supply)	~2004	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	$0.10	$1.01	8/3/18
	2	Each	Wire nuts (protect Load ends from accidental short in installation) [Ideal #30-451J]				DKE			$0.10	$0.20	8/1/18
	1	Each	6" zip tie, White (to secure harness to power supply) [NAPA Auto Store 770-9204, https://www.napaonline.com/en/p/BK_7709204, $5.49/100, 8/1/18]	~2015	Qualtek	17-M150N-C	DKE	Q731-ND	https://www.digikey.com/product-detail/en/qualtek/17-M150N-C/Q731-ND/4072233	$0.03	$0.03	8/5/18		Assemble and install harness; Test	2.75
Misc	1	Oz	Flux Remover (all soldered connections) [not ordered, not used]		Techspray	1631-16S	DKE	1873-1102-ND	https://www.digikey.com/product-detail/en/techspray/1631-16S/1873-1102-ND/7914566	$1.85	$1.85	8/3/18
Labels	12	Inches	3/8" .lbx: W100 Battery+, W100 Battery-, W100 Load+, W100 Load-, W100 34V MAX 12V	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.03	$0.36	8/3/18
	2	Inches	1/2" .lbx: W100 Power Supply Status	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.08	8/3/18
	7.6	Inches	3/4" .lbx: W100 Fan, W100 Status LED, W100 Battery Type, W100 Load Ratings	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.33	8/3/18
	2.3	Inches	1" yellow .lbx: W100 CAUTION!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.07	$0.16	8/3/18		Print with Battery I NEED WATER!!!! (it will save tape)
	5.5	Inches	1-1/2" .lbx: W100 SN Man'f	~2010	Brother	TZe-261	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZe-261&rh=i%3Aaps%2Ck%3Abrother+TZe-261	$0.06	$0.31	8/3/18		Print and apply labels; Ready for delivery	1.00

TOTALS:									TOTALS:		$162.72		$19.91		8.75

Battery	1	Each	12 Volt 105 AH Flooded Deep Cycle, Wingnut Terminal (WNT) 5/16" (wingnuts included) [Battery Outfitters, Columbia MO]	4/22/15	Trojan	27TMX	BFMS (Bill's Floor Machine Service), Kansas City MO		B1	$151.60	$151.60	~2018	$42.12	Drive to BFMS; Purchase; Initial Test and Charge	3.00
	6.3	Inches	1" yellow .lbx, two labels: I NEED WATER!!!!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.07	$0.45	8/3/18		Print with Label W100 CAUTION! (it will save tape)
W100 Mount	4	Each	Top Fixing Bracket [not ordered or used]		Delta Electronics	LM-01	DKE?		http://www.deltapsu.com/download/delta-standard-power-supplies-catalog					Package and label Mounting Kit	0.50
	4	Each	Metric machine screw phillips pan head M4x0.7x6, SS 18-8 (to mount brackets to Power Supply) [zinc plated steel, DigiKey 335-1147-ND, $0.67x4, to mount W100 to inside wall of equipment box @ RW]	7/25/18			BDC	11876	https://www.boltdepot.com/Product-Details.aspx?product=11876	$0.05	$0.19	8/4/18
	4	Each	Sheet metal screw #6x1/2", hex washer head self drilling, SS 410 (for mounting W100 to a wall, sheet metal or wood) [not ordered or used]				BDC	7148	https://www.boltdepot.com/Product-Details.aspx?product=7148	$0.07	$0.27	8/4/18
	1	Each	Small Plastic Bag for "W100 Mounting Kit" [not used]
	2	Inches	1/2" .lbx: W100 Mounting Kit [not used]	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.08	8/3/18

TOTALS:									TOTALS:		$152.59		$42.12		3.50

## WP4A
WISPers: WP4A	D		PARTS and ASSEMBLY LABOR	Quantity:		1	WP4		W100_3

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor		Assembled
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	1	Each	24v/200w Power Supply [Ordered only 2 and did not get Quantity 5 Price Break]	6/12/19	Delta Electronics	PMT-24V200W1AM	DKE	1145-1076-ND	PMT-24V200W1AM	$44.74	$44.74	6/8/19	$4.50	Order; Rec'v; Unpack (all DigiKey and BoltsDepot items); Inventory Label	0.75
	1	Each	AC Power Cord: Input, >3 feet							$3.00	$3.00	Estimate
	1	Each	4" zip tie, Black (AC Line) [Not needed or used]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	6/8/19		Cut, tin (label colors if needed)	0.25
	1	Each	4" zip tie, White (AC Neutral) [Not needed or used]		Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	$0.03	$0.03	6/8/19
Genasun	1	Each	Genasun 10.5A MPPT, 12V Lead Acid	4/22/15	Genasun	GV-10-Pb-12V	alteEstore.com	GESGV-10-PB-12V	C1	$89.00	$89.00	6/8/19	$13.43	Order; Rec'v; Unpack, Controllers updated, Inventory sticker (base) [print other 1/2" labels]; Remove cover; Sticker Genasun_#	0.50
	1.5	Inches	1/2" .lbx: Inventory Sticker 0.5 [Not used]	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.06	8/3/18
	1.5	Inches	1/4" .lbx: Genasun #		Brother	TZe-211	Amazon.com			$0.03	$0.04	Estimate
	2	Each	6-32x5/16" phillips pan head machine screw, Zinc plated steel [Dad's stock]				BDC	9226	https://www.boltdepot.com/Product-Details.aspx?product=9226	$0.01	$0.03	6/8/19		Mount Genasun on Power Supply	0.25
Fan	1	Each	120vac 80x80x25mm 21 cfm [Ordered only 2 and did not get Quantity 10 Price Break]	6/12/19	Qualtek	FAA1-08025NBHW31	DKE	Q560-ND	https://www.digikey.com/products/en?keywords=Q560-ND	$13.36	$13.36	6/8/19		Remove Power Supply cover; Remove fan filter; Mount Fan over Genasun; Replace fan filter; Replace Power Supply cover; Bend LED out; Cut leads 5.5" beyond fan, 5.25" shrink, strip and tin fan leads; Attach fan to L & N; Test	1.25
	1	Each	Fan guard, plastic with filter [Ordered only 2 and did not get Quantity 10 Price Break]	6/12/19	Qualtek	09325-F/30	DKE	CR212-ND	https://www.digikey.com/products/en?keywords=CR212-ND	$1.50	$1.50	6/8/19
	4	Each	6-32x3" Phillips flat head machine screws, SS 18-8 (2-3/4" is the ideal length, but 3" can be used, top stop nut 1/2" from end, then lock washer, washer, cover, washer, bottom nut, final check that screws protrude no more than about 3/8" into power supply)	6/12/19			BDC	1246	https://www.boltdepot.com/Product-Details.aspx?product=1246	$0.14	$0.57	6/8/19	$3.40
	8	Each	#6 SAE flat washers, Zinc plated steel [Old stock]				BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	$0.01	$0.10	6/8/19
	8	Each	#6 split lock washers, Zinc plated steel [Old stock]				BDC	3022	https://www.boltdepot.com/Product-Details.aspx?product=3022	$0.01	$0.09	6/8/19
	12	Each	6-32 Hex machine screw nuts, Zinc plated steel [Old stock]				BDC	2643	https://www.boltdepot.com/Product-Details.aspx?product=2643	$0.01	$0.17	6/8/19
	5.25	Inches	1/8" Shrink tubing (for leads)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.64	6/8/19
	1	Each	4" zip tie, Black (to hold fan wire leads to #6 riser bolt) [Old stock]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	6/8/19
Supply	36	Inches	#22 Stranded Red (Power Supply to Genasun Positive) [Old stock]		CNC Tech	1569-22-1-0500-004-1-TS	DKE	CN531R-25-ND	https://www.digikey.com/products/en?keywords=CN531R-25-ND	$0.02	$0.81	6/8/19		Cut, strip 22 guage so end can be doubled back, tin and wire Genasun to Power Supply	0.50
	3	Each	4" zip ties, Red (to hold #22 loops to Power Supply) [Old stock]		Belden	DT-04-18-RE-C	DKE	BEL8885-ND	https://www.digikey.com/products/en/cables-wires-management/cable-ties-and-cable-lacing/482?k=&pkeyword=&pv37=1&FV=fffc0087%2C24200199%2Cffe001e2&quantity=0&ColumnSort=0&page=1&stock=1&pageSize=25	$0.03	$0.08	6/8/19
	4	Inches	#18 Stranded Black (Power Supply to Genasun Negative) [Old stock]		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.13	6/8/19
Harness	28	Inches	#12 Stranded Red (Load Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.03	DKE	C76822R-50-ND	https://www.digikey.com/products/en?keywords=C76822R-50-ND	$0.05	$1.30	6/8/19
	1	Each	#12 Inline ATM fuse holder	4/27/19	Eaton/Bussman	BP/HHM-RP	Ace Hardware			$3.58	$3.58	4/27/19	$2.00	Drive to Ace Hardware E.S.; Procure (based on buying 5 and divided between 3 Excelsior Springs items)	0.13
	2	Inches	3/16" Shrink tubing (for inline fuse butt splice)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.25	6/8/19
	2	Each	ATM fuses 20A (1 spare)	5/10/19	Couper/Bussman	BP/ATM-20-RP	WalMart			$0.79	$1.59	5/10/19	$2.15
	1	Inch	Silver tape (spare fuse) [Old stock from an HVAC supply house]		Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		$0.01	$0.01	8/1/18		Drive to WalMart E.S.; Procure (based on buying 10 and divided between 3 Excelsior Springs items)	0.13
	36	Inches	#12 Stranded Black (Load Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.01	DKE	C76822B-50-ND	https://www.digikey.com/products/en?keywords=C76822B-50-ND	$0.05	$1.67	6/8/19
	4	Feet	#10 Stranded Red (Battery Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.03	DKE	C76832R-50-ND	https://www.digikey.com/products/en?keywords=C76832R-50-ND	$0.80	$3.18	6/8/19
	4	Feet	#10 Stranded Black (Battery Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	$0.80	$3.18	6/8/19		Assemble; #12 solder work and tinning the ends of the #10 can be done with Weller D550; Inline splices and ring connectors require a torch; Install harness; Brief test on 12v battery	2.00
	6	Inches	#22 Solid (stripped, for 2x inline splices) [Old stock]		SparkFun Electronics	PRT-08023	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	$0.01	$0.05	6/8/19
	5	Inches	1/4" Shrink tubing (for 2x inline splices)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.16	$0.79	6/8/19
	3	Inches	1/2" Shrink tubing (for 2x battery ring connectors)	10/1/18	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.20	$0.59	6/8/19
	2	Each	Ring connectors #10 - 5/16" (Battery) [Scott's Bargain Barn]		3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.24	$0.48	6/8/19
	10	Grams	"44" Rosin Core Solder .050"	~2004	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	$0.10	$1.00	6/8/19
	2	Each	Wire nuts (protect Load ends from accidental short in installation) [Ideal #30-451J]				DKE			$0.10	$0.20	8/1/18
	1	Each	6" zip tie, White (to secure harness to power supply) [NAPA Auto Store 770-9204, https://www.napaonline.com/en/p/BK_7709204, $5.49/100, 8/1/18]	~2015	Qualtek	17-M150N-C	DKE	Q731-ND	https://www.digikey.com/product-detail/en/qualtek/17-M150N-C/Q731-ND/4072233	$0.03	$0.03	6/8/19
Misc	1	Oz	Flux Remover (all soldered connections) [Not ordered, not used]		Techspray	1631-16S	DKE	1873-1102-ND	https://www.digikey.com/product-detail/en/techspray/1631-16S/1873-1102-ND/7914566	$1.96	$1.96	6/8/19
Labels	11.5	Inches	3/8" .lbx: W100 Battery+, W100 Battery-, W100 Load+, W100 Load-, W100 34V MAX 12V	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.03	$0.35	8/3/18		Print and apply labels; Print 3/4" with W100 Mount Mounting Screws; Print 1” yellow with I NEED WATER labels for battery (it will save tape)	0.75
TOTALS:	2	Inches	1/2" .lbx: W100 Power Supply Status	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.08	6/22/19
	7.0	Inches	3/4" .lbx: W100 Fan, W100 Status LED, W100 Battery Type, W100 Load Ratings	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.31	6/22/19
	4.3	Inches	1" yellow .lbx: W100 CAUTION!	~2010	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.05	$0.23	6/22/19
	2.3	Inches	1-1/2" .lbx: W100 SN Man'f	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.08	$0.18	6/22/19
W100 Mount	4	Each	Top Fixing Bracket (alternative to Delta Electronics LM-01), 3/4"x1/2" Corner Brace, Zinc	6/12/19	Hardware Essentials	H#853084	Ace Hardware	008236987720 (516606)		$0.69	$2.76	6/12/19	$2.76	Drive to Ace Hardware E.S.; Procure (based on buying 5 sets and divided between 3 Excelsior Springs items)	0.13
	4	Each	Metric machine screw phillips pan head M4x0.7x6, SS 18-8 (to mount brackets to Power Supply) [These work, but bracket, lockwasher & starwasher use up > 2mm, when reordered consider 7 or 8 mm length if available]	6/12/19			BDC	11876	https://www.boltdepot.com/Product-Details.aspx?product=11876	$0.05	$0.19	6/9/19
	4	Each	Split Washer M4 [#8 from stock]							$0.02	$0.08	6/22/19		Install Brackets (M4 screw, lock washer, bracket, toothed washer, VERY TIGHT and straight); Package and label Mounting Screws; Ready for Delivery	0.25
TOTALS:	4	Each	Toothed Washer M4 [#8 from stock]							$0.02	$0.08	6/22/19
	4	Each	Sheet metal screw #8x1/2", hex washer head self drilling, SS 410 (for mounting W100 with brackets to a wall, sheet metal or wood) [#8x1/2" zinc from stock]				BDC	7154	https://www.boltdepot.com/Product-Details.aspx?product=7154	$0.08	$0.31	6/9/19
	1	Each	Small Plastic Bag for sheet metal screws [Leftover bags in stock]							$0.05	$0.05	6/22/19
	2.1	Inches	3/4" .lbx: W100 Mounting screws	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.09	6/22/19

W100 TOTALS:											$178.97		$28.24		6.90

Battery	1	Each	12 Volt 105 AH Flooded Deep Cycle, Wingnut Terminal (WNT) 5/16" (wingnuts included)	6/5/19	Trojan	27TMX	BFMS (Bill's Floor Machine Service), Kansas City MO	27TMX	B54	$166.50	$166.50	6/5/19	$45.24	Drive to BFMS; Purchase; Initial Test and Charge; Labels	4.00
	8.0	Inches	1" yellow .lbx, two labels, one label per filler cap on 27TMX: I NEED WATER!!!!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.08	$0.64	6/22/19
	0.5	Gal	Distilled Water [planned but not provided, can remove on future assemblies]	8/5/19	Great Value		WalMart	0 78742 35191 9		$0.94	$0.47	8/5/19	$0.06	While at WalMart anyway purchase; Clean and dry jar; Apply label	0.25
	1.0	Each	Small jar to use to facilitate filling the battery with water [planned but not provided, can remove on future assemblies]							$0.00	$0.00	8/6/19
	2.5	Inches	1" .lbx: Battery Watering Jar [planned but not provided, can remove on future assemblies]	~2010	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.05	$0.14	6/22/19

Battery TOTALS:											$167.75		$45.30		4.25

## WP5A
WISPers: WP5A	D		PARTS and ASSEMBLY LABOR	Quantity:		1	WP5		W100_4

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor		Assembled
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	1	Each	24v/200w Power Supply [Ordered only 2 and did not get Quantity 5 Price Break]	6/12/19	Delta Electronics	PMT-24V200W1AM	DKE	1145-1076-ND	PMT-24V200W1AM	$44.74	$44.74	6/8/19	$4.50	Order; Rec'v; Unpack (all DigiKey and BoltsDepot items); Inventory Label	0.75
	1	Each	AC Power Cord: Input, >3 feet							$3.00	$3.00	Estimate
	1	Each	4" zip tie, Black (AC Line) [Not needed or used]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	6/8/19		Cut, tin (label colors if needed)	0.25
	1	Each	4" zip tie, White (AC Neutral) [Not needed or used]		Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	$0.03	$0.03	6/8/19
Genasun	1	Each	Genasun 10.5A MPPT, 12V Lead Acid	5/4/15	Genasun	GV-10-Pb-12V	alteEstore.com	GESGV-10-PB-12V	C2	$89.00	$89.00	6/8/19	$13.47	Order; Rec'v; Unpack, Controllers updated, Inventory sticker (base) [print other 1/2" labels]; Remove cover; Sticker Genasun_#	0.50
	1.5	Inches	1/2" .lbx: Inventory Sticker 0.5 [Not used]	8/12/15	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.06	8/3/18
	1.5	Inches	1/4" .lbx: Genasun #		Brother	TZe-211	Amazon.com			$0.03	$0.04	Estimate
	2	Each	6-32x5/16" phillips pan head machine screw, Zinc plated steel Dad's stock]				BDC	9226	https://www.boltdepot.com/Product-Details.aspx?product=9226	$0.01	$0.03	6/8/19		Mount Genasun on Power Supply	0.25
Fan	1	Each	120vac 80x80x25mm 21 cfm [Ordered only 2 and did not get Quantity 10 Price Break]	6/12/19	Qualtek	FAA1-08025NBHW31	DKE	Q560-ND	https://www.digikey.com/products/en?keywords=Q560-ND	$13.36	$13.36	6/8/19		Remove Power Supply cover; Remove fan filter; Mount Fan over Genasun; Replace fan filter; Replace Power Supply cover; Bend LED out; Cut leads 5.5" beyond fan, 5.25" shrink, strip and tin fan leads; Attach fan to L & N; Test	1.25
	1	Each	Fan guard, plastic with filter [Ordered only 2 and did not get Quantity 10 Price Break]	6/12/19	Qualtek	09325-F/30	DKE	CR212-ND	https://www.digikey.com/products/en?keywords=CR212-ND	$1.50	$1.50	6/8/19
	4	Each	6-32x3" Phillips flat head machine screws, SS 18-8 (2-3/4" is the ideal length, but 3" can be used, top stop nut 1/2" from end, then lock washer, washer, cover, washer, bottom nut, final check that screws protrude no more than about 3/8" into power supply)	6/12/19			BDC	1246	https://www.boltdepot.com/Product-Details.aspx?product=1246	$0.14	$0.57	6/8/19	$3.40
	8	Each	#6 SAE flat washers, Zinc plated steel [Old stock]				BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	$0.01	$0.10	6/8/19
	8	Each	#6 split lock washers, Zinc plated steel [Old stock]				BDC	3022	https://www.boltdepot.com/Product-Details.aspx?product=3022	$0.01	$0.09	6/8/19
	12	Each	6-32 Hex machine screw nuts, Zinc plated steel [Old stock]				BDC	2643	https://www.boltdepot.com/Product-Details.aspx?product=2643	$0.01	$0.17	6/8/19
	5.25	Inches	1/8" Shrink tubing (for leads)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.64	6/8/19
	1	Each	4" zip tie, Black (to hold fan wire leads to #6 riser bolt) [Old stock]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	6/8/19
Supply	36	Inches	#22 Stranded Red (Power Supply to Genasun Positive) [Old stock, White]		CNC Tech	1569-22-1-0500-004-1-TS	DKE	CN531R-25-ND	https://www.digikey.com/products/en?keywords=CN531R-25-ND	$0.02	$0.81	6/8/19		Cut, strip 22 guage so end can be doubled back, tin and wire Genasun to Power Supply	0.50
	3	Each	4" zip ties, Red (to hold #22 loops to Power Supply) [Old stock]		Belden	DT-04-18-RE-C	DKE	BEL8885-ND	https://www.digikey.com/products/en/cables-wires-management/cable-ties-and-cable-lacing/482?k=&pkeyword=&pv37=1&FV=fffc0087%2C24200199%2Cffe001e2&quantity=0&ColumnSort=0&page=1&stock=1&pageSize=25	$0.03	$0.08	6/8/19
	4	Inches	#18 Stranded Black (Power Supply to Genasun Negative) [Old stock]		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.13	6/8/19
Harness	28	Inches	#12 Stranded Red (Load Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.03	DKE	C76822R-50-ND	https://www.digikey.com/products/en?keywords=C76822R-50-ND	$0.05	$1.30	6/8/19
	1	Each	#12 Inline ATM fuse holder	4/27/19	Eaton/Bussman	BP/HHM-RP	Ace Hardware			$3.58	$3.58	4/27/19	$2.00	Drive to Ace Hardware E.S.; Procure (based on buying 5 and divided between 3 Excelsior Springs items)	0.13
	2	Inches	3/16" Shrink tubing (for inline fuse butt splice)	5/30/15	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/products/en?keywords=EPS2316-ND	$0.13	$0.25	6/8/19
	2	Each	ATM fuses 20A (1 spare)	5/10/19	Couper/Bussman	BP/ATM-20-RP	WalMart			$0.79	$1.59	5/10/19	$2.15
	1	Inch	Silver tape (spare fuse) [Old stock from an HVAC supply house]		Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		$0.01	$0.01	8/1/18		Drive to WalMart E.S.; Procure (based on buying 10 and divided between 3 Excelsior Springs items)	0.13
	36	Inches	#12 Stranded Black (Load Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.01	DKE	C76822B-50-ND	https://www.digikey.com/products/en?keywords=C76822B-50-ND	$0.05	$1.67	6/8/19
	4	Feet	#10 Stranded Red (Battery Positive) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.03	DKE	C76832R-50-ND	https://www.digikey.com/products/en?keywords=C76832R-50-ND	$0.80	$3.18	6/8/19
	4	Feet	#10 Stranded Black (Battery Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	$0.80	$3.18	6/8/19		Assemble; #12 solder work and tinning the ends of the #10 can be done with Weller D550; Inline splices and ring connectors require a torch; Install harness; Brief test on 12v battery	2.00
	6	Inches	#22 Solid (stripped, for 2x inline splices) [Old stock]		SparkFun Electronics	PRT-08023	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	$0.01	$0.05	6/8/19
	5	Inches	1/4" Shrink tubing (for 2x inline splices)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.16	$0.79	6/8/19
	3	Inches	1/2" Shrink tubing (for 2x battery ring connectors)	10/1/18	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/products/en?keywords=EPS2012-ND	$0.20	$0.59	6/8/19
	2	Each	Ring connectors #10 - 5/16" (Battery) [Scott's Bargain Barn]		3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.24	$0.48	6/8/19
	10	Grams	"44" Rosin Core Solder .050"	~2004	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	$0.10	$1.00	6/8/19
	2	Each	Wire nuts (protect Load ends from accidental short in installation) [Ideal #30-451J]				DKE			$0.10	$0.20	8/1/18
	2	Each	6" zip tie, White (to secure harness to power supply) [NAPA Auto Store 770-9204, https://www.napaonline.com/en/p/BK_7709204, $5.49/100, 8/1/18]	~2015	Qualtek	17-M150N-C	DKE	Q731-ND	https://www.digikey.com/product-detail/en/qualtek/17-M150N-C/Q731-ND/4072233	$0.03	$0.07	6/8/19
Misc	1	Oz	Flux Remover (all soldered connections) [Not ordered, not used]		Techspray	1631-16S	DKE	1873-1102-ND	https://www.digikey.com/product-detail/en/techspray/1631-16S/1873-1102-ND/7914566	$1.96	$1.96	6/8/19
Labels	11.5	Inches	3/8" .lbx: W100 Battery+, W100 Battery-, W100 Load+, W100 Load-, W100 34V MAX 12V	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.03	$0.35	8/3/18		Print and apply labels; Print 3/4" with W100 Mount Mounting Screws; Print 1” yellow with I NEED WATER labels for battery (it will save tape)	0.75
TOTALS:	2	Inches	1/2" .lbx: W100 Power Supply Status		Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.08	6/22/19
	7.0	Inches	3/4" .lbx: W100 Fan, W100 Status LED, W100 Battery Type, W100 Load Ratings	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.31	6/22/19
	4.3	Inches	1-1/2" .lbx: W100 SN Man'f	~2010	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.05	$0.23	6/22/19
	2.3	Inches	1" yellow .lbx: W100 CAUTION!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.08	$0.18	6/22/19
W100 Mount	4	Each	Top Fixing Bracket (alternative to Delta Electronics LM-01), 3/4"x1/2" Corner Brace, Zinc	6/12/19	Hardware Essentials	H#853084	Ace Hardware	008236987720 (516606)		$0.69	$2.76	6/12/19	$2.76	Drive to Ace Hardware E.S.; Procure (based on buying 5 sets and divided between 3 Excelsior Springs items)	0.13
	4	Each	Metric machine screw phillips pan head M4x0.7x6, SS 18-8 (to mount brackets to Power Supply) [These work, but bracket, lockwasher & starwasher use up > 2mm, when reordered consider 7 or 8 mm length if available]	6/12/19			BDC	11876	https://www.boltdepot.com/Product-Details.aspx?product=11876	$0.05	$0.19	6/9/19
	4	Each	Split Washer M4 [#8 from stock]							$0.02	$0.08	6/22/19		Install Brackets (M4 screw, lock washer, bracket, toothed washer, VERY TIGHT and straight); Package and label Mounting Screws; Ready for Delivery	0.25
TOTALS:	4	Each	Toothed Washer M4 [#8 from stock]							$0.02	$0.08	6/22/19
	4	Each	Sheet metal screw #8x1/2", hex washer head self drilling, SS 410 (for mounting W100 with brackets to a wall, sheet metal or wood) [#8x1/2" zinc from stock]				BDC	7154	https://www.boltdepot.com/Product-Details.aspx?product=7154	$0.08	$0.31	6/9/19
	1	Each	Small Plastic Bag for sheet metal screws [Leftover bags in stock]							$0.05	$0.05	6/22/19
	2.1	Inches	3/4" .lbx: W100 Mounting screws	1/22/16	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.09	6/22/19

W100 TOTALS:											$179.01		$28.28		6.90

Battery	1	Each	12 Volt 105 AH Flooded Deep Cycle, Wingnut Terminal (WNT) 5/16" (wingnuts included)	5/7/20	Trojan	27TMX	BFMS (Bill's Floor Machine Service), Kansas City MO	27TMX	B56	$166.50	$166.50	5/7/20	$44.85	Drive to BFMS; Purchase; Initial Test and Charge; Labels	4.00
	8.0	Inches	1" yellow .lbx, two labels, one label per filler cap on 27TMX: I NEED WATER!!!!	~2010	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.08	$0.64	6/22/19
	0.5	Gal	Distilled Water [planned but not provided, can remove on future assemblies]	8/5/19	Great Value		WalMart	0 78742 35191 9		$0.94	$0.47	8/5/19	$0.06	While at WalMart anyway purchase; Clean and dry jar; Apply label	0.25
	1.0	Each	Small jar to use to facilitate filling the battery with water [planned but not provided, can remove on future assemblies]							$0.00	$0.00	8/6/19
	2.5	Inches	1" .lbx: Battery Watering Jar [planned but not provided, can remove on future assemblies]	~2010	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.05	$0.14	6/22/19

Battery TOTALS:											$167.75		$44.91		4.25

## WP6-10A
WISPers: WP6-10A	D		PARTS and ASSEMBLY LABOR	Quantity:		5	WP6 ... WP10		W100_5 ... W100_9

Sub Assembly	Quantity	Units	Description	Order Information										Projected Labor		Assembled
				Stock / Order Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Link	Unit Cost	Total Cost	Pricing Date	S&H, Tax	Description	Labor Hours
Supply	1	Each	24v/200w Power Supply	5/26/20	Delta Electronics	PMT-24V200W1AM	DKE	1145-1076-ND	PMT-24V200W1AM	$47.34	$47.34	5/26/20	$1.80	Procurement: All Suppliers; Order; Rec'v; Inventory, accounting and .ods updates	2.95
	1	Each	AC Power Cord: Input, 5 feet							$3.00	$3.00	Estimate
	0.4	Each	4" zip tie, Black (AC Line) [used on 2/5]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.01	6/8/19		Inventory Label; Cut; Strip 1”; Tin; Label colors if needed; Remove cover & mark w/template; .ods	0.48
	0.4	Each	4" zip tie, White (AC Neutral) [used on 2/5]		Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	$0.03	$0.01	6/8/19
Labels	1.4	Inches	1/4": Genasun #	6/22/19	Brother	TZe-211	Amazon.com			$0.03	$0.04	6/22/19		Print labels (except 1” W100 SN Man’f and Battery Inventory Label); Labels are applied to different Sub-Assemblies as built; Quantity of tape and time to print based upon building 5 units all at once; Print same width labels together; Chain print to save tape	0.32
	11.2	Inches	3/8": W100 Battery+, W100 Battery-, W100 Load+, W100 Load-, W100 34V MAX 12V	8/12/15	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	$0.03	$0.34	8/3/18
	3.3	Inches	1/2": Power Supply Inventory Sticker, Genasun Inventory Sticker, W100 Power Supply Status	6/22/19	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	$0.04	$0.13	6/22/19
	8.3	Inches	3/4": W100 Fan ..., W100 Status ..., W100 Battery ..., W100 Load ..., W100 Mounting …	6/22/19	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	$0.04	$0.37	6/22/19
	7.0	Inches	1" yellow: W100 CAUTION!, I NEED WATER!!!! (one label per filler cap on 27TMX)	6/22/19	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	$0.08	$0.58	6/22/19
	4.0	Inches	1": W100 SN Man'f	6/22/19	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.06	$0.23	6/22/19		Print and apply SN label: Record under Misc.
	2.6	Inches	1": Battery Inventory Sticker	6/22/19	Brother	TZe-251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	$0.06	$0.15	6/22/19		Print and apply to Battery: Record under Battery
Genasun	1	Each	Genasun 10.5A MPPT, 12V Lead Acid	5/26/20	Genasun	GV-10-Pb-12V	alteEstore.com	GESGV-10-PB-12V	https://www.altestore.com/store/charge-controllers/solar-charge-controllers/mppt-solar-charge-controllers/genasun-gv-10-pb-12v-105a-mppt-controller-for-12v-lead-acid-batteries-p10626/	$89.00	$89.00	5/26/20	$3.50	Genasun_# & Inventory Label; Remove cover; FLA/SLA jumpers; Mount on Power Supply; .ods	0.33
	2	Each	6-32x5/16" phillips pan head machine screw, Zinc plated steel [Dad's stock]				BDC	9226	https://www.boltdepot.com/Product-Details.aspx?product=9226	$0.01	$0.03	6/8/19
Fan	1	Each	120vac 80x80x25mm 21 cfm	5/26/20	Qualtek	FAA1-08025NBHW31	DKE	Q560-ND	https://www.digikey.com/products/en?keywords=Q560-ND	$14.17	$14.17	5/26/20		Remove fan filter; Mount Fan over Genasun (no washer on fan; nut 7/16” from end of screw, do NOT run fan leads behind bolt); Replace Power Supply cover; Replace fan filter; Bend LED out; Cut leads 6" beyond fan, shrink, strip and tin fan leads (pencil iron)	0.75
	1	Each	Fan guard, plastic with filter	5/26/20	Qualtek	09325-F/30	DKE	CR212-ND	https://www.digikey.com/products/en?keywords=CR212-ND	$1.56	$1.56	5/26/20
	4	Each	6-32x3" Phillips flat head machine screws, SS 18-8	6/12/19			BDC	1246	https://www.boltdepot.com/Product-Details.aspx?product=1246	$0.14	$0.57	6/8/19
	8	Each	#6 SAE flat washers, Zinc plated steel [old stock]				BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	$0.01	$0.10	6/8/19
	8	Each	#6 split lock washers, Zinc plated steel [old stock]				BDC	3022	https://www.boltdepot.com/Product-Details.aspx?product=3022	$0.01	$0.09	6/8/19
	12	Each	6-32 Hex machine screw nuts, Zinc plated steel [old stock]				BDC	2643	https://www.boltdepot.com/Product-Details.aspx?product=2643	$0.01	$0.17	6/8/19
	5.25	Inches	1/8" Shrink tubing (for leads)	5/30/15	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	$0.12	$0.64	6/8/19
Supply	36	Inches	#22 Stranded Red (Power Supply to Genasun Positive) [old stock, WP6-WP9 black, WP10 green]		CNC Tech	1569-22-1-0500-004-1-TS	DKE	CN531R-25-ND	https://www.digikey.com/products/en?keywords=CN531R-25-ND	$0.02	$0.81	6/8/19		Cut; Strip 22 guage so end can be doubled back; Tin (pencil iron); Wire Genasun to Power Supply (7 loops)	0.33
	3	Each	4" zip ties, Red (to hold #22 loops to Power Supply) [old stock]		Belden	DT-04-18-RE-C	DKE	BEL8885-ND	https://www.digikey.com/products/en/cables-wires-management/cable-ties-and-cable-lacing/482?k=&pkeyword=&pv37=1&FV=fffc0087%2C24200199%2Cffe001e2&quantity=0&ColumnSort=0&page=1&stock=1&pageSize=25	$0.03	$0.08	6/8/19
	4	Inches	#18 Stranded Black (Power Supply to Genasun Negative) [old stock]		CNC Tech	1569-18-1-0500-001-1-TS	DKE	CN548B-25-ND	https://www.digikey.com/products/en?keywords=CN548B-25-ND	$0.03	$0.13	6/8/19
Harness	48	Inches	#10 Stranded Black (Battery Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	$0.07	$3.18	6/8/19		Positive fuse butt splice; Inline splices, torch, 2x (Red/Blk); Ring connectors, 2x (Battery Red/Blk); Strip/tin, 2x (Load Red/Blk); Strip/tin/bend into S for zip tie to PS, 2x (Genasun Red/Blk); Labels, 4x (Battery/Load/Red/Blk); Install fuse and silver tape spare fuse; Install wire nuts on Load ends; Do not install harness yet	1.73
	48	Inches	#10 Stranded Red (Battery Positive)	5/26/20	Remington Industries	10STRREDGPT25	DKE	2328-10STRREDGPT25-ND	https://www.digikey.com/product-detail/en/10STRREDGPT25/2328-10STRREDGPT25-ND/11611780/?itemSeq=327489136	$0.06	$2.98	5/26/20
	45	Inches	#12 Stranded Black (Load Negative) [Scott's Bargain Barn]		General Cable/Carol Brand	76822.R8.01	DKE	C76822B-50-ND	https://www.digikey.com/products/en?keywords=C76822B-50-ND	$0.05	$2.08	6/8/19
	36	Inches	#12 Stranded Red (Load Positive) [3 pieces from Scott's Bargain Barn]	5/26/20	Remington Industries	12STRREDGPT25	DKE	2328-12STRREDGPT25-ND	https://www.digikey.com/product-detail/en/12STRREDGPT25/2328-12STRREDGPT25-ND/11612528/?itemSeq=327489099	$0.04	$1.55	5/26/20
	1	Each	#12 Inline ATM fuse holder [WalMart/Scott’s Bargain Barn, Eaton/Bussman, BP/HHM-RP‎]	6/1/20	OptiFuse	LPM-01B-12R	DKE	2298-LPM-01B-12R-ND	https://www.digikey.com/product-detail/en/LPM-01B-12R/2298-LPM-01B-12R-ND/11577603/?itemSeq=327490263	$2.18	$2.18	6/2/20	$3.90
	2	Inches	1/4” Shrink tubing (for inline fuse butt splice)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.16	$0.32	6/8/19
	2	Each	ATM fuses 20A (1 installed, 1 spare)	5/26/20	Eaton – Bussmann Electrical Division	BK/ATM-20	DKE	283-2330-ND	https://www.digikey.com/product-detail/en/BK%2FATM-20/283-2330-ND/264845/?itemSeq=327489614	$1.21	$2.42	5/26/20
	1	Inch	Silver tape (spare fuse) [Old stock from an HVAC supply house]		Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		$0.01	$0.01	8/1/18
	2	Each	4" zip ties, Red (to hold 2x inline splice together while wrapping/soldering) [old stock]		Belden	DT-04-18-RE-C	DKE	BEL8885-ND	https://www.digikey.com/products/en/cables-wires-management/cable-ties-and-cable-lacing/482?k=&pkeyword=&pv37=1&FV=fffc0087%2C24200199%2Cffe001e2&quantity=0&ColumnSort=0&page=1&stock=1&pageSize=25	$0.03	$0.05	6/8/19
	6	Inches	#22 Solid (stripped, for 2x inline splices) [old stock]		SparkFun Electronics	PRT-08023	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	$0.01	$0.05	6/8/19
	5	Inches	1/4" Shrink tubing (for 2x inline splices)	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.16	$0.79	6/8/19
	2	Each	Ring connectors #10 - 5/16" (Battery)	5/26/20	3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	$0.21	$0.42	5/26/20
	2.5	Inches	1/4" Shrink tubing (for 2x battery ring connectors) [3/8” used because 1/4” out of stock]	5/30/15	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	$0.16	$0.40	6/8/19
	2	Each	Wire nuts (protect Load ends from accidental short in installation) [Ideal #30-451J]				DKE			$0.10	$0.20	8/1/18
W100 Mount	2	Each	Top Fixing Bracket (alternative to Delta Electronics LM-01), 3/4"x1/2" Corner Brace, Zinc [SBB]	6/1/20	Hardware Essentials	H#853084	Ace Hardware	008236987720 (516606)		$0.69	$1.38	6/1/20	$4.01	Install Brackets (M4 screw, split washer, bracket, toothed washer, VERY TIGHT and straight, top right and lower left); Label and package Mounting Screws	0.43
	2	Each	Metric machine screw phillips pan head M4x0.7x6, SS 18-8	6/12/19			BDC	11876	https://www.boltdepot.com/Product-Details.aspx?product=11876	$0.05	$0.09	6/9/19
	2	Each	Split Washer M4 [#8 from stock]							$0.02	$0.04	Estimate
	2	Each	Toothed Washer M4 [#8 from stock]							$0.02	$0.04	Estimate
	1	Each	Small Plastic Bag for sheet metal screws [Leftover bags in stock]								$0.00
	2	Each	Sheet metal screw #8x1/2", hex washer head self drilling, SS 410 (for mounting W100 with brackets to a wall, sheet metal or wood) [#8x1/2" zinc from stock]				BDC	7154	https://www.boltdepot.com/Product-Details.aspx?product=7154	$0.08	$0.15	6/9/19
Misc	25	Grams	Acetone for cleaning flux from ALL soldered connections [old stock]							$0.01	$0.14	Estimate		Attach fan to L & N with power cord (very tight 4x repeat, zip tie); Attach harness (do NOT zip tie yet); Quick test, no load; Retighten AC connections to PS; Apply labels 7x; Print and apply SN label (see above); Quick DR test, zip ties on harness and start Burn-in under bench w/slated battery (see comment); Retighten screws on Genasun and PS; Ready for Delivery; Put away tools and extra stock; Clean bench and sweep	2.65
	41	Grams	"44" Rosin Core Solder .050" [4gm ~2004]	5/26/20	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	$0.09	$3.86	5/26/20
	5	Grams	Butane for torch [old stock]		Zippo Manufacturing Company	Ronson Multi-Fill Ultra Butane Fuel 2.75oz (78g)				$0.13	$0.65	Estimate
	1	Each	4" zip tie, Black (to hold fan wire leads to #6 riser bolt) [old stock, some white]		Belden	DT-04-18-0-C	DKE	BEL8887-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-0-C/BEL8887-ND/8599224	$0.03	$0.03	6/8/19
	2	Each	6" zip tie, White (to secure harness to power supply) [NAPA Auto Store 770-9204, https://www.napaonline.com/en/p/BK_7709204, $5.49/100, 8/1/18]	~2015	Qualtek	17-M150N-C	DKE	Q731-ND	https://www.digikey.com/product-detail/en/qualtek/17-M150N-C/Q731-ND/4072233	$0.03	$0.07	6/8/19

							W100:				$182.62		$13.21		9.98

Battery	1	Each	12 Volt 105 AH Flooded Deep Cycle, Wingnut Terminal (WNT) 5/16" (wingnuts included)	5/7/20	Trojan	27TMX	BFMS (Bill's Floor Machine Service), Kansas City MO	27TMX	B57-B61	$161.88	$161.88	6/10/20	$17.94	Order; Drive to BFMS; Summary and History sheets; Unload Subaru; Clean; Initial electrolyte and OCV checks; Inventory labels printed and applied; Water Me! Labels applied; Initial Charge on W100 (each battery individually, see Misc); Electrolyte levels corrected; Float until delivery (2 days minimum)	3.70

							Battery				$161.88		$17.94		3.70

							W100 and Battery				$344.49		$31.15		13.68

							W100, Battery, S&H Total					$375.64
							Sub Assemblies					9
							Parts					49

## WP11P
WISPers: WP11P	B				PARTS - BoM, Ordering & Inventory					Quantity:	1	WP11		W150_1

Part #	Units *	Quantity	Description *		Stock Quantities				Order Information					$.$$
			Specification	Substitute	Before	Ordered	Used	Remaining	Order Date	Pricing Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Web Link	Unit Cost	W150 / Subtotal	Production / Run / Subtotal	Tariff Tax S&H Miles	Production / Run / Total Cost
			Components
C1	Each	1	Battery Charger: 75 W			2	1	1	6/24/22	6/24/22	Mean Well	SCP-75-12	DKE	1866-4339-ND	BC9	32.35	32.35	32.35	13.27	45.62
	H	1	Charger: Blind mount
C2	Each	1	NTC Thermistor: 100KOHM 4190K BEAD		1	2	1	2	6/24/22	6/24/22	Vishay	NTCLE100E3104HB0	DKE	BC2520-ND	https://www.digikey.com/en/products/detail/vishay-beyschlag-draloric-bc-components/NTCLE100E3104HB0/773995?s=N4IgTCBcDaIEIGEwFYwAYC0A5AIiAugL5A	0.91	0.91	0.91	0.19	1.10
	W	1	BTS
C3	Each	1	Diode: 800V/80A, With Mounting Hardware			2	1	1	8/27/22	8/27/22	Vishay	VS-80PF80	DKE	VS-80PF80-ND	https://www.digikey.com/en/products/detail/vishay-general-semiconductor-diodes-division/vs-80pf80/4932266	6.60	6.60	6.60	1.37	7.97
	H	1	Diode
C4	Each	1	Diode Suppression Contactor: 30A/28VDC			1	1		8/27/22	8/27/22	Omron	MJN1Z-E-RP-AC120	MOU	653-MJN1Z-E-RP-AC120	https://www.mouser.com/ProductDetail/Omron-Automation-and-Safety/MJN1Z-E-RP-AC120?qs=CqvodWcFzOePCe%2FIlIpfnw%3D%3D	36.43	36.43	36.43	7.99	44.42
	H	1	Contactor
C5	Each	1	Load Supply: 13.5V 200W Switching Power Supply			1	1		8/27/22	8/27/22	Mean Well	RSP-200-13.5	DKE	1866-4241-ND	S17	54.39	54.39	54.39	11.06	65.45
	H	1	Load Supply: Blind Mount
C6	Each	1	ATM Fuse Holder: Inline, 30A, #12 AWG		3		1	2	10/12/21	11/6/22	NTE Electronics	74-IFHMAL30	DKE	2368-74-IFHMAL30-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-ifhmal30/11651173	3.55	3.55	3.55		3.55
	W	1	Battery Positive to RSP +V
C7	Each	2	ATM Fuse: 25A, White		21		2	19	10/12/21	11/6/22	NTE Electronics	74-MAF25A	DKE	2368-74-MAF25A-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-maf25a/11650963	0.23	0.45	0.45		0.45
	W	1	Battery Positive to RSP +V: Installed
	W	1	Battery Positive to RSP +V: Spare
C8	Each	1	DC to DC Converter: 150w, Wide Input 9-36vdc , Output 48-57.6vdc		1		1		11/17/21	11/17/21	Traco Power	TEP 150-2418WI	DKE	1951-1270-ND	V11	218.30	218.30	218.30		218.30
	H	1	Traco
C9	Each	1	Resistor: 1/4W metal film 15.0KΩ 1%	Kit from www.techam.com	7		1	6		10/15/22	Yageo	MFR-25FBF52-15K	DKE	15.0KXBK-ND	https://www.digikey.com/en/products/detail/yageo/MFR-25FBF52-15K/13252	0.06	0.06	0.06		0.06
	W	1	Traco Output Trim R: Resistor 1 of 2
C10	Each	1	Resistor: 1/4W metal film 180Ω 1%	220Ω; Kit from www.techam.com	10		1	9		10/16/22	Yageo	MFR-25FBF52-180R	DKE	MFR-25FBF52-180R-ND	https://www.digikey.com/en/products/detail/yageo/mfr-25fbf52-180r/9138058	0.06	0.06	0.06		0.06
	W	1	Traco Output Trim R: Resistor 2 of 2
C11	Each	1	Barrier Strip: Dual Row 4 Position			3	1	2	9/7/22	9/7/22	TE Connectivity	1546307-4	DKE	A112364-ND	https://www.digikey.com/en/products/detail/te-connectivity-amp-connectors/1546307-4/2283955?s=N4IgTCBcDaIIIEYFgMwDYAsBaAcgERAF0BfIA	3.23	3.23	3.23	6.99	10.22
	H	1	Barrier Strip
C12	Each	1	Power Cable Switch: DPST (ON/OFF) 7A/72VDC			4	1	3	6/27/22	6/27/22	Bulgin	S3950BA	DKE Waldom Electronics (WEC)	2266-S3950BA-ND	https://www.digikey.com/en/products/detail/bulgin/s3950ba/5058694	6.71	6.71	6.71	9.99	16.70
	PCS	1	Power Cable Switch Assembly
			Hardware
H1	Each	1	Backplate: Aluminum Sheet 10x14x0.090"	11.25x15.25"		1	1		9/12/22	9/12/22		3003-H14 (11.25x15.25")	MBTF	090ALSM + 0000CUT		12.53	12.53	12.53	51.17	63.70
	B	1	Paint
H2	Oz	1.6	Paint: High Heat		36.0		1.6	34.4		10/15/22	Rust-Oleum	7778 BAR-B-Q BLACK	Amazon.com	7778830	https://www.amazon.com/gp/product/B0010O0C94/ref=ox_sc_act_title_1?smid=ATVPDKIKX0DER&th=1	0.50	0.81	0.81		0.81
	B	1.6	Paint
H3	Each	5	1/2" High Threaded Stud Bumper	1/4-20x1/2-3/4" HH tap bolt, split washer, nut			5			Estimate					0.35	1.75	1.75		1.75
	H	5	Feet Installed
H4	Each	2	3x0.5x7mm Button Head Socket Screw	L=5mm used w/o Split Washer	83		2	81	8/11/17	10/16/22			BDC	18787	https://www.boltdepot.com/Product-Details.aspx?product=18787	$0.04	0.08	0.08		0.08
	H	2	Charger: Blind mount
H5	Each	0	3mm Split Washer	Not used			0					0.00	0.00	0.00		0.00
	H	0	Charger: Blind mount
H6	Each	11	#6-32x3/8" Button Head Socket Screw	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot			11			Estimate					0.03	0.33	0.33		0.33
	H	2	Contactor
	H	4	Traco
	H	2	Power Cable Switch Assembly
	H	3	Barrier Strip
H7	Each	1	#6-32x3/4" RH Screw: Slot Drive, Zinc plated steel		10		1	9		Estimate					0.02	0.02	0.02		0.02
	H	1	Barrier Strip: Power Cable shield ground point, lower left
H8	Each	5	#6 SAE Flat Washer: Zinc plated steel	Old stock	105		5	100		10/16/22			BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	0.02	0.08	0.08		0.08
	H	2	Contactor
	H	2	Power Cable Switch Assembly
	H	1	Barrier Strip: Power Cable shield ground point, lower left
H9	Each	9	#6 Split Washer		27		9	18		Estimate					0.02	0.15	0.15		0.15
	H	4	Traco
	H	2	Power Cable Switch Assembly
	H	3	Barrier Strip
H10	Each	4	4x0.7x6mm Button Head Socket Screw	Philips pan head, SS 18-8	82		4	78	6/12/19	10/16/22			BDC	11876	https://www.boltdepot.com/Product-Details.aspx?product=11876	0.06	0.25	0.25		0.25
	H	4	Load Supply: Blind Mount
H11	Each	4	4mm Split Washer	#8 Split Washer	44		4	40		Estimate					0.02	0.08	0.08		0.08
	H	4	Load Supply: Blind Mount
H12	Each	1	1/4" External Zig-zag Star Washer				1					0.00	0.00	0.00		0.00
	H	1	Diode
H13	Each	1	1/4" Flat Washer				1					0.00	0.00	0.00		0.00
	H	1	Diode
H14	Each	1	1/4"-28 Nut				1					0.00	0.00	0.00		0.00
	H	1	Diode
H15	Each	1	5/16"-18x1.25" Hex Head Tap Bolt	1", old stock, unknown grade			1			10/17/22			BDC	18314	https://www.boltdepot.com/Product-Details.aspx?product=18314	0.20	0.20	0.20		0.20
	H	1	FG Post					BDC
H16	Each	1	5/16" Split Washer: Zinc plated grade 8 yellow	Old stock, unknown grade			1			10/17/22			BDC	3038	https://www.boltdepot.com/Product-Details.aspx?product=3038	0.04	0.04	0.04		0.04
	H	1	FG Post					BDC
H17	Each	1	5/16" External Star Washer	Old stock, unknown grade			1			10/17/22			BDC	4081	https://www.boltdepot.com/Product-Details.aspx?product=4081	0.08	0.08	0.08		0.08
	H	1	FG Post					BDC
H18	Each	2	5/16"-18 Nut: SS 316	Old stock, unknown grade			2			10/17/22			BDC	15984	https://www.boltdepot.com/Product-Details.aspx?product=15984	0.11	0.21	0.21		0.21
	H	2	FG Post
H19	Inches	2	Aluminum Angle 1x2x0.125"	Scrap from RW solar panel mount			2			Estimate					0.52	1.03	1.03		1.03
	PCS	2	Power Cable Switch Assembly
			Wire
W1	Inches	41	#10 Stranded Black	Scott's Bargain Barn			41			11/6/22	General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	0.07	2.72	2.72	8.75	11.47
	W	36	Battery Negative to FG Post
	W	5	Contactor, Top Left NC Contact to FG Post
W2	Inches	36	#12 Stranded Red				36		5/26/20	11/6/22	Remington Industries	12STRREDGPT25	DKE	2328-12STRREDGPT25-ND	https://www.digikey.com/product-detail/en/12STRREDGPT25/2328-12STRREDGPT25-ND/11612528/?itemSeq=327489099	0.05	1.93	1.93		1.93
	W	28	Battery Positive to RSP +V
	W	8	RSP +V to Traco +Vin
W3	Inches	23.3	#12 Solid Brown	Old stock from building construction			23.3			11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	0.37	0.37		0.37
	W	6.0	Contactor, Top Right NC Contact to RSP -V
	W	8.5	Diode to RSP -V
	W	8.8	RSP -V to Traco -Vin
W4	Inches	6	#14 Solid Bare (insulation stripped)	Old stock from building construction (gray or blue)			6			11/7/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-14-Gauge-Gray-Solid-Copper-THHN-Wire-112-1460J/305306723	0.01	0.06	0.06		0.06
	W	6	Traco Inputs: +Vin and -Vin
W5	Each	1	AC Power Cord: NEMA, 15A 120VAC L/N/G, 6ft	Old stock, 5 ft			1			Estimate					3.00	3.00	3.00		3.00
	W	1	120 VAC Cord to SCP and FG Post
W6	Inches	14.5	#16 Stranded Black	Scott's Bargain Barn			14.5			11/7/22	CNC Tech	1569-16-1-0500-001-1-TS	DKE	CN642B-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-001-1-TS/9450423	0.03	0.46	0.46		0.46
	W	6.0	120 VAC Line from SCP to Contactor to RSP: Charger to Contactor (assembly)
	W	8.5	120 VAC Line from SCP to Contactor to RSP: Contactor to Load Supply (assembly)
W7	Inches	38.0	#16 Stranded White	Scott's Bargain Barn			38.0			11/7/22	CNC Tech	1569-16-1-0500-002-1-TS	DKE	CN643W-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-002-1-TS/9450424	0.03	1.21	1.21		1.21
	W	7.0	120 VAC Neutral from SCP to Contactor to RSP: Charger to Contactor (assembly)
	W	7.5	120 VAC Neutral from SCP to Contactor to RSP: Contactor to Load Supply (assembly)
	W	6.0	Traco -Vout to Barrier Strip
	W	8.0	Traco Outputs, Barrier Strip to Power Cable Switch (right side)
	W	9.5	Traco Outputs, Barrier Strip to Power Cable Switch (left side)
W8	Inches	23.5	#16 Stranded Red	Old stock			23.5			11/7/22	CNC Tech	1569-16-1-0500-004-1-TS	DKE	CN645R-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-004-1-TS/9450426	0.03	0.75	0.75		0.75
	W	6.0	Traco +Vout to Barrier Strip
	W	8.0	Traco Outputs, Barrier Strip to Power Cable Switch (right side)
	W	9.5	Traco Outputs, Barrier Strip to Power Cable Switch (left side)
W9	Inches	9	#22 Solid Bare (insulation stripped)	Old stock			9			11/7/22	SparkFun Electronics	PRT-08023 [Red]	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	0.01	0.08	0.08		0.08
	W	3	Battery Positive to RSP +V: Fuse holder
	W	3	RSP +V to Traco +Vin: "V"
	W	3	RSP -V to Traco -Vin: "V"
W10	Inches	41	#24 to #20 2-Conductor Stranded Zip/Rip Cord	Cannibalized from adapter bricks			41			Estimate					0.02	0.68	0.68		0.68
	W	41	BTS
			Miscellaneous
M1	Each	6	5/16" Ring Connector #10-12 AWG: Bare (No Insulation)				6	11	6/27/22	11/9/22	3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	0.20	1.19	1.19	3.50	4.69
	W	2	Battery Negative to FG Post
	W	1	Battery Positive to RSP +V
	W	1	Contactor, Top Left NC Contact to FG Post
	W	1	Charger B- to FG Post
	W	1	120 VAC Cord to SCP and FG Post: Gnd (green)
M2	Each	1	5/16" Ring Connector #? AWG: Bare	#4 AWG			1	3	12/29/20	12/29/20	TE Connectivity	33470	MOU	571-33470		0.54	0.54	0.54		0.54
	W	1	BTS: Sensor epoxied into connector
M3	Each	2	1/4" Female Spade Connector #10-12 AWG: Bare	Old stock: Calterm 61320			2	32		11/9/22	Molex	192030379	DKE	WM19887-ND	https://www.digikey.com/en/products/detail/molex/0192030379/3187492	0.09	0.19	0.19		0.19
	W	1	Contactor, Top Left NC Contact to FG Post
	W	1	Contactor, Top Right NC Contact to RSP -V
M4	Each	6	1/4" Female Spade Connector #14-16 AWG: Bare	Old stock: Calterm 61320 and Calterm 61180			6	38		11/9/22	Molex	192030390	DKE	WM19888-ND	https://www.digikey.com/en/products/detail/molex/0192030390/3187491	0.09	0.52	0.52		0.52
	W	1	120 VAC Line from SCP to Contactor to RSP
	W	1	120 VAC Neutral from SCP to Contactor to RSP
	W	2	Traco Outputs, Barrier Strip to Power Cable Switch (right side)
	W	2	Traco Outputs, Barrier Strip to Power Cable Switch (left side)
M5	Inches	3.5	1/8" Shrink Tubing				3.5	79.3	5/30/15	11/10/22	3M	EPS-200 1/8"BL 48"BX	DKE	EPS2018-ND	https://www.digikey.com/products/en?keywords=EPS2018-ND	0.19	0.68	0.68		0.68
	W	2.1	Charger B+ to RSP +V: Extra wires
	W	1.4	BTS: NTC
M6	Inches	5.0	3/16" Shrink Tubing				5.0	54.5	6/27/22	11/10/22	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-3-16-BL48-BX/260270	0.22	1.10	1.10	1.58	2.69
	W	0.7	Contactor, Top Right NC Contact to RSP -V
	W	1.4	Traco Outputs, Barrier Strip to Power Cable Switch (right side)
	W	1.4	Traco Outputs, Barrier Strip to Power Cable Switch (left side)
	W	1.5	BTS: NTC
M7	Inches	13.1	1/4” Shrink Tubing				13.1	17.5	6/27/22	11/10/22	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	0.26	3.42	3.42	0.94	4.36
	W	1.4	Battery Negative to FG Post: Ring connectors
	W	2.0	Battery Positive to RSP +V: Fuse holder butt splice
	W	0.7	Battery Positive to RSP +V: Ring connector
	W	1.4	Contactor, Top Left NC Contact to FG Post: Spade and ring connectors
	W	2.0	RSP +V to Traco +Vin: Butt splice
	W	2.0	RSP -V to Traco -Vin: Butt splice
	W	0.7	Charger B- to FG Post: Ring connector
	W	0.5	120 VAC Cord to SCP and FG Post: Ring connector, Gnd (green)
	W	0.7	120 VAC Line from SCP to Contactor to RSP: Spade connector
	W	0.7	120 VAC Neutral from SCP to Contactor to RSP: Spade connector
	W	1.0	Traco Output Trim R (estimated from memory, could find no records)
M8	Inches	4	1/2" Shrink Tubing				4	56	6/27/22	11/10/22	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-1-2-BL-48-BX/260262	0.34	1.37	1.37	1.23	2.60
	W	4	BTS: 2 layers over sensor ring connector
M9	Oz	0.45	Penatrox a-13 Electrical Joint Compound	PENA13-14, 4 fl. oz.			0.5	4.3		10/16/22	Burndy	PENA138	Amazon.com	PENETROX A-13, 8 fl. oz.	https://www.amazon.com/Burndy-A13-8-Oxide-Inhibiting-Compounds-Container/dp/B00CBKBZO2/ref=sr_1_1?gclid=Cj0KCQjw166aBhDEARIsAMEyZh7w66CXA1fkdfGT0na5LTNuqM_CwmKyOjJmdIP748Th28Dxvora2mkaAvNOEALw_wcB&hvadid=580957328063&hvdev=c&hvlocphy=9023208&hvnetw=g&hvqmt=b&hvrand=17878932423775935625&hvtargid=kwd-301888752915&hydadcr=3649_13538990&keywords=burndy+penetrox+a+13&qid=1665931056&qu=eyJxc2MiOiIxLjQ4IiwicXNhIjoiMC4wMCIsInFzcCI6IjAuMDAifQ%3D%3D&sr=8-1&ufe=app_do%3Aamzn1.fos.006c50ae-5d4c-4777-9bc0-4513d670b6bc	6.88	3.09	3.09		3.09
	H	0.10	Charger
	H	0.15	Load Supply
	H	0.05	FG Post
	H	0.05	Diode
	H	0.05	Traco
	W	0.05	120 VAC Cord to SCP and FG Post: (4) ring connectors tightened onto FG Post
M10	Oz	0.3	Epoxy: Resin and Hardener				0.3		8/9/22	8/9/22	Devcon	5 Minute Epoxy, 2 Bottles 8.50 Fl Oz total	Amazon.com			2.12	0.63	0.63	7.20	7.83
	PCS	0.1	Power Cable Switch Assembly: Switch epoxied on aluminum bracket
	W	0.2	BTS: Sensor epoxied into connector
M11	Grams	6	Butane for Blazer Micro Torch				6			Estimate	Zippo Manufacturing Company	Ronson Multi-Fill Ultra Butane Fuel 2.75oz (78g)				0.13	0.77	0.77		0.77
	W	2	Battery Positive to RSP +V: Butt splice (fuse holder)
	W	2	RSP +V to Traco +Vin: Butt splice
	W	2	RSP -V to Traco -Vin: Butt splice
M12	Grams	50	Solder: "44" Rosin Core .050"				50	313	5/26/20	11/10/22	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	0.13	6.71	6.71		6.71
	W	50	Wiring and Cabling: All solder/tin/torch operations
M13	Grams	25	Acetone for cleaning flux from ALL soldered connections				25			Estimate					0.01	0.14	0.14		0.14
	W	25	Wiring and Cabling: All solder/tin/torch operations
M14	Each	16	Zip Tie: 4", White	Red			16	3		11/10/22	Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	0.04	0.58	0.58		0.58
	W	14	Wiring and Cabling: Multiple operations
	L	2	Labels: Coil up AC input and battery cables, apply M14 zip ties
M15	Inches	1	Silver Tape	Old stock from an HVAC supply house			1			8/1/18	Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		0.01	0.01	0.01		0.01
	W	1	Battery Positive to RSP +V: Spare fuse
M16	Each	0.2	Weller D550 Soldering Gun Tip				0.2	1.8		11/15/22	Apex Tool Group	7250W	DKE	7250W-ND	https://www.digikey.com/en/products/detail/apex-tool-group/7250w/4524804	7.10	1.42	1.42		1.42
	W	0.2	Wiring and Cabling: Many solder/tin operations
			Labels
L1	Inches	5.0	0.35" White				5.0	157	8/12/15	11/11/22	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	0.05	0.23	0.23		0.23
	L	0.9	Print and Apply Labels: Leader (one for entire production run)
	L	2.3	Print and Apply Labels: W150 Barrier Strip 0.35.lbx
	L	1.8	Print and Apply Labels: W150 Do Not Overtighten 0.35.lbx (2)
L2	Inches	30.9	0.47" White				30.9	157	6/22/19	11/11/22	Brother	TZe-231	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_1?url=search-alias%3Daps&field-keywords=brother+tze+231&rh=i%3Aaps%2Ck%3Abrother+tze+231	0.04	1.33	1.33		1.33
	P	2.7	Orders Followup: Leaders (three .ods tracked items V, BC, S; one leader each for entire production run)
	P	9.9	Orders Followup: Inventory Sticker 0.47.lbx (three each for three .ods tracked items V, BC, S)
	L	0.9	Print and Apply Labels: Leader (one for entire production run)
	L	1.2	Print and Apply Labels: Traco (date) Output Set.lbx
	L	3.0	Print and Apply Labels: W150 Wire Label AC Plug 0.47.lbx
	L	5.8	Print and Apply Labels: W150 Output 0.47.lbx
	L	1.3	Print and Apply Labels: W150 Load Supply 0.47.lbx
	L	1.5	Print and Apply Labels: W150 FG Post 0.47.lbx
	L	4.6	Print and Apply Labels: W150 No User Serviceable Parts 0.47.lbx
L3	Inches	3.2	0.7" White				3.2	100	6/22/19	11/11/22	Brother	TZe-S241	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+tze+S241&rh=i%3Aaps%2Ck%3Abrother+tze+S241	0.05	0.15	0.15		0.15
	L	0.9	Print and Apply Labels: Leader (one for entire production run)
	L	2.3	Print and Apply Labels: W150 Tower Power Cable 0.7.lbx
L4	Inches	6.4	0.94" White				6.4	404	6/22/19	11/11/22	Brother	TZe-S251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	0.07	0.47	0.47		0.47
	L	0.9	Print and Apply Labels: Leader (one for entire production run)
	L	4.0	Print and Apply Labels: W150 SN Man'f 0.94.lbx (edited for each W150)
	L	1.5	Print and Apply Labels: W150 Battery Charger 0.94.lbx
L5	Inches	4.8	0.94" Yellow				4.8	361	6/22/19	11/11/22	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	0.07	0.35	0.35		0.35
	L	0.9	Print and Apply Labels: Leader (one for entire production run)
	L	3.9	Print and Apply Labels: W150 Caution! 120 VAC 0.94 Yellow.lbx (3)
			Accessories
		0	No Accessories yet

62	Ingredients (Unique Parts)					416.82	416.82	125.23	542.05
	128	Subcounts (Assembly Steps)

## WP11A
WISPers: WP11A	D				ASSEMBLY LABOR	Quantity:	1
						WP11	W150_1

Labor				Assembly Phase Descriptions and Notes
Date Started	Date Completed	Hours	Hours Each	Part Number(s)	Procedure Specification	Problems, Exceptions	Next Time, Improvements
Fr6/10/22	Sa9/17	10.3	10.3		Procurement [P]
Fr6/10	Mo9/12	0.5	0.5	All	Planning: Copy and link the PARTS and ASSEMBLY LABOR sheets from the previous run and plan the next run / Generally all comments are left in place until they no longer apply (they can be edited for this run's data) / PARTS: Set Quantity; Copy Stock Quantities (values and highlighting) from Remaining to Before; Clear values from Ordered / Clear values, formulas and highlighting from Remaining; Enter default formulas in Remaining (=Before+Ordered-Used) / Update list for design changes*; Clear bench to layout parts; Take inventory and update Stock Quantities > Before; Plan orders / ASSEMBLY LABOR: Set Quantity; Clear values from Date Started and Date Completed (including section headers) and unmerge cells / Clear values and formulas in Hours (excluding section headers) but do not unmerge cells; Update list for procedure changes* / Record data for any already completed work	No PARTS and ASSEMBLY LABOR sheets existed / Performed in several time consuming stages and steps over days and weeks / S&H expenses were high due to multiple orders from the same supplier and mileage to SBB and MBTF	Procurement should be performed all at once, working from these sheets / No mileage: All orders delivered here
Fr6/24	Mo9/12	6.6	6.6	C1-5 C11-12 H1 / M1 M6-8 M10 L2	Orders; Budget Management; Save important datasheets to LIB; Create summary and History sheets for tracked items
Tu6/28	Sa9/17	3.2	3.2		Orders Followup: Receiving; Resolve supplier errors; L2 inventory labels; Print and annotate invoices (scans for LIB, .ods updates, file)
Tu8/9	We8/10	3.8	3.8		Power Cable Switch Assembly [PCS]
Tu8/9	We8/10	3.8	3.8	C12 H19 M10	Fabricate aluminum brackets; Weigh Epoxy; Epoxy switch into bracket; Weigh Epoxy	Failed to weigh epoxy; Labels printed	Design change will eliminate the PCS Assembly
Tu9/27	Th9/29	11.0	11.0		Backplate Fabrication [B]
Tu9/27	We9/28	1.4	1.4	H1-2	Paint: Weigh paint; Set up on the porch, if air T is low paint in the sun, otherwise in the shade, backplate 50-90⁰F (monitor closely with Fluke IRT), avoid overheating from the sun; Shake can vigorously for several minutes; Remove plastic covering and paint immediately, spraying 12-16" from backplate; Two or three light coats separated by minutes; Clear nozzle; Weigh paint; Allow to dry 12 hours at 75⁰F before scribing	Backplate ordered too large and was cut down to size / Too much sun (paint hardened too quickly)	Order backplates sheared to 10x14" / Control temperature more carefully
Th9/29	Th9/29	9.6	9.6	H1	Scribe Hole Locations: On only one of the backplates for the run; Browne & Sharpe; Angle blocks; North bench; As per Cardboard Template / Scribe locations by halves / quadrants (right side, left side, bottom, top); Scribe lines should continue through all locations that are in line
			0		Gather and layout all tooling that will be needed to drill, mill, tap and deburr the holes [detailed list should go here, include clamp bolt sets]	No detailed list exists yet	Record tooling list
			0		Mill Holes: 10x14x3/4" plywood support with openings in the mounting hole areas on top and bottom center; The Clausing does not have enough travel to cover more than ~4.5" width for each set, so start with the left side / Stack all the backplates for the run (thickness limited by tap depth, but should be able to do five at once); Optimize alignment between the plates and check set with dial indicator on 14" side / Drill the two mounting holes first, insert and tighten temporary 1/4"-20 bolts to clamp the backplate stack together / Drill/mill all the holes for the left side; Reset for the right side (check set with dial indicator); Drill/mill all the holes for the right side
			0		Tap Holes: Clamped stack in Dad's vise (protect with paper); Tap from the top scribed backplate side; Remove temporary 1/4"-20 bolts
			0		Clean Up: Backplates individually clamped in Dad's vise (protect with paper); Countersink both sides of 1/4" zip tie holes; Clean backplates (isopropyl, paper towels); Clean up mill/garage areas (tools put away, sweep/vacuum)
Sa8/20	Fr9/30	3.1	3.1		Hardware Assembly [H]
Sa8/20	Fr9/30	3.1	3.1	H3-H18 / M9	Count out the small parts in tuna cans; Weigh Penatrox	PARTS sheet did not exist, done "on the fly" / Penatrox was not weighed	Pre-count will save time and identify errors / Pre-weigh the Penatrox
			0	H1 H3	Feet Installed	HH bolt substitute was time consuming	Order/use threaded stud bumpers
			0	C1 / H1 H4-5 / M9	Charger: Apply M9 Penatrox and mount with H4 screws and H5 split washers	Applied too much Penatrox / Substitute screws L=5mm too short / Split washer was not used	More conservative use of Penatrox / Order/use L=7mm screws and split washers
			0	C4 H1 H6 H8	Contactor: Mount with H6 screws and H8 flat washers	Various specs for mix of H6 screws	Order/use button head socket screws
			0	C5 H1 H10-11 / M9	Load Supply: Apply M9 Penatrox and mount with H10 screws and H11 split washers	Applied too much Penatrox / H8 substitute philips screws are hard to tighten	More conservative use of Penatrox / Order/use button head socket screws
			0	H1 H15-18 / M9	FG Post: Apply M9 Penatrox; H15 bolt and H16 split washer tightened onto backplate; H17 star washer and H18 nut tightened onto bolt / Additional H18 top nut left loose for assembly of (4) ring connectors	Did not apply Penatrox / H15 substitute bolt too short (1")	Apply Penatrox / Use 1.25 to 1.5" bolt
			0	C3 H1 H12-14 / M9	Diode: Apply M9 Penatrox on base and thread; 11/16" wrench, 28 lbf-in maximum (tighten by feel, not aggressive, do not overtighten) / Install H12-14 washers and nut (tighten by feel, not aggressive, do not overtighten but make sure star washer is firmly dug into aluminum)
			0	C8 H1 H6 H9 / M9	Traco: Apply M9 Penatrox and mount with H6 screws and H9 split washers	Applied too much Penatrox / Various specs for mix of H6 screws	More conservative use of Penatrox / Order/use button head socket screws
			0	C12 H1 H19 H6 H8-9	Power Cable Switch Assembly: Mount with H6 screws, H8 flat washer and H9 split washer	Various specs for mix of H6 screws	Design change will eliminate the PCS Assembly
			0	C11 H1 H6-9	Barrier Strip: Mount with (3) H6 screws and (3) H9 split washers; Power Cable Shield ground point (lower left) H7 screw and H8 flat washer	Various specs for mix of H6 screws	Order/use button head socket screws
			0	H3-H18	Put away remaining parts (label with quantities/dates)
Th8/18	Su10/2	15.1	15.1		Wiring and Cabling [W]
			0	W1-10 / M1-8 M10-14	Wire and shrink tubing stocks laid out on the bench; Cut all wire, cable and shrink as per PARTS sheet (W1-10, M5-8)* / Count out connectors M1-4 and zip ties M14 in tuna cans; Weigh Epoxy M10, Butane M11, Solder M12 and Acetone M13	PARTS sheet did not exist, done "on the fly" / Consumables not weighed	Improve length measuring tools* / Pre-counts will save time and identify errors* / Pre-weigh the consumables
Fr8/19	Fr9/30	1.3	1.3	W1 / M1 M7 M14	Battery Negative to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink; Repeat for other end / Attach to FG Post (leave top nut loose); M14 zip tie	Acetone was not used	Use acetone to clean solder flux
		1.3	1.3	C5-7 / W2 W9 / M1 M7 M15	Battery Positive to RSP +V: W2 and C6 fuse holder strip/twist 1.0"; W9 butt splice wrap/torch/clean; M7 shrink / C6 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink / Install C7 fuse; Attach C7 spare fuse with M15 silver tape; W2 strip/twist/tin 1.0" (voltmeter clip lead test point); Attach to C5	Acetone was not used	Use acetone to clean solder flux
Sa10/1	Sa10/1	5.4	5.4	C4 W1 / M1 M3 M7	Contactor, Top Left NC Contact to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink / W1 strip/twist 0.4"; M3 spade crimp/solder/clean; M7 shrink; Attach to C4 and FG post (leave top nut loose)	Acetone was not used	Spade connector might use M6 shrink / Use acetone to clean solder flux
			0	C4-5 W3 M3 M6	Contactor, Top Right NC Contact to RSP -V: W3 strip 0.4"; M3 spade crimp/solder/clean; M6 shrink; W3 strip 0.4"; Attach to C4 and C5	Acetone was not used	Use acetone to clean solder flux
			0	C3 C5 W3	Diode to RSP -V: W3 strip 0.4" (for C5) and 0.6" (for C3); Attach to C5; Solder to C3 anode (quick, not too hot); Clean	Acetone was not used	Use acetone to clean solder flux
			0	W4	Traco Inputs: W4 strip all (2x); W4 bent into "V" shape (2x)
			0	C5 C8 / W2 W4 W9 M7	RSP +V to Traco +Vin: W2 strip/twist 1.0"; W4 W2 W9 butt splice wrap/torch/clean; M7 shrink / W2 strip/tin 0.4"; Attach to C8 and C5 (Extech test loop)	Acetone was not used	Use acetone to clean solder flux
			0	C5 C8 W3 W4 W9 M7	RSP -V to Traco -Vin: W3 strip 1.0"; W4 W3 W9 butt splice wrap/torch/clean; M7 shrink; W3 strip 0.4"; Attach to C8 and C5	Acetone was not used	Use acetone to clean solder flux
			0	C1 M1 M7	Charger B- to FG Post: Cut C1 B- wire (black) 3" from PCB; C1 B- strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink / Attach to FG Post (leave top nut loose)	Acetone was not used	Use acetone to clean solder flux
			0	C1 C5 / M5 M14	Charger B+ to RSP +V: Cut C1 B+ wire (red) ???" from PCB*; C1 B+ strip/twist/tin 0.4"; Attach to C5 (Extech test loop) / M5* shrink on extra wires from C1 (blk, org, yel); M14 zip tie extras to C1 charger grill; M14 zip ties between C1 and C5	Acetone was not used / Did not record lengths and size data*	Use acetone to clean solder flux / Get the length and size data
			0	C1 / W5 / M1 M7 M9	120 VAC Cord to SCP and FG Post: W5 cut 6', strip outer jacket 1.5"; W5 L/N strip/twist/tin 0.3" / W5 Gnd (green) strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink / M9 Penatrox on (4) ring connectors (Battery Negative, Contactor, Charger B- and AC Gnd) and tighten FG Post very tight / Loosely attach W5 L/N to C1	Acetone was not used / Penatrox was not used	Use acetone to clean solder flux / Apply Penatrox on FG Post ring connectors
			0	C1 C4-5 W6 / M4 M7	120 VAC Line from SCP to Contactor to RSP: W6x2 strip/twist 0.4"; W6x2 M4 spade crimp/solder/clean; M7 shrink / W6x2 strip/tin 0.3"; Attach to C4 lower left, C1 and C5 Line	Acetone was not used	Spade connector might use M6 shrink / Use acetone to clean solder flux
			0	C1 C4-5 W7 / M4 M7 M14	120 VAC Neutral from SCP to Contactor to RSP: W7x2 strip/twist 0.4"; W7x2 M4 spade crimp/solder/clean; M7 shrink / W7x2 strip/tin 0.3"; Attach to C4 lower right, C1 and C5 Neutral; M14 zip ties	Acetone was not used	Spade connector might use M6 shrink / Use acetone to clean solder flux
Sa8/20	Su10/2	3.3	3.3	C8 C11 W7	Traco -Vout to Barrier Strip: W7 strip/twist/tin/clean 0.3" (both ends); Attach to C8 and C11	Acetone was not used	Use acetone to clean solder flux
			0	C8 C11 W8 M14	Traco +Vout to Barrier Strip: W8 strip/twist/tin/clean 0.3" (both ends); Attach to C8 and C11 (Extech test loop); M14 zip tie	Acetone was not used	Use acetone to clean solder flux
			0	C11-12 W7-W8 / M4 M6	Traco Outputs, Barrier Strip to Power Cable Switch (right side): W7 and W8 strip/twist 0.4"; W7 and W8 M4 spade crimp/solder/clean / M6x2 shrink; W7 and W8 strip/twist/tin/clean 0.3"; Attach both wires to C11 and C12 (observe polarity)	Acetone was not used	Design change will eliminate the PCS Assembly / Use acetone to clean solder flux
			0	C11-12 W7-W8 / M4 M6 M14	Traco Outputs, Barrier Strip to Power Cable Switch (left side): W7 and W8 strip/twist 0.4"; W7 and W8 M4 spade crimp/solder/clean / M6x2 shrink; W7 and W8 strip/twist/tin/clean 0.3"; Attach both wires to C11 and C12 (observe polarity); M14 zip ties	Acetone was not used	Design change will eliminate the PCS Assembly / Use acetone to clean solder flux
			0	C8-10 / M7	Traco Output Trim R: C9/C10 twisted together, solder/clean; Cut C9/C10 assembly to <=1.5"*; M7* shrink; Install on C8	Trim R was assembled and installed in [T48S] and there are no detailed records / Acetone was not used	Assemble and install Trim R at this step / Record detailed assembly data / Use acetone to clean solder flux
Th8/18	Fr9/30	3.4	3.4	C1-2 / W10 / M2 M5-6 M8 / M10 M14	BTS: Assemble sensor to zip wire, epoxy into battery post connector and solder zip wire to charger CN2 connector pins: / Assemble C2 NTC sensor to W10 zip wire with layers of shrink: / W10 split 1.5"*1 strip/tin 0.3"*1 and preload with M5*1 shrink; C2 NTC cut ?.?"*1; W10 C2 dual butt solder/clean/shrink; Add M6 shrink / M10 epoxy C2 sensor assembly into M2 ring with double layer of M8 shrink / Solder BTS assembly to CN2 connector pins: C1 heat and remove CN2 connector plastic shell; W10 split 0.7"*2 strip/tin 0.5"*2 / W10 bend small loops and crimp to CN2 connector pins; Tack solder/clean; M14 strain relief zip tie on C1 grill; M14 zip ties*3	BTS was not entirely assembled in this phase / Did not record lengths and size data / Acetone was not used / Short cable: 17.5" from bottom of W150	Fabricate entire BTS assembly in this step / Get the length and size data / Use acetone to clean solder flux
Su10/2	Su10/2	0.4	0.4	H5 M9-11 M13-14	PARTS Sheet: Update zip tie count; Weigh Penatrox, Butane, Solder, Acetone and Epoxy and update consumption / Tighten all screws; Wire stocks returned to W side; Clean up the bench	PARTS sheet did not exist, done "on the fly" / Consumables not weighed	Weigh the consumables
Fr8/19	Fr10/7	1.7	1.7		Configuration and Testing
Su10/2	Su10/2	0.0	0		Bench Setup: Each W150 is configured and tested individually; No battery is required; W150 next to Engel; Set Z19 for target 25.0⁰C / BTS and Z19 T2 bolted together in metal pipe with bubble wrap to keep air out of the pipe in center of Engel enclosure / ITECH and Fluke turned on (keep shop ambient stable throughout configuration and testing); ITECH Von Living 5.0v	27TMX battery was used (other tests)	No battery
Fr8/19	Fr8/19	1.7	1.7	C1	Charger Configuration: ITECH on end of battery cables; W150 AC power applied (T1 UPS) / Verify that contactor opens and that three supplies are up (green LEDs, Fluke on Load Supply and Traco output) / ITECH CC 100mA; Stabilize Engel/BTS at 25.0⁰C; Adjust charger for target 13.500vI (record achieved value)	Charger was not configured when on W150	Configure at this step
Su10/2	Mo10/3	0.0	0	C1	Charger Burn-In: [ITECH remains on end of battery cables]; 100wIS* for >=12 hours / ITECH load OFF and disconnected (protect battery cable ends from accidental short)	Charger burn-in was done with dead battery	Burn-in with ITECH at this step
Su10/2	Tu10/4	0.0	0	C5	Load Supply Configuration: ITECH with Sense on RSP +V and Diode anode*; No load (except Traco idle) / Wait for W150 stabilization at bench ambient (cool-down from burn-in); Adjust Load Supply for target 13.700vI (record achieved value)	Supply was configured using Fluke	Configure using ITECH at this step
Su10/2	Mo10/3	0.0	0	C5 C8	Load Supply and Traco Burn-In: ITECH with Sense on Traco output at Barrier Strip; 0wIS, record Traco output vI; 180wIS for >=12 hours / ITECH load OFF and disconnected; W150 AC power disconnected; BTS removed from Engel / (Go to Bench/BTS Setup for next W150 in Production Run)	Burn-In was 175w during other testing	Burn-In at 180w and without Charger at max power
Th10/6	Th10/6	0.0	0		After all the W150s are Configured and Tested: Engel/Dinico/ITECH/Fluke OFF and Status=Available
Fr10/7	Fr10/7	2.5	2.5		Labels [L]
Fr10/7	Fr10/7	0.0	0		Tighten ALL Screws
Fr10/7	Fr10/7	2.5	2.5	L1-5	Print and Apply Labels: See PARTS for LBX files (filenames indicate locations on W150); Save on leader tape length and win a prize
Fr10/7	Fr10/7		0	M14	Coil up AC Input and Battery Cables: M14 zip ties
We6/15	Sa11/19/22	0	0		Completion
Tu6/28	Fr10/21		0		Photos
We6/15	Sa11/19		0	C1 C5 C8	WISPer, tracked equipment and Location .ods records completed
Fr10/14	Sa11/19/22		0		PARTS and ASSEMBLY LABOR sheets completed
Fr6/10/22	Sa11/19/22	47.5	47.5		Entire Assembly Procedure Completed

## WP12-13P
WISPers: WP12-13P	B				PARTS - BoM, Ordering & Inventory					Quantity:	2	WP12 ... WP13		W150_2 ... W150_3

Part #	Units *	Quantity	Description *		Stock Quantities				Order Information					$.$$
			Specification	Substitute	Before	Ordered	Used	Remaining	Order Date	Pricing Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Web Link	Unit Cost	W150 / Subtotal	Production / Run / Subtotal	Tariff Tax S&H Miles	Production / Run / Total Cost
			Components
C1	Each	1	Battery Charger: 75 W		1	1	2		11/25/22	11/25/22	Mean Well	SCP-75-12	MOU	709-SCP75-12	BC10-11	33.58	33.58	67.16	2.80	69.96
	H	1	Charger: Blind mount
C2	Each	1	NTC Thermistor: 100KOHM 4190K BEAD		2		2		6/24/22	6/24/22	Vishay	NTCLE100E3104HB0	DKE	BC2520-ND	https://www.digikey.com/en/products/detail/vishay-beyschlag-draloric-bc-components/NTCLE100E3104HB0/773995?s=N4IgTCBcDaIEIGEwFYwAYC0A5AIiAugL5A	0.91	0.91	1.82		1.82
	W	1	BTS
C3	Each	1	Diode: 800V/80A, With Mounting Hardware		1	1	2		11/25/22	11/25/22	Vishay	VS-80PF80	DKE	VS-80PF80-ND	https://www.digikey.com/en/products/detail/vishay-general-semiconductor-diodes-division/vs-80pf80/4932266	6.60	6.60	13.20	0.23	13.43
	H	1	Diode
C4	Each	1	Diode Suppression Contactor: 30A/28VDC			2	2		11/25/22	11/25/22	Omron	MJN1Z-E-RP-AC120	MOU	653-MJN1Z-E-RP-AC120	https://www.mouser.com/ProductDetail/Omron-Automation-and-Safety/MJN1Z-E-RP-AC120?qs=CqvodWcFzOePCe%2FIlIpfnw%3D%3D	36.43	36.43	72.86	6.09	78.95
	H	1	Contactor
C5	Each	1	Load Supply: 13.5V 200W Switching Power Supply			2	2		11/25/22	11/25/22	Mean Well	RSP-200-13.5	DKE	1866-4241-ND	S18-19	54.39	54.39	108.78	14.71	123.49
	H	1	Load Supply: Blind Mount
C6	Each	1	ATM Fuse Holder: Inline, 30A, #12 AWG			12	2	10	11/25/22	11/25/22	NTE Electronics	74-IFHMAL30	DKE NTE	2368-74-IFHMAL30-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-ifhmal30/11651173	3.55	3.55	7.10	9.60	16.70
	W	1	Battery Positive to RSP +V
C7	Each	2	ATM Fuse: 30A, Green			25	4	21	11/25/22	11/25/22	NTE Electronics	74-MAF30A	DKE NTE	2368-74-MAF30A-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-maf30a/11653142	0.23	0.45	0.90	1.34	2.24
	W	1	Battery Positive to RSP +V: Installed
	W	1	Battery Positive to RSP +V: Spare
C8	Each	1	DC to DC Converter: 150w, Wide Input 9-36vdc , Output 48-57.6vdc			5	2	3	10/14/22	10/14/22	Traco Power	TEP 150-2418WI	SPSE	TEP 150-2418WI	V12-16	220.35	220.35	440.70	14.79	455.49
	H	1	Traco
C9	Each	1	Resistor: 1/4W Metal Film 15.0KΩ 1%	Kit from www.techam.com	6		2	3		10/15/22	Yageo	MFR-25FBF52-15K	DKE	15.0KXBK-ND	https://www.digikey.com/en/products/detail/yageo/MFR-25FBF52-15K/13252	0.06	0.06	0.11		0.11
	W	1	Traco Output Trim R: Resistor 1 of 2
C10	Each	1	Resistor: 1/4W Metal Film 180Ω 1%	WP12 used 150Ω; Not used for WP13 (solitary C9)	9		2	7		1/9/23	Yageo	MFR-25FBF52-180R	DKE	MFR-25FBF52-180R-ND	https://www.digikey.com/en/products/detail/yageo/mfr-25fbf52-180r/9138058	0.06	0.06	0.11		0.11
	W	1	Traco Output Trim R: Resistor 2 of 2
C11	Each	1	Barrier Strip: Dual Row 4 Position		2		2		9/7/22	9/7/22	TE Connectivity	1546307-4	DKE	A112364-ND	https://www.digikey.com/en/products/detail/te-connectivity-amp-connectors/1546307-4/2283955?s=N4IgTCBcDaIIIEYFgMwDYAsBaAcgERAF0BfIA	3.23	3.23	6.46		6.46
	H	1	Barrier Strip
C12	Each	1	Power Cable Switch: SPST (ON/OFF) 7A/72VDC	DPDT	3		2	1	6/27/22	6/27/22	Bulgin	S3950BA	DKE Waldom Electronics (WEC)	2266-S3950BA-ND	https://www.digikey.com/en/products/detail/bulgin/s3950ba/5058694	6.71	6.71	13.42		13.42
	PCS	1	Power Cable Switch Assembly
			Hardware
H1	Each	1	Backplate: Aluminum Sheet 10x14x0.090"			2	2		10/20/22	10/22/22		3003-H14 (10x14")	MBTF	090ALSM + 0000CUT		10.42	10.42	20.84	28.67	49.51
	B	1	Paint
H2	Oz	1.1	Paint: High Heat		34.4		2.2	32.2		10/15/22	Rust-Oleum	7778 BAR-B-Q BLACK	Amazon.com	7778830	https://www.amazon.com/gp/product/B0010O0C94/ref=ox_sc_act_title_1?smid=ATVPDKIKX0DER&th=1	0.50	0.55	1.11		1.11
	B	1.1	Paint
H3	Each	5	Bumper Foot: 1/2" High, Nylon, Screw Mount, Cylindrical, Recessed Center, 5/8" OD			10	10		11/25/22	11/25/22	Essentra Components	BRR025A	DKE	RPC5642-ND	https://www.digikey.com/en/products/detail/essentra-components/BRR025A/9343103	0.22	1.08	2.15	0.08	2.23
	H	5	Feet Installed
H4	Each	2	3x0.5x6mm Star Drive Pan Head Screw: T10 Torx, SS 18-8 (A-2)	L=5mm used w/o Split Washer		100	4	96	11/25/22	11/25/22			BDC	19243	https://www.boltdepot.com/Product-Details.aspx?product=19243	0.06	0.11	0.22	1.49	1.71
	H	2	Charger: Blind mount
H5	Each	2	3mm Split Washer: SS 18-8 (A-2)	#6 Split Washer		100	4	96	11/25/22	11/25/22			BDC	4810	https://www.boltdepot.com/Product-Details.aspx?product=4810	0.02	0.03	0.06	0.41	0.48
	H	2	Charger: Blind mount
H6	Each	11	#6-32x3/8" Star Drive Pan Head Screw: T15 Torx, SS 18-8 (A-2)	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		100	22	78	11/25/22	11/25/22			BDC	19124	https://www.boltdepot.com/Product-Details.aspx?product=19124	0.12	1.30	2.60	3.20	5.81
	H	2	Contactor
	H	4	Traco
	H	2	Power Cable Switch Assembly
	H	3	Barrier Strip
H7	Each	1	#6-32x3/4" RH Screw: Slot Drive, Zinc plated steel		9		2	7		11/23/22			BDC	1712	https://www.boltdepot.com/Product-Details.aspx?product=1712	0.02	0.02	0.05		0.05
	H	1	Barrier Strip: Power Cable shield ground point, lower left
H8	Each	5	#6 SAE Flat Washer: Zinc plated steel	Old stock	100		10	90		11/24/22			BDC	2973	https://www.boltdepot.com/Product-Details.aspx?product=2973	0.02	0.08	0.17		0.17
	H	2	Contactor
	H	2	Power Cable Switch Assembly
	H	1	Barrier Strip: Power Cable shield ground point, lower left
H9	Each	6	#6 Split Washer: SS 18-8	Old stock, probably not SS 18-8		100	12	90	11/25/22	11/25/22			BDC	2953	https://www.boltdepot.com/Product-Details.aspx?product=2953	0.02	0.15	0.30	0.67	0.96
	H	4	Traco
	H	2	Power Cable Switch Assembly
H10	Each	4	4x0.7x6mm Star Drive Pan Head Screw: T20 Torx, SS 18-8 (A-2)	Philips pan head		100	8	92	11/25/22	11/25/22			BDC	19246	https://www.boltdepot.com/Product-Details.aspx?product=19246	0.07	0.28	0.56	1.89	2.45
	H	4	Load Supply: Blind Mount
H11	Each	4	4mm Split Washer: SS 18-8 (A-2)	Old stock #8 Split Washer		100	8	92	11/25/22	11/25/22			BDC	4811	https://www.boltdepot.com/Product-Details.aspx?product=4811	0.02	0.06	0.13	0.44	0.56
	H	4	Load Supply: Blind Mount
H12	Each	5	#8-32x1/2" Star Drive Pan Head Screw: T20 Torx	3/8" as ordered		100	10	90	11/25/22	11/25/22			BDC	19134	https://www.boltdepot.com/Product-Details.aspx?product=19134	0.14	0.71	1.43	3.86	5.29
	H	5	Feet Installed
H13	Each	1	5/16"-18x1.25" Hex Head Tap Bolt	1.25", old stock, unknown grade	9		2	7		11/24/22			BDC	18314	https://www.boltdepot.com/Product-Details.aspx?product=18314	0.20	0.20	0.41		0.41
	H	1	FG Post
H14	Each	1	5/16" Split Washer: Zinc plated grade 8 yellow	Old stock, unknown grade			2			11/24/22			BDC	3038	https://www.boltdepot.com/Product-Details.aspx?product=3038	0.04	0.04	0.07		0.07
	H	1	FG Post
H15	Each	1	5/16" Internal Star Washer: SS 410	Old stock, unknown grade			2			12/5/22			BDC	4093	https://www.boltdepot.com/Product-Details.aspx?product=4093	0.07	0.07	0.15		0.15
	H	1	FG Post
H16	Each	2	5/16"-18 Nut: SS 316	Old stock, unknown grade			4			11/24/22			BDC	15984	https://www.boltdepot.com/Product-Details.aspx?product=15984	0.11	0.21	0.43		0.43
	H	2	FG Post
H17	Each	1	5/16" Flat Washer: SS 316	Old stock, unknown grade			2			Estimate			BDC			0.05	0.05	0.10		0.10
	W	1	120 VAC Cord to SCP and FG Post
H18	Inches	2	Aluminum Angle 1x2x0.125"	Scrap from RW solar panel mount			4			Estimate					0.52	1.03	2.06		2.06
	PCS	2	Power Cable Switch Assembly
			Wire
W1	Inches	42	#10 Stranded Black	Scott's Bargain Barn			83	151		11/6/22	General Cable/Carol Brand	76832.18.01	DKE	C76832B-50-ND	https://www.digikey.com/products/en?keywords=C76832B-50-ND	0.07	2.75	5.50		5.50
	W	36.5	Battery Negative to FG Post
	W	5	Contactor, Top Left NC Contact to FG Post
W2	Inches	36	#12 Stranded Red				73	59	5/26/20	11/6/22	Remington Industries	12STRREDGPT25	DKE	2328-12STRREDGPT25-ND	https://www.digikey.com/product-detail/en/12STRREDGPT25/2328-12STRREDGPT25-ND/11612528/?itemSeq=327489099	0.05	1.95	3.90		3.90
	W	28.3	Battery Positive to RSP +V
	W	8	RSP +V to Traco +Vin
W3	Inches	22.8	#12 Solid Brown	Old stock from building construction			45.6	297		11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	0.36	0.71		0.71
	W	6.0	Contactor, Top Right NC Contact to RSP -V
	W	8.0	Diode to RSP -V
	W	8.8	RSP -V to Traco -Vin
W4	Inches	6	#14 Solid Bare	Old stock from building construction (gray or blue)			12			11/7/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-14-Gauge-Gray-Solid-Copper-THHN-Wire-112-1460J/305306723	0.01	0.06	0.12		0.12
	W	3	RSP +V to Traco +Vin
	W	3	RSP -V to Traco -Vin
W5	Each	1	AC Power Cord: NEMA, 15A 120VAC L/N/G, 6ft	Old stock, 5.8 ft			2			Estimate					3.00	3.00	6.00		6.00
	W	1	120 VAC Cord to SCP and FG Post
W6	Inches	14.5	#16 Stranded Black	Scott's Bargain Barn			29.0			11/7/22	CNC Tech	1569-16-1-0500-001-1-TS	DKE	CN642B-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-001-1-TS/9450423	0.03	0.46	0.92		0.92
	W	6.0	120 VAC Line from SCP to Contactor to RSP: Charger to Contactor (assembly)
	W	8.5	120 VAC Line from SCP to Contactor to RSP: Contactor to Load Supply (assembly)
W7	Inches	22.5	#16 Stranded White	Scott's Bargain Barn			45.0			11/7/22	CNC Tech	1569-16-1-0500-002-1-TS	DKE	CN643W-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-002-1-TS/9450424	0.03	0.71	1.43		1.43
	W	7.0	120 VAC Neutral from SCP to Contactor to RSP: Charger to Contactor (assembly)
	W	7.0	120 VAC Neutral from SCP to Contactor to RSP: Contactor to Load Supply (assembly)
	W	6.0	Traco -Vout to Barrier Strip
	W	2.5	Traco Outputs, Barrier Strip to Barrier Strip (Jumper)
W8	Inches	23.5	#16 Stranded Red	Old stock		300	47.0	253	11/25/22	11/25/22	Remington Industries	16UL1015STRRED25	DKE Remington	2328-16UL1015STRRED25-ND	https://www.digikey.com/en/products/detail/remington-industries/16UL1015STRRED25/11613256	0.05	1.06	2.13	0.00	2.13
	W	6.0	Traco +Vout to Barrier Strip
	W	8.0	Traco Outputs, Barrier Strip to Power Cable Switch (right side top)
	W	9.5	Traco Outputs, Power Cable Switch (left side top) to Barrier Strip
W9	Inches	9	#22 Solid Bare	Old stock, insulation stripped			18			11/7/22	SparkFun Electronics	PRT-08023 [Red]	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	0.01	0.08	0.17		0.17
	W	3	Battery Positive to RSP +V: Fuse holder
	W	3	RSP +V to Traco +Vin: "V"
	W	3	RSP -V to Traco -Vin: "V"
W10	Inches	41	#24 to #20 2-Conductor Stranded Zip/Rip Cord	Cannibalized from adapter bricks			82			Estimate					0.02	0.68	1.37		1.37
	W	41	BTS
			Miscellaneous
M1	Each	4	5/16" Ring Connector #10-12 AWG: Bare (No Insulation)		11	100	8	101	11/25/22	11/25/22	3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	0.18	0.70	1.41	0.62	2.02
	W	2	Battery Negative to FG Post
	W	1	Battery Positive to RSP +V
	W	1	Contactor, Top Left NC Contact to FG Post
M2	Each	2	5/16" Ring Connector #14-16 AWG: Bare	SBB blue insulation*			4	3	1/20/21	Estimate					0.10	0.20	0.40		0.40
	W	1	Charger B- to FG Post	#10-#12*
	W	1	120 VAC Cord to SCP and FG Post: Gnd (green)	SBB blue insulation
M3	Each	1	5/16" Ring Connector #4 AWG: Bare (No Insulation)		3		2	1	12/29/20	12/29/20	TE Connectivity	33470	MOU	571-33470		0.54	0.54	1.09		1.09
	W	1	BTS: Sensor epoxied into connector
M4	Each	2	1/4" Female Spade Connector #10-12 AWG: Bare	Old stock: Calterm 61320	32		4	30		11/9/22	Molex	192030379	DKE	WM19887-ND	https://www.digikey.com/en/products/detail/molex/0192030379/3187492	0.09	0.19	0.38		0.38
	W	1	Contactor, Top Left NC Contact to FG Post
	W	1	Contactor, Top Right NC Contact to RSP -V
M5	Each	4	1/4" Female Spade Connector #14-16 AWG: Bare	Old stock: Calterm 61180	36		8	28		11/9/22	Molex	192030390	DKE	WM19888-ND	https://www.digikey.com/en/products/detail/molex/0192030390/3187491	0.09	0.35	0.70		0.70
	W	1	120 VAC Line from SCP to Contactor to RSP: Assembly
	W	1	120 VAC Neutral from SCP to Contactor to RSP: Assembly
	W	1	Traco Outputs, Barrier Strip to Power Cable Switch (right side top)
	W	1	Traco Outputs, Power Cable Switch (left side top) to Barrier Strip
M6	Inches	3.5	3/32" Shrink Tubing	Old stock, not EPS-200			7.0	35	Unknown	Estimate					0.19	0.68	1.35		1.35
	W	2.1	Charger B+ to RSP +V: Extra wires
	W	1.4	BTS: NTC
M7	Inches	5.8	3/16" Shrink Tubing		54.5		11.6	45.3	6/27/22	11/10/22	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-3-16-BL48-BX/260270	0.22	1.28	2.56		2.56
	W	0.6	Contactor, Top Right NC Contact to RSP -V
	W	0.7	Charger B- to FG Post: Ring connector
	W	0.6	120 VAC Cord to SCP and FG Post: Ring connector, Gnd (green)
	W	0.7	Traco Outputs, Barrier Strip to Power Cable Switch (right side top)
	W	0.7	Traco Outputs, Power Cable Switch (left side top) to Barrier Strip
	W	1.5	BTS: NTC
	W	1.0	Traco Output Trim R
M8	Inches	11.0	1/4” Shrink Tubing		17.5	240	22.0	239	11/25/22	11/25/22	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	0.25	2.74	5.48	2.11	7.59
	W	1.6	Battery Negative to FG Post: Ring connectors
	W	2.0	Battery Positive to RSP +V: Fuse holder butt splice
	W	0.8	Battery Positive to RSP +V: Ring connector
	W	1.6	Contactor, Top Left NC Contact to FG Post: Spade and ring connectors
	W	1.8	RSP +V to Traco +Vin: Butt splice
	W	1.8	RSP -V to Traco -Vin: Butt splice
	W	0.7	120 VAC Line from SCP to Contactor to RSP: Spade connector
	W	0.7	120 VAC Neutral from SCP to Contactor to RSP: Spade connector
M9	Inches	3	1/2" Shrink Tubing		56		6	48	6/27/22	11/10/22	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-1-2-BL-48-BX/260262	0.34	1.03	2.05		2.05
	W	3	BTS: 2 layers over sensor ring connector
M10	Oz	0.1	Penatrox a-13 Electrical Joint Compound	PENA13-14, 4 fl. oz.	4.3		0.2	4.0		10/16/22	Burndy	PENA138	Amazon.com	PENETROX A-13, 8 fl. oz.	https://www.amazon.com/Burndy-A13-8-Oxide-Inhibiting-Compounds-Container/dp/B00CBKBZO2/ref=sr_1_1?gclid=Cj0KCQjw166aBhDEARIsAMEyZh7w66CXA1fkdfGT0na5LTNuqM_CwmKyOjJmdIP748Th28Dxvora2mkaAvNOEALw_wcB&hvadid=580957328063&hvdev=c&hvlocphy=9023208&hvnetw=g&hvqmt=b&hvrand=17878932423775935625&hvtargid=kwd-301888752915&hydadcr=3649_13538990&keywords=burndy+penetrox+a+13&qid=1665931056&qu=eyJxc2MiOiIxLjQ4IiwicXNhIjoiMC4wMCIsInFzcCI6IjAuMDAifQ%3D%3D&sr=8-1&ufe=app_do%3Aamzn1.fos.006c50ae-5d4c-4777-9bc0-4513d670b6bc	6.88	0.69	1.38		1.38
	H		Charger
	H		Load Supply
	H		FG Post
	H		Diode
	H		Traco
	W		Battery Negative to FG Post
	W		Battery Positive to RSP +V
	W		Contactor, Top Left NC Contact to FG Post
	W		Contactor, Top Right NC Contact to RSP -V
	W		Diode to RSP -V
	W		RSP +V to Traco +Vin
	W		RSP -V to Traco -Vin
	W		Charger B- to FG Post
	W		120 VAC Cord to SCP and FG Post: (4) ring connectors tightened onto FG Post
M11	Oz	0.1	Epoxy: Resin and Hardener				0.2	9.3	8/9/22	8/9/22	Devcon	5 Minute Epoxy, 2 Bottles 8.50 Fl Oz total	Amazon.com			2.12	0.21	0.42		0.42
	PCS	0.05	Power Cable Switch Assembly: Switch epoxied on aluminum bracket
	W	0.05	BTS: Sensor epoxied into connector
M12	Grams	8	Solder: "44" Rosin Core .050"		313		16	297	5/26/20	11/10/22	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	0.13	1.07	2.15		2.15
	W	8	Wiring and Cabling: All solder/tin/torch operations
M13	Each	18	Zip Tie: 4", White	Red	3	100	36	66	11/25/22	11/25/22	Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	0.04	0.65	1.31	0.13	1.43
	H	2	Charger
	W	1	Battery Negative to FG Post
	W	2	Battery Positive to RSP +V
	W	1	Charger B- to FG Post
	W	1	Charger B+ to RSP +V
	W	1	120 VAC Cord to SCP and FG Post
	W	3	120 VAC Neutral from SCP to Contactor to RSP
	W	1	Traco +Vout to Barrier Strip
	W	1	Traco Outputs, Power Cable Switch (left side top) to Barrier Strip
	W	5	BTS
M14	Inches	3	Silver Tape	Old stock from an HVAC supply house			6			8/1/18	Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		0.01	0.02	0.05		0.05
	B	2	Scribe Hole Locations
	W	1	Battery Positive to RSP +V: Spare fuse
			Labels
L1	Inches	5.2	0.35" White: 9mm		157		10.4	147	8/12/15	11/11/22	Brother	TZe-221	Amazon.com		https://www.amazon.com/s/?ie=UTF8&keywords=brother+tze+221&tag=googhydr-20&index=aps&hvadid=153750618191&hvpos=1t4&hvnetw=g&hvrand=1720664198234197072&hvpone=&hvptwo=&hvqmt=e&hvdev=c&hvdvcmdl=&hvlocint=&hvlocphy=9023208&hvtargid=kwd-27725364190&ref=pd_sl_	0.05	0.24	0.48		0.48
	L	0.9	Print and Apply Labels: Leaders (two)
	W	2.0	Traco Output Trim R: W150 Traco Trim R VTS KΩF 0.35.lbx (edited for each Trim R Assembly)
	L	2.3	Print and Apply Labels: W150 Barrier Strip 0.35.lbx
L2	Inches	2.3	0.35" Yellow: 9mm			314	4.5	310	11/25/22	11/25/22	Brother	TZe-S621	PTD		https://www.ptouchdirect.com/ptouch/tzes621.html	0.05	0.10	0.21	-1.44	-1.23
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	1.8	Print and Apply Labels: W150 Do Not Overtighten 0.35.lbx (2)
L3	Inches	23.8	0.47" White: 12mm		157	314	47.6	424	11/25/22	11/25/22	Brother	TZe-S231	PTD		https://www.ptouchdirect.com/ptouch/tzes231cs.html	0.05	1.16	2.32	-1.53	0.79
	P	1.4	Orders Followup: Leaders (three .ods tracked items V, BC, S; one leader each for entire production run)
	P	9.9	Orders Followup: Inventory Sticker 0.47.lbx (three each for three .ods tracked items V, BC, S)
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	3.0	Print and Apply Labels: W150 Wire Label AC Plug 0.47.lbx
	L	4.3	Print and Apply Labels: W150 Operating Ranges 0.47.lbx
	L	1.3	Print and Apply Labels: W150 Load Supply 0.47.lbx
	L	3.5	Print and Apply Labels: W150 Wire Label BTS 0.47.lbx
L4	Inches	6.6	0.47" Yellow: 12mm			314	13.1	301	11/25/22	11/25/22	Brother	TZe-S631	PTD		https://www.ptouchdirect.com/ptouch/tzes631.html	0.05	0.33	0.65	-1.57	-0.92
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	1.5	Print and Apply Labels: W150 FG Post 0.47.lbx
	L	4.6	Print and Apply Labels: W150 No User Serviceable Parts 0.47.lbx
L5	Inches	2.8	0.7" White: 18mm		100	314	5.5	409	11/25/22	11/25/22	Brother	TZe-S241	PTD		https://www.ptouchdirect.com/ptouch/tzes241.html	0.06	0.16	0.31	-1.79	-1.47
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	2.3	Print and Apply Labels: W150 Tower Power Cable 0.7.lbx
L6	Inches	7.2	0.94" White: 24mm		404		14.3	390	6/22/19	11/11/22	Brother	TZe-S251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	0.07	0.52	1.05		1.05
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	4.0	Print and Apply Labels: W150 SN Man'f 0.94.lbx (edited for each W150)
	L	1.5	Print and Apply Labels: W150 Battery Charger 0.94.lbx
	L	1.2	Print and Apply Labels: W150 Traco Output 0.94.lbx
L7	Inches	4.4	0.94" Yellow: 24mm		361		8.7	353	6/22/19	11/11/22	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	0.07	0.31	0.63		0.63
	L	0.5	Print and Apply Labels: Leader (one for entire production run)
	L	3.9	Print and Apply Labels: W150 Caution! 120 VAC 0.94 Yellow.lbx (3)
			Accessories
		0	No Accessories yet

61	Ingredients (Unique Parts)					407.02	814.04	86.80	900.84
	142	Subcounts (Assembly Steps)

## WP12-13A
WISPers: WP12-13A	D				ASSEMBLY LABOR	Quantity:	2
						WP12 ... WP13	W150_2 ... W150_3

Labor				Assembly Phase Descriptions and Notes
Date Started	Date Completed	Hours	Hours Each	Part Number(s)	Procedure Specification	Problems, Exceptions	Next Time, Improvements
Tu7/19/22	Su12/25	39.5	19.8		Procurement [P]
Th8/4	Th11/24	16.5	8.3	All	Planning: Copy and link the PARTS and ASSEMBLY LABOR sheets from the previous run and plan the next run / Generally all comments are left in place until they no longer apply (they can be edited for this run's data) / PARTS Sheet Preparation: (Do NOT set Quantity yet); (Collapse grouped subcount lines and be careful not to clobber them when copying!) / Copy Stock Quantities from Remaining to Before (select Visible Rows Only, copy Values and Formats then copy Comments) / Clear values from Ordered; Clear values, formulas, comments and highlighting from Remaining / Enter default formulas in Remaining (=Before+Ordered-Used, select Visible Rows Only when copying) / Clear values and formulas from Tariff Tax S&H Miles; Set Quantity / ASSEMBLY LABOR Sheet Preparation: Clear values from Date Started and Date Completed (including section headers) and unmerge cells / Clear values and formulas in Hours (excluding section headers) but do not unmerge cells; Set Quantity / Both Sheets: Record data for any already completed work; Update list for design and procedure changes* / Clear bench to layout parts; Take inventory and update Stock Quantities > Before; Plan orders	Not everything was ordered at the same time: The Tracos were ordered early because I was worried about getting stock; The aluminum was ordered early just so I could feel good about making progress (but it turns out OK, as I could paint the backplate on a warm day and get started) / Still learning the system: Quite a bit of extra time to massage and fix problems with the PARTS and ASSEMBLY LABOR sheets	Procurement should be performed all at once, working from these sheets / There were a lot of parts ordered for this run that won't have to be ordered for a long time (7 items from BDC, 9 items from DKE, 2 items from MOU, 4 items from PTD) / Now that the system is well developed it should go faster, probably 1/3 the time
Fr10/14	Fr11/25	10.9	5.5	C1 C3-C8 / H1 H3-H6 H9-H12 / W8 M1 M8 M13 L2-L5	Orders; Budget Management; Save important datasheets to LIB*; Create Summary and History sheets for tracked items
Mo10/17	Su12/25	12.1	6.1	L3	Orders Followup: Receiving; Resolve supplier errors; Hand labels; L3 inventory labels / Print and annotate invoices (scans for LIB, .ods updates, file)
Tu8/9	We8/10	0	0		Power Cable Switch Assembly [PCS]
Tu8/9	We8/10	0.0	0	C12 H18 M11	Fabricate aluminum brackets; Weigh Epoxy; Epoxy switch into bracket; Weigh Epoxy
We11/23	Mo12/5	10.7	5.4		Backplate Fabrication [B]
We11/23	We11/23	1.6	0.8	H1-H2	Paint: Weigh paint; Set up on the porch, if air T is low paint in the sun, otherwise in the shade, backplate 50-90⁰F (monitor closely with Fluke IRT), avoid overheating from the sun; Shake can vigorously for several minutes; Remove plastic covering and paint immediately, spraying 12-16" from backplate; Two or three light coats separated by minutes; Clear nozzle; Weigh paint; Allow to dry 12 hours at 75⁰F before scribing	Painted on porch, good Ts, but difficult to hold 12-16" spray distance due to wind	Spray without wind
Fr12/2	Fr12/2	1.5	0.8	H1 M14	Scribe Hole Locations: On only one of the backplates for the run; Browne & Sharpe; Angle blocks, M14 silver tape / As per Cardboard Template: Scribe locations by halves / quadrants (right side, left side, bottom, top) / Scribe lines should continue through all locations that are in line (except mounting holes top and bottom)	Added M14 silver tape to PARTS / One line was underscribed and had to be redone	Time s/b less if I do it right (careful to overscribe enough!); Otherwise pretty firm time estimate in production (even for 5 in run)
Fr12/2	Fr12/2	0.3	0.2		Gather and Layout Tooling ― All that will be needed to drill, mill, tap and deburr the holes (common Clausing tools/wrenches not listed): / 10x14" Plywood or Partical Board: Relieved with openings in the mounting hole areas on top and bottom (for inserting the Clamp Bolt Sets) / Relieve with 15/16" hole saw, Dad's vise, handrill, bandsaw, clean up sawdust; Board s/b useable on at least 4 production runs / C-Clamps: For temporary use in clamping the backplate stack together to move from Dad's vise to the mill / Clamp Bolt Sets (2x): 5/16"-18x1" HH tap bolt; 5/16" washer (under head); 5/16" star lockwasher (under backplates); 5/16"-18 nut / Clamp Bolts are inserted from the top, may have to add additional washers under head for small runs less than 3 backplates / 1" bolts s/b long enough for up to 5 backplates; [Bolt sets stored in Hardware box between runs] / Drills: 1/8", 11/64", 1/4", 5/16" / Taps and Matching Drills: With tap handle and pliers*M / #6-32 : #35 0.110" or 7/64" 0.109" / #8-32 : #29 0.136" / 1/4"-28 : #3 0.213" / 5/16"-18 : F 0.257" or G 0.261" / Center Drills: #2 (3/16" OD); #4 (5/16" OD); #5 (7/16" OD) / Headlamp; Countersink*; Isopropyl Alcohol for Clean Up*; Paper Towels for Clean Up*M	Detailed list did not exist yet / Produced list for this run / Production Procedure changes: R&D time not tallied here	Design Change: No tapped holes; KEPS Nuts / Use checklist to gather and layout tools
Sa12/3	Mo12/5	0.0	0	H1	Clamp Backplate Stack Together: Stack all the backplates for the run* in Dad's vise (Board, plates, paper on top) / Optimize alignment between the plates (right side edges sitting down on vise rods, short edges tapped into alignment) / Tighten vise and install C-Clamps in the area where the mounting/clamp holes are to go (in relieved area of Board underneath)	I did not use Dad's vise or C-Clamps to bring the stack together on this run, as I was able to get the two plates aligned well enough on the Mill / I used the dial indicator to make the right side set, but then realized it is unnecessary / Center Drills are dull	Use Dad's vise and C-Clamps to align and clamp the stack together / Do NOT use Dial Indicator to align to table / Buy new Center Drills / Design Change: No tapped holes; KEPS Nuts
	Mo12/5	4.7	2.4	H1	Mill Holes: 10x14x3/4" plywood or partical board support; Cardboard backplate protectors under clamps on Clausing table / The Clausing does not have enough travel to cover more than ~4.5" width for each set; Start with the right side (least amount of travel) / Clamp the backplate stack down to the table firmly* and remove the C-Clamps; Spot and overdrill all small holes* with Center Drill / Drill the two mounting holes, insert and tighten temporary 5/16"-18 bolts, nuts and washers to clamp the backplate stack together / Drill/mill all the holes for the right side; Reset for the left side; Drill/mill all the holes for the left side
Mo12/5	Mo12/5	1.2	0.6	H1	Tap Holes: Clamp stack in Dad's vise (protect with paper); Tap from the top scribed backplate side; Remove temporary 5/16"-18 bolts	Dropped star washer, lost on the floor
Mo12/5	Mo12/5	1.4	0.7	H1	Countersink: Backplates individually clamped in Dad's vise (protect with paper) / Countersink both sides of 1/4" zip tie holes and front sides of Diode and FG Post holes	Wasted some time deburring	No deburring
Mo12/5	Mo12/5		0	H1	Clean Up: Clean backplates (isopropyl, paper towels); Clean up mill/garage areas (tools put away, sweep/vacuum)
Mo12/5	We12/7	3.3	1.7		Hardware Assembly [H]
Mo12/5	Mo12/5	1.0	0.5	H3-H17 M10 M13	Prep: Count out the small parts H3-H17 in tuna cans; Weigh and warm M10 Penatrox*; Check/modify beginning inventory on M13 zip ties
Mo12/5	Mo12/5		0	H3 H12	Feet Installed	Ideal Spec s/b 1/2" screws (but 3/8" OK)	Design Change: No tapped holes; KEPS Nuts
Mo12/5	Mo12/5	0.4	0.2	C1 H4 H5 / M10 M13	Charger: Cut C1 B+ red wire 10.7" from PCB; Cut other wires 3.0" from PCB; M13 zip ties on all wires near PCB and to grill (temporary) / Apply M10 Penatrox and mount with H4 screws and H5 split washers	Applied too much Penatrox	More conservative use of Penatrox
Mo12/5	Mo12/5	0.3	0.2	C4 H6 H8	Contactor: Mount with H6 screws and H8 flat washers		Design Change: No tapped holes; KEPS Nuts
Mo12/5	Mo12/5		0	C5 H10 H11 M10	Load Supply: Apply M10 Penatrox and mount with H10 screws and H11 split washers
Tu12/6	Tu12/6	0.3	0.2	H13-H17 / M10	FG Post: Apply M10 Penatrox; H13 bolt and H14 split washer tightened onto backplate; H15 star washer and H16 nut tightened onto bolt / Additional H16 top nut left loose for assembly of (4) ring connectors; (H17 washer will be applied in Wiring and Cabling before tightening)		Design Change: No tapped holes
Tu12/6	Tu12/6	0.3	0.2	C3 / M10	Diode: Apply M10 Penatrox on base and thread; 11/16" wrench, 28 lbf-in maximum (tighten by feel, not aggressive, do not overtighten) / Install included washers and nut (tighten by feel, not aggressive, do not overtighten but make sure star washer is firmly dug into aluminum)		Design Change: No tapped holes
Tu12/6	Tu12/6	0.2	0.1	C8 H6 H9 M10	Traco: Apply M10 Penatrox and mount with H6 screws and H9 split washers		Design Change: No tapped holes; KEPS Nuts
Tu12/6	Tu12/6	0.3	0.2	C12 H6 H8 H9 H18	Power Cable Switch Assembly: Mount with H6 screws, H8 flat washer and H9 split washer	(1) backplate thread stripped (backed with nut)	Design change will eliminate the PCS Assembly
Tu12/6	Tu12/6	0.2	0.1	C11 H6-H8	Barrier Strip: Mount with (3) H6 screws; Power Cable Shield ground point (lower left) H7 screw and H8 flat washer	Eliminated H9 split washers	Design Change: No tapped holes; KEPS Nuts
Tu12/6	We12/7	0.3	0.2	H3-H17	Put away remaining parts (label with quantities/dates); Update Remaining Stock Quantities on PARTS list as needed
We12/7	Sa1/7/23	24.1	12.1		Wiring and Cabling [W]
We12/7	Fr12/9	3.7	1.9	C2 C6 C7 C9 C10 / W1-W10 / M1-M5 M10-M12	Prep: Count out C2 NTCs, C6-C7 fuses/holders and C9-C10 resistors in tuna cans / Wire stocks W1-W10 laid out on the bench; Cut all wire and cable as per PARTS sheet*; Count out connectors M1-4 in tuna cans / Check/update Remaining Stock Quantities for NTCs, fuses/holders, resistors, wire and connectors while counting and cutting / Weigh Epoxy M11 and Solder M12 (record "before" weights in comments on PARTS sheet); Warm M10 Penatrox*	Fabricated a wooden shrink cutting block
Fr12/9	Fr12/9	0.6	0.3	H16 W1 / M1 M8 M10 M13	Battery Negative to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M8 shrink; Repeat for other end / Attach to FG Post (M10 Penatrox bottom side, leave H16 top nut loose); M13 zip tie	Could not find flux brush, refilled acetone / W1 ~29.5" below backplate	Buy metal flux brushes (and more acetone) / Increased W1 length by 0.5"
Fr12/9	Fr12/9	1.3	0.7	C5-C7 / W2 W9 / M1 M8 M10 M13 M14	Battery Positive to RSP +V: W2 and C6 fuse holder strip/twist 1.0"; W9 butt splice wrap/torch/clean*; M8 shrink / C6 strip/twist 0.4"; M1 ring crimp/solder/clean; M8 shrink; Install C7 fuse; Attach C7 spare fuse with M14 silver tape / W2 strip/twist/tin/clean 0.9" (voltmeter clip lead test point); Apply M10 and attach to C5 +V middle screw; M13 zip ties	W2 ~29.7" below backplate	Increased W2 length by 0.3"
Fr12/9	Fr12/9	0.3	0.2	C4 H16 / W1 / M1 M4 M8 M10	Contactor, Top Left NC Contact to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M8 shrink / W1 strip/twist 0.4"; M4 spade crimp/solder/clean; M8 shrink / Attach to C4 (apply M10) and FG post (M10 bottom side, leave H16 top nut loose)	The W1 scraps from the W side already had spade connectors on them
Fr12/9	Fr12/9	0.4	0.2	C4 C5 W3 / M4 M7 M10	Contactor, Top Right NC Contact to RSP -V: W3 strip 0.3"; M4 spade crimp/solder/clean; M7 shrink; W3 strip 0.4" / Bend and prefit W3 from C5 to C4; Attach to C4 (apply M10); Apply M10 and attach to C5 -V left screw
Sa12/10	Sa12/10	0.4	0.2	C3 C5 W3 / M10	Diode to RSP -V: W3 strip 0.6" (for C3) and 0.4" (for C5); Bend and prefit W3 from C5 to C3 / Apply M10 and attach to C5 -V middle screw; Solder to C3 anode (quick, not too hot); Clean	Shortened W3 from 8.5 to 8.0"
Sa12/10	Sa12/10	1.4	0.7	C5 C8 / W2 W4 W9 / M8 M10	RSP +V to Traco +Vin: W4 bent into "V" shape* / W2 strip/twist 1.0"; W4 W2 W9 butt splice wrap/torch/clean; M8 shrink; W2 strip/twist/tin/clean 0.4" / Bend and prefit W2 from C8 +Vin to C5 +V right screw (form vertical Extech test loop on left side); Attach to C8*; Apply M10 and attach to C5	Shortened M8 from 2.0 to 1.8" / Applied M10 to Traco end and had to clean with Q-tip and acetone	Do not apply M10 Penatrox on Traco end
Sa12/10	Sa12/10	0.6	0.3	C5 C8 / W3 W4 W9 / M8 M10	RSP -V to Traco -Vin: W4 bent into "V" shape / W3 strip 1.0"; W4 W3 W9 butt splice wrap/torch/clean; M8 shrink; W3 strip 0.4" / Bend and prefit W3 from C8 -Vin to C5 -V right screw; Attach to C8*; Apply M10 and attach to C5	Applied M10 to Traco end and had to clean with Q-tip and acetone	Do not apply M10 Penatrox on Traco end
Su12/11	Sa12/11	0.9	0.5	C1 / H16 / M2 M6 M7 M10 M13	Charger B- to FG Post: Remove temporary zip tie from C1 grill; M6 shrink on extra wires from C1 (blk, org, yel) and M13 zip tie to grill / Slip M7 shrink over C1 B- and strip/twist 0.4"; M2 ring crimp/solder/clean; M7 shrink / Attach to FG Post (M10 Penatrox bottom side, leave H16 top nut loose)	I forgot to slip the M7 shrink over C1 B- / #10-12 ring connectors were used (hard to crimp, too large)	Specified #14-16 ring connectors with 3/16" shrink
Su12/11	Sa12/11	0.3	0.2	C1 C5 M13	Charger B+ to RSP +V: C1 B+ strip/twist/tin/clean 0.4"; Attach to C5 +V left screw; M13 zip tie below C1 (Extech test loop)	Forgot to clean with acetone	Use acetone to clean solder flux
Mo12/12	Mo12/2	0.8	0.4	C1 / H16 H17 / W5 / M2 M7 M10 M13	120 VAC Cord to SCP and FG Post: W5 cut to 6 feet long (if not done in Prep); Coil the plug end with M13 zip tie (temporary) / W5 strip outer jacket 1.5"; W5 L/N strip/twist/tin/clean 0.3"; W5 Gnd (green) strip/twist 0.4"; M2 ring crimp/solder/clean; M7 shrink / Apply M10 Penatrox bottom side and place on FG Post; Add H17 washer, M10 Penatrox and H16 nut / Tighten H16 nut very tight on (4) ring connectors (Battery Negative, Contactor, Charger B- and AC Gnd); Loosely attach W5 L/N to C1	W5 cords 5.8 feet long
Mo12/12	Mo12/2	0.7	0.4	C1 C4 C5 W6 / M5 M8	120 VAC Line from SCP to Contactor to RSP: W6x2 strip/twist 0.4"; W6x2 M5 spade crimp/solder/clean; M8 shrink / W6x2 strip/twist/tin/clean 0.3"; Attach to C4 lower left, C1 and C5 Line
Mo12/12	Mo12/2	0.7	0.4	C1 C4 C5 / W7 / M5 M8 M13	120 VAC Neutral from SCP to Contactor to RSP: W7x2 strip/twist 0.4"; W7x2 M5 spade crimp/solder/clean; M8 shrink / W7x2 strip/twist/tin/clean 0.3"; Attach to C4 lower right, C1 and C5 Neutral / (3) M13 zip ties (below C1, below C5 and exit at bottom); Apply AC to check for DOAs (Charger, Load Supply, Traco)	Shortened W7 to 7.0" x2	Eliminate zip tie holes directly below contactor
Mo12/12	Mo12/2	0.3	0.2	C8 C11 W7	Traco -Vout to Barrier Strip: W7 strip/twist/tin/clean 0.3" (both ends); Attach to C8 and C11 3rd from left
Mo12/12	Mo12/2	0.2	0.1	C11 W7	Traco Outputs, Barrier Strip to Barrier Strip (Jumper): W7 strip/twist/tin/clean 0.3" (both ends); Attach to C11 3rd from left to left		Design change will eliminate the Jumper
Mo12/12	Mo12/2	0.4	0.2	C8 C11 W8 M13	Traco +Vout to Barrier Strip: W8 strip/twist/tin/clean 0.3" (both ends); Attach to C8 and C11 right (Extech test loop); M13 zip tie
Mo12/12	Mo12/2	0.4	0.2	C11 C12 W8 / M5 M7	Traco Outputs, Barrier Strip to Power Cable Switch (right side top): W8 strip/twist 0.4"; M5 spade crimp/solder/clean; M7 shrink / W8 strip/twist/tin/clean 0.3"; Attach to C11 right and C12 (right side top)		Design change will eliminate the PCS Assembly
Mo12/12	Mo12/2	0.3	0.2	C11 C12 W8 / M5 M7 M13	Traco Outputs, Power Cable Switch (left side top) to Barrier Strip: W8 strip/twist 0.4"; M5 spade crimp/solder/clean; M7 shrink / W8 strip/twist/tin/clean 0.3"; Attach to C11 2nd from left and C12 (left side top); M13 zip tie		Design change will eliminate the PCS Assembly
Tu12/13	Tu12/13	0.5	0.3	C8-C10 / M7 L1	Traco Output Trim R: C9/C10 twisted together, solder/trim/clean; Cut C9/C10 assembly to 1.2"; M7 shrink/crimp / Measure with Fluke, print and apply L1; Install on C8	Trim R Assembly for WP13 produced a somewhat low Traco output *	2nd Production Run will use solitary 15.0K to target 52.83 VTS (eliminate C10)
Tu12/13	Sa1/7/23	2.6	1.3	C1 C2 / W10 / M3 M6 M7 M9 / M11 M13	BTS: Assemble sensor to zip wire, epoxy into battery post connector and solder zip wire to charger CN2 connector pins: / Assemble C2 NTC sensor to W10 zip wire with layers of shrink: W10 split 1.5", strip/twist/tin 0.3" and preload with M6 shrink / C2 NTC cut to 0.6"; W10 C2 dual butt solder/clean/shrink; Add M7 shrink (crimp/seal tip) / Epoxy Sensor Assembly Into Ring with Double Layer of Shrink: Flatten M3 ring in garage vise for a snug fit to sensor; "Helping Hand" with paper towel underneath, 60⁰ angle down from ring (almost vertical); M11 epoxy, do not get epoxy on ring!; M9 shrink 2x crimp/seal / Solder BTS Assembly to CN2 Connector Pins: C1 heat and remove CN2 connector plastic shell; W10 split 0.7" strip/tin 0.4" / W10 bend small loops, M13 zip tie to side hole on C1, crimp to CN2 connector pins; Pencil iron tack solder/clean / M13 strain relief zip tie on C1 grill; (3) M13 zip ties *	BC10/WP12 BTS: Was already assembled to the zip wire and soldered to the CN2 pins [T48S]; Extends 48" below the W150 backplate bottom; Completely finished assembly of WP12 before coming back to assemble the BC11/WP13 BTS	Fabricate entire BTS assembly in this step / Finish all units in production run before proceeding
Tu12/13	Sa1/7/23	7.3	3.7	C2 C6-C7 C9-C10 / W1-W10 / M1-M13	Completion: Check/update Remaining Stock Quantities for NTCs, fuses/holders, resistors, wire, connectors, shrink tubing and zip ties* / Weigh M10 Penatrox, M11 Epoxy and M12 Solder (update consumption on PARTS sheet) / M13 zip ties count checked/modified*; Tighten all wiring connection screws; Clean up the bench	Step not completed all at once (WP13 was delayed until after finishing WP12)*	Finish all units in production run before proceeding to Configuration and Testing / * Note on M10-12 consumptions
Tu12/13	Mo1/30/23	7.4	3.7		Configuration and Testing
Tu12/13	Sa1/7/23	1.1	0.6		Bench Setup: Each W150 is configured and tested individually; No battery is required; W150 next to Engel; Set Z19 for target 25.0⁰C / BTS and Z19 T2 bolted together in metal pipe with bubble wrap to keep air out of the pipe in center of Engel enclosure / ITECH and Fluke turned on (keep shop ambient stable throughout configuration and testing); ITECH Von Living 5.0v	WP12 and WP13 were not done one after the other (almost a month apart)	Save time by moving through all the W150s in the Production Run without interruptions
Tu12/13	Sa1/7/23	1.5	0.8	C1	Charger Configuration: ITECH on end of battery cables, Sense ON; W150 AC power applied (T1 UPS) / Verify that contactor opens and that three supplies are up (green LEDs, Fluke on Load Supply and Traco output) / ITECH CC 150mA; Stabilize Engel/BTS at 25.0⁰C; Adjust charger for target 13.500vI (record achieved value)	BC10/WP12: Charger adjusted on T48S (recorded achieved value)
Tu12/13	Su1/8/23	0.8	0.4	C1	Charger Burn-In: [ITECH remains on end of battery cables]; 90wIS* for >=12 hours ... / ITECH load OFF and disconnected (protect battery cable ends from accidental short)	BC10/WP12: Burn-in only 1.2 hours	Burn-in for >=12 hours
Tu12/13	Su1/8/23	1.1	0.6	C5	Load Supply Configuration: ITECH Sense on RSP +V and Diode anode*; No load (except Traco idle) / Wait for W150 stabilization (cool-down from burn-in, vI stable for 15m); Adjust Load Supply for target 13.700vI (record achieved value)	Hunted for the right screwdriver	Save time by moving through all the W150s in the Production Run without interruptions
Tu12/13	Mo1/30/23	2.4	1.2	C5 C8	Load Supply and Traco Burn-In: ITECH with Sense on Traco output at Barrier Strip / 20wIS; Wait ~1h for stabilization (≤ ± 1mV change over a 15m period), record Traco output vI * / 180wIS for >=12 hours ... / ITECH load OFF and disconnected; W150 AC power disconnected; BTS removed from Engel / (Go to Bench/BTS Setup for next W150 in Production Run)	Traco output vI was recorded at 0wIS and without sufficient time to stabilize	Record Traco output vI at 20wIS after sufficient stabilization
Su1/8/23		0.5	0.3		After all the W150s are Configured and Tested: Engel/Dinico/ITECH/Fluke OFF and Status=Available
We12/14	Mo1/30/23	2.7	1.4		Labels [L]
We12/14	Mo1/30/23	0.6	0.3		Tighten ALL Screws; Tools for this put away	Not completed all at once (WP13 was delayed until after finishing WP12)	Finish all units in production run at the same time
We12/14		1.4	0.7	L1-L7	Print and Apply Labels: See PARTS for LBX files (filenames indicate locations on W150); Clean with isopropyl before applying* / Update PARTS list Labels Remaining Stock Quantities as needed (there's other consumption besides for the W150s)
We12/14		0.7	0.4		Prep for Transport: Coil up AC Input and Battery Cables (twist ties, old stock); Box for protection and transport
Fr7/22/22	Sa2/4/23	0.6	0.3		Completion
We8/10/22	Sa2/4/23		0		Photos
Fr7/22/22	Sa2/4/23		0	C1 C5 C8	WISPer, tracked equipment and Location .ods records completed
Mo11/21/22	Sa2/4/23	0.6	0.3		PARTS and ASSEMBLY LABOR sheets completed: FTR Assembly Hours totalled and checked against totals here; Protect sheets (no password)
Tu7/19/22	Sa2/4/23	88.3	44.2		Entire Assembly Procedure Completed

## WP14-15P
WISPers: WP14-15P	B					PARTS - BoM for each WISPer					Run Quantity:	2	WP14 ... WP15		W150_4 ... W150_5

		Quantity	Unit	Description			Stock Quantities				Order Information					$.$$
Part #	Part#			Name	Specification	Substitute	Before	Ordered	Used	Remaining	Order Date	Pricing Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Web Link	Unit Cost	W150 / Subtotal	Production / Run / Subtotal	Tariff Tax S&H Miles	Production / Run / Total Cost
				Components
C1	C1	1	Each	Battery Charger	75 W			2	#VALUE!		3/8/23	3/8/23	Mean Well	SCP-75-12	MOU	709-SCP75-12	BC12-13	33.58	#VALUE!	#VALUE!	8.44	#VALUE!
		1	HA		Charger: Blind mount
C2	C2	1	Each	NTC Thermistor	100KOHM 4190K BEAD			10	#VALUE!	#VALUE!	3/8/23	3/8/23	Vishay	NTCLE100E3104HB0	DKE	BC2520-ND	https://www.digikey.com/en/products/detail/vishay-beyschlag-draloric-bc-components/NTCLE100E3104HB0/773995?s=N4IgTCBcDaIEIGEwFYwAYC0A5AIiAugL5A	0.81	#VALUE!	#VALUE!	0.71	#VALUE!
		1	WC		BTS
C3	C3	1	Each	Diode	800V/80A, With Mounting Hardware			2	#VALUE!		3/8/23	3/8/23	Vishay	VS-80PF80	DKE	VS-80PF80-ND	https://www.digikey.com/en/products/detail/vishay-general-semiconductor-diodes-division/vs-80pf80/4932266	6.60	#VALUE!	#VALUE!	1.15	#VALUE!
		1	HA		Diode
C4	C4	1	Each	Diode Bypass Contactor	30A/28VDC			2	#VALUE!		3/8/23	3/8/23	Omron	MJN1Z-E-RP-AC120	MOU	653-MJN1Z-E-RP-AC120	https://www.mouser.com/ProductDetail/Omron-Automation-and-Safety/MJN1Z-E-RP-AC120?qs=CqvodWcFzOePCe%2FIlIpfnw%3D%3D	38.46	#VALUE!	#VALUE!	9.66	#VALUE!
		1	HA		Contactor
C5	C5	1	Each	Load Supply	13.5V 200W Switching Power Supply			2	#VALUE!		3/8/23	3/8/23	Mean Well	RSP-200-13.5	SPSE	RSP-200-13.5	S20-21	49.20	#VALUE!	#VALUE!	40.15	#VALUE!
		1	HA		Load Supply: Blind Mount
C6	C6	1	Each	Battery Fuse Holder	Inline, ATM, 30A, #12 AWG		10		#VALUE!	#VALUE!	11/25/22	2/19/23	NTE Electronics	74-IFHMAL30	DKE NTE	2368-74-IFHMAL30-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-ifhmal30/11651173	3.37	#VALUE!	#VALUE!		#VALUE!
		1	WC		Battery Positive to RSP +V
C7	C7	2	Each	Battery Fuses	ATM, 30A, Green		21		#VALUE!	#VALUE!	11/25/22	2/19/23	NTE Electronics	74-MAF30A	DKE NTE	2368-74-MAF30A-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-maf30a/11653142	0.23	#VALUE!	#VALUE!		#VALUE!
		1	WC		Battery Positive to RSP +V: Installed
		1	WC		Battery Positive to RSP +V: Spare
C8	C8	1	Each	DC/DC Converter	150w, Wide Input 9-36vdc , Output 48-57.6vdc		3		#VALUE!	#VALUE!	10/14/22	10/14/22	Traco Power	TEP 150-2418WI	SPSE	TEP 150-2418WI	V14-15	220.35	#VALUE!	#VALUE!		#VALUE!
		1	HA		Traco
C9	C9	1	Each	Trim Resistor	1/4W Metal Film 15.0KΩ 0.1%	1% from kit from www.techam.com	3		#VALUE!	#VALUE!		2/18/23	Yageo	MFP-25BRD52-15K	DKE	15KADCT-ND	https://www.digikey.com/en/products/detail/yageo/MFP-25BRD52-15K/2058801?s=N4IgTCBcDaILIDEAKBaMBWAQgJQCLrBQEZ0BpEAXQF8g	0.50	#VALUE!	#VALUE!		#VALUE!
		1	WC		Traco Output Trim R
C10	C10	1	Each	Meter	Digital Panel Voltmeter 6 to 75V Red LED, 1.2" Round Hole			2	#VALUE!		11/21/22	3/10/23	Murata	DMR20-10-DCM-R-C	DKE	811-2858-ND	Z21-22	52.75	#VALUE!	#VALUE!	-105.50	#VALUE!
		1	HA		Meter
C11	C11	1	Each	Meter Switch	DP3T On-On-On, Panel Mount			2	#VALUE!		3/8/23	3/8/23	NKK Switches	M2044SS1W01	DKE	360-2082-ND	https://www.digikey.com/en/products/detail/nkk-switches/M2044SS1W01/1007139	15.39	#VALUE!	#VALUE!	5.75	#VALUE!
		1	HA		Meter Switch
C12	C12	1	Each	DC/DC Output Switch	SPST On-Off, Panel Mount			2	#VALUE!		3/8/23	3/8/23	NKK Switches	M2011SS1W01	DKE	360-2827-ND	https://www.digikey.com/en/products/detail/nkk-switches/M2011SS1W01/1049352	4.73	#VALUE!	#VALUE!	1.77	#VALUE!
		1	HA		Traco Output Switch
C13	C13	1	Each	Barrier Strip	3 Positions, Single Row, Bottom Termination Solder Turrets			2	#VALUE!		3/8/23	3/8/23	Molex	387203803	DKE	WM20049-ND	https://www.digikey.com/en/products/detail/molex/0387203803/3599369	4.51	#VALUE!	#VALUE!	0.78	#VALUE!
		1	HA		Barrier Strip
C14	C14	2	Each	Meter Assembly Fuses	0.25A Slow Blow, 30VDC, Pigtail or Pico		55		#VALUE!	#VALUE!		2003?		230 2AG - 2A 250V				0.40	#VALUE!	#VALUE!		#VALUE!
		2	WC		Meter Fuse Assemblies: 2x (RSP +V and RSP -V)
				Hardware
H1	H1	1	Each	Backplate	Aluminum Sheet 10x14x0.080"			2	#VALUE!		3/8/23	3/8/23		3003-H14 (10x14")	MBTF	080ALSM + 0000CUT		11.39	#VALUE!	#VALUE!	24.32	#VALUE!
		1	PS		Paint Aluminum Plates
H2	H2	1	Each	Meter/Output Plate	Aluminum Sheet 3x5x0.080"			2	#VALUE!		3/8/23	3/8/23		3003-H14 (3x5")	MBTF	080ALSM + 0000CUT		1.22	#VALUE!	#VALUE!	2.61	#VALUE!
		1	PS		Paint Aluminum Plates
H3	H3	1.4	Oz	Paint	High Heat		32.2		#VALUE!	#VALUE!		10/15/22	Rust-Oleum	7778 BAR-B-Q BLACK	Amazon.com	7778830	https://www.amazon.com/gp/product/B0010O0C94/ref=ox_sc_act_title_1?smid=ATVPDKIKX0DER&th=1	0.50	#VALUE!	#VALUE!		#VALUE!
		1.4	PS		Paint Aluminum Plates
H4	H4	4	Each	Backplate Feet	1/2" High, Nylon, Screw Mount, Cylindrical, Recessed Center, 5/8" OD			25	#VALUE!	#VALUE!	3/8/23	3/8/23	Essentra Components	BRR025A	DKE	RPC5642-ND	https://www.digikey.com/en/products/detail/essentra-components/BRR025A/9343103	0.22	#VALUE!	#VALUE!	0.48	#VALUE!
		4	HA		Feet Installed
H5	H5	2	Each	3x0.5x6mm Star Drive Pan Head Screw	T10 Torx, SS 18-8 (A-2)	L=5mm used w/o Split Washer	96		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	19243	https://www.boltdepot.com/Product-Details.aspx?product=19243	0.06	#VALUE!	#VALUE!		#VALUE!
		2	HA		Charger: Blind mount
H6	H6	2	Each	3mm Split Washer	SS 18-8 (A-2)	#6 Split Washer	96		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	4810	https://www.boltdepot.com/Product-Details.aspx?product=4810	0.02	#VALUE!	#VALUE!		#VALUE!
		2	HA		Charger: Blind mount
H7	H7	4	Each	#6-32 Meter Plate Standoffs	Male-Female, 1" High, 1/4" Hex, Aluminum	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		10	#VALUE!	#VALUE!	3/8/23	3/8/23	RAF Electronic Hardware	4542-632-AL	DKE	1772-1387-ND	https://www.digikey.com/en/products/detail/raf-electronic-hardware/4542-632-AL/7680798	0.44	#VALUE!	#VALUE!	0.38	#VALUE!
		4	HA		Meter/Output Plate Standoffs
H8	H8	10	Each	#6-32x3/8" Star Drive Pan Head Screw	T15 Torx, SS 18-8	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot	78		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	19124	https://www.boltdepot.com/Product-Details.aspx?product=19124	0.12	#VALUE!	#VALUE!		#VALUE!
		2	HA		Contactor
		4	HA		Traco
		4	WC		Install Meter/Output Assembly
H9	H9	2	Each	#6-32x3/4" Star Drive Pan Head Screw	T15 Torx, SS 18-8	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		100	#VALUE!	#VALUE!	3/8/23	3/8/23			BDC	19127	https://www.boltdepot.com/Product-Details.aspx?product=19127	0.14	#VALUE!	#VALUE!	3.88	#VALUE!
		2	HA		Barrier Strip
H10	H10	4	Each	#6 Split Washer	SS 18-8	Old stock, probably not SS 18-8	90		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	2953	https://www.boltdepot.com/Product-Details.aspx?product=2953	0.02	#VALUE!	#VALUE!		#VALUE!
		4	WC		Install Meter/Output Assembly
H11	H11	12	Each	#6-32 KEPS Nut	SS 18-8	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		100	#VALUE!	#VALUE!	3/8/23	3/8/23			BDC	12019	https://www.boltdepot.com/Product-Details.aspx?product=12019	0.05	#VALUE!	#VALUE!	1.39	#VALUE!
		2	HA		Contactor
		4	HA		Traco
		4	HA		Meter Plate Standoffs
		2	HA		Barrier Strip
H12	H12	4	Each	4x0.7x6mm Star Drive Pan Head Screw	T20 Torx, SS 18-8 (A-2)	Philips pan head	92		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	19246	https://www.boltdepot.com/Product-Details.aspx?product=19246	0.07	#VALUE!	#VALUE!		#VALUE!
		4	HA		Load Supply: Blind Mount
H13	H13	4	Each	4mm Split Washer	SS 18-8 (A-2)	Old stock #8 Split Washer	92		#VALUE!	#VALUE!	11/25/22	11/25/22			BDC	4811	https://www.boltdepot.com/Product-Details.aspx?product=4811	0.02	#VALUE!	#VALUE!		#VALUE!
		4	HA		Load Supply: Blind Mount
H14	H14	4	Each	#8-32x5/8" Star Drive Pan Head Screw	T20 Torx, SS 18-8	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		100	#VALUE!	#VALUE!	3/8/23	3/8/23			BDC	19136	https://www.boltdepot.com/Product-Details.aspx?product=19136	0.15	#VALUE!	#VALUE!	4.27	#VALUE!
		4	HA		Feet Installed
H15	H15	4	Each	#8-32 KEPS Nut	SS 18-8	RH Mix: 5/16" philips, 3/8" slot, 1/2" slot		100	#VALUE!	#VALUE!	3/8/23	3/8/23			BDC	12020	https://www.boltdepot.com/Product-Details.aspx?product=12020	0.06	#VALUE!	#VALUE!	1.72	#VALUE!
		4	HA		Feet Installed
H16	H16	1	Each	5/16"-18x1.25" Hex Head Tap Bolt		Old stock, unknown grade	7		#VALUE!	#VALUE!		2/22/23			BDC	18314	https://www.boltdepot.com/Product-Details.aspx?product=18314	0.20	#VALUE!	#VALUE!		#VALUE!
		1	HA		FG Post
H17	H17	2	Each	5/16" External Star Washer	SS 410	Old stock, Internal Star, unknown grade	25		#VALUE!	#VALUE!		2/22/23			BDC	4081	https://www.boltdepot.com/Product-Details.aspx?product=4081	0.08	#VALUE!	#VALUE!		#VALUE!
		2	HA		FG Post: Above and below backplate
H18	H18	2	Each	5/16"-18 Nut	SS 316	Old stock, unknown grade			#VALUE!			2/22/23			BDC	15984	https://www.boltdepot.com/Product-Details.aspx?product=15984	0.11	#VALUE!	#VALUE!		#VALUE!
		2	HA		FG Post: (1) to tighten post to backplate in HA; (1) to tighten connector stack in WC
H19	H19	1	Each	5/16" Split Washer	Zinc plated grade 8 yellow	Old stock, unknown grade			#VALUE!			2/22/23			BDC	3038	https://www.boltdepot.com/Product-Details.aspx?product=3038	0.04	#VALUE!	#VALUE!		#VALUE!
		1	WC		Contactor to FG Post: To place tension on connector stack and resist loosening
				Wire
W1	W1	40.0	Inches	#10 Stranded Black		Scott's Bargain Barn	151		#VALUE!	#VALUE!		2/23/23	Prysmian Group	76832.18.01	DKE	C76832B-100-ND	https://www.digikey.com/en/products/detail/prysmian-group/76832-18-01/5452535	0.07	#VALUE!	#VALUE!		#VALUE!
		36.0	WC		Battery Negative to FG Post
		4.0	WC		Contactor to FG Post
W2	W2	28.1	Inches	#12 Stranded Red			59		#VALUE!	#VALUE!	5/26/20	2/23/23	Remington Industries	12STRREDGPT25	DKE	2328-12STRREDGPT25-ND	https://www.digikey.com/product-detail/en/12STRREDGPT25/2328-12STRREDGPT25-ND/11612528/?itemSeq=327489099	0.05	#VALUE!	#VALUE!		#VALUE!
		28.1	WC		Battery Positive to RSP +V: +V left screw right side
W3	W3	7.1	Inches	#12 Solid Red		Old stock from building construction			#VALUE!			11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	#VALUE!	#VALUE!		#VALUE!
		7.1	WC		RSP +V to Traco +Vin: +V left screw left side (stripped long); Extech test loop
W4	W4	19.3	Inches	#12 Solid Brown		Old stock from building construction	297		#VALUE!	#VALUE!		11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	#VALUE!	#VALUE!		#VALUE!
		11.0	WC		Contactor to Diode to RSP -V: Top right NC contact through Diode to RSP -V right screw left side
		8.3	WC		RSP -V to Traco -Vin: -V right screw right side
W5	W5	6	Inches	#14 Solid Bare		Old stock from building construction (gray or blue)			#VALUE!			11/7/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-14-Gauge-Gray-Solid-Copper-THHN-Wire-112-1460J/305306723	0.01	#VALUE!	#VALUE!		#VALUE!
		3	WC		RSP +V to Traco +Vin: "V"
		3	WC		RSP -V to Traco -Vin: "V"
W6	W6	1	Each	AC Power Cord	NEMA, 15A 120VAC L/N/G, 5' 9"				#VALUE!			Estimate					3.00	#VALUE!	#VALUE!		#VALUE!
		1	WC		120 VAC Cord to Charger
W7	W7	14.5	Inches	#16 Stranded Black		Scott's Bargain Barn			#VALUE!			11/7/22	CNC Tech	1569-16-1-0500-001-1-TS	DKE	CN642B-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-001-1-TS/9450423	0.03	#VALUE!	#VALUE!		#VALUE!
		6.0	WC		120 VAC Line from Charger to Contactor to Load Supply: Wire 1 of 2 in assembly
		8.5	WC		120 VAC Line from Charger to Contactor to Load Supply: Wire 2 of 2 in assembly
W8	W8	14.0	Inches	#16 Stranded White		Scott's Bargain Barn			#VALUE!			11/7/22	CNC Tech	1569-16-1-0500-002-1-TS	DKE	CN643W-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-002-1-TS/9450424	0.03	#VALUE!	#VALUE!		#VALUE!
		7.0	WC		120 VAC Neutral from Charger to Contactor to Load Supply: Wire 1 of 2 in assembly
		7.0	WC		120 VAC Neutral from Charger to Contactor to Load Supply: Wire 2 of 2 in assembly
W9	W9	5.0	Inches	#18 Solid Bare		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		3.0	WC		Meter/Output Assembly GND: Barrier Strip mounting screw to Barrier Strip Gnd to Meter Switch pin 6
		2.0	WC		Meter Switch Jumpers: Pins 3 to 5 and pins 9 to 11 (2 jumpers)
W10	W10	2.0	Inches	#18 Solid Blue		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		2.0	WC		Meter Switch to Meter Inputs: Meter Switch pin 8 to Meter (+)
W11	W11	2.0	Inches	#18 Solid Green		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		2.0	WC		Meter Switch to Meter Inputs: Meter Switch pin 2 to Meter (-)
W12	W12	10.0	Inches	#18 Solid Red		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		1.5	WC		Meter Fuse Assemblies: Short stub to inline fuse from +V right screw right side
		7.0	WC		Meter Fuse Assemblies: Inline fuse to Meter Switch pin 10
		1.5	WC		Meter Switch Jumper (RSP +V): Meter Switch pins 10 to 12
W13	W13	11.7	Inches	#18 Solid Brown		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		1.5	WC		Meter Fuse Assemblies: Short stub to inline fuse from -V left screw left side
		7.2	WC		Meter Fuse Assemblies: Inline fuse to Meter Switch pin 4
		3.0	WC		Meter Switch to Output Switch (RSP -V): Meter Switch pin 4 to Output Switch
W14	W14	6.0	Inches	#18 Solid Yellow		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		6.0	WC		Output Switch to Traco Ctrl
W15	W15	9.0	Inches	#18 Solid Orange		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		2.0	WC		Barrier Strip to Meter Switch (Traco +Vout): Barrier Strip to Meter Switch pin 7
		7.0	WC		Barrier Strip to Traco +Vout
W16	W16	9.0	Inches	#18 Solid White		Stripped from thermostat cable			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		2.0	WC		Barrier Strip to Meter Switch (Traco -Vout): Barrier Strip to Meter Switch pin 1
		7.0	WC		Barrier Strip to Traco -Vout
W17	W17	9	Inches	#22 Solid Bare		Old stock, insulation stripped			#VALUE!			11/7/22	SparkFun Electronics	PRT-08023 [Red]	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	0.01	#VALUE!	#VALUE!		#VALUE!
		3	WC		Battery Positive to RSP +V: Fuse holder butt splice
		3	WC		RSP +V to Traco +Vin: "V" butt splice
		3	WC		RSP -V to Traco -Vin: "V" butt splice
W18	W18	41	Inches	#24 to #20 2-Conductor Stranded Zip/Rip Cord		Cannibalized from adapter bricks			#VALUE!			Estimate					0.02	#VALUE!	#VALUE!		#VALUE!
		41	WC		BTS
				Miscellaneous
M1	M1	4	Each	5/16" Ring Connector #10-12 AWG	Bare (No Insulation)		101		#VALUE!	#VALUE!	11/25/22	11/25/22	3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	0.18	#VALUE!	#VALUE!		#VALUE!
		2	WC		Battery Negative to FG Post
		1	WC		Battery Positive to RSP +V
		1	WC		Contactor to FG Post
M2	M2	1	Each	5/16" Ring Connector #4 AWG	Bare (No Insulation)		1	10	#VALUE!	#VALUE!	3/8/23	3/8/23	TE Connectivity	33470	MOU	571-33470	https://www.mouser.com/ProductDetail/TE-Connectivity/33470?qs=PhejhE5GxlxR3fqYNXf3FA%3D%3D	0.83	#VALUE!	#VALUE!	1.04	#VALUE!
		1	WC		BTS: Sensor epoxied into connector
M3	M3	2	Each	1/4" Female Spade Connector #10-12 AWG	Bare	Old stock: Calterm 61320	30		#VALUE!	#VALUE!		11/9/22	Molex	192030379	DKE	WM19887-ND	https://www.digikey.com/en/products/detail/molex/0192030379/3187492	0.09	#VALUE!	#VALUE!		#VALUE!
		1	WC		Contactor to FG Post
		1	WC		Contactor to Diode to RSP -V
M4	M4	2	Each	1/4" Female Spade Connector #14-16 AWG	Bare	Old stock: Calterm 61180	28		#VALUE!	#VALUE!		11/9/22	Molex	192030390	DKE	WM19888-ND	https://www.digikey.com/en/products/detail/molex/0192030390/3187491	0.09	#VALUE!	#VALUE!		#VALUE!
		1	WC		120 VAC Line from Charger to Contactor to Load Supply: Assembly of 2 wires on one connector
		1	WC		120 VAC Neutral from Charger to Contactor to Load Supply: Assembly of 2 wires on one connector
M5	M5	3.5	Inches	3/32" Shrink Tubing		Old stock, not EPS-200	35		#VALUE!	#VALUE!	Unknown	Estimate					0.19	#VALUE!	#VALUE!		#VALUE!
		2.1	WC		Charger Wires Prep: 3 extra wires
		1.4	WC		BTS: NTC
M6	M6	6.7	Inches	3/16" Shrink Tubing			45.3		#VALUE!	#VALUE!	6/27/22	11/10/22	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-3-16-BL48-BX/260270	0.22	#VALUE!	#VALUE!		#VALUE!
		0.6	WC		Contactor to Diode to RSP -V: Spade connector
		4.0	WC		Meter Fuse Assemblies: 2x (RSP +V and RSP -V)
		0.6	WC		Traco Output Trim R
		1.5	WC		BTS: NTC
M7	M7	11.0	Inches	1/4” Shrink Tubing			239		#VALUE!	#VALUE!	11/25/22	11/25/22	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	0.25	#VALUE!	#VALUE!		#VALUE!
		0.7	WC		120 VAC Line from Charger to Contactor to Load Supply: Spade connector
		0.7	WC		120 VAC Neutral from Charger to Contactor to Load Supply: Spade connector
		1.6	WC		Battery Negative to FG Post: 2x ring connectors
		1.6	WC		Contactor to FG Post: Spade and ring connectors
		2.0	WC		Battery Positive to RSP +V: Fuse holder butt splice
		0.8	WC		Battery Positive to RSP +V: Ring connector
		1.8	WC		RSP +V to Traco +Vin: Butt splice
		1.8	WC		RSP -V to Traco -Vin: Butt splice
M8	M8	3	Inches	1/2" Shrink Tubing			48		#VALUE!	#VALUE!	6/27/22	11/10/22	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-1-2-BL-48-BX/260262	0.34	#VALUE!	#VALUE!		#VALUE!
		3	WC		BTS: 2 layers over sensor ring connector
M9	M9	0.1	Oz	Penatrox a-13 Electrical Joint Compound		PENA13-14, 4 fl. oz.	4.0		#VALUE!	#VALUE!		10/16/22	Burndy	PENA138	Amazon.com	PENETROX A-13, 8 fl. oz.	https://www.amazon.com/Burndy-A13-8-Oxide-Inhibiting-Compounds-Container/dp/B00CBKBZO2/ref=sr_1_1?gclid=Cj0KCQjw166aBhDEARIsAMEyZh7w66CXA1fkdfGT0na5LTNuqM_CwmKyOjJmdIP748Th28Dxvora2mkaAvNOEALw_wcB&hvadid=580957328063&hvdev=c&hvlocphy=9023208&hvnetw=g&hvqmt=b&hvrand=17878932423775935625&hvtargid=kwd-301888752915&hydadcr=3649_13538990&keywords=burndy+penetrox+a+13&qid=1665931056&qu=eyJxc2MiOiIxLjQ4IiwicXNhIjoiMC4wMCIsInFzcCI6IjAuMDAifQ%3D%3D&sr=8-1&ufe=app_do%3Aamzn1.fos.006c50ae-5d4c-4777-9bc0-4513d670b6bc	6.88	#VALUE!	#VALUE!		#VALUE!
			HA		Charger
			HA		Diode
			HA		Load Supply
			HA		Traco
			HA		FG Post
			HA		Meter/Output Plate Standoffs
			WC		Battery Negative to FG Post
			WC		Contactor to FG Post: (2) ring connectors tightened onto FG Post
			WC		Contactor to Diode to RSP -V: Spade connector on Contactor; RSP -V
			WC		Battery Positive to RSP +V
			WC		RSP +V to Traco +Vin
			WC		RSP -V to Traco -Vin
			WC		Meter/Output Assembly GND
			WC		Install Meter/Output Assembly
M10	M10	0.05	Oz	Epoxy	Resin and Hardener		9.3		#VALUE!	#VALUE!	8/9/22	8/9/22	Devcon	5 Minute Epoxy, 2 Bottles 8.50 Fl Oz total	Amazon.com			2.12	#VALUE!	#VALUE!		#VALUE!
		0.05	WC		BTS: Sensor epoxied into connector
M11	M11	8	Grams	Solder	"44" Rosin Core .050"		297		#VALUE!	#VALUE!	5/26/20	11/10/22	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	0.13	#VALUE!	#VALUE!		#VALUE!
		8	WC		All solder/tin/torch operations
M12	M12	19	Each	Zip Tie	4", White	Red	66		#VALUE!	#VALUE!	11/25/22	11/25/22	Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	0.04	#VALUE!	#VALUE!		#VALUE!
		1	HA		Charger
		1	WC		Charger Wires Prep
		1	WC		120 VAC Cord to Charger
		3	WC		120 VAC Neutral from Charger to Contactor to Load Supply
		1	WC		Battery Negative to FG Post
		2	WC		Battery Positive to RSP +V
		1	WC		Charger B+ to RSP +V
		4	WC		Install Meter/Output Assembly
		5	WC		BTS
M13	M13	3	Inches	Silver Tape		Old stock from an HVAC supply house			#VALUE!			8/1/18	Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		0.01	#VALUE!	#VALUE!		#VALUE!
		2	PS		Scribe Hole Locations on Plates
		1	WC		Battery Positive to RSP +V: Spare fuse
				Labels
L1	L1	2.9	Inches	0.23" White	6mm				#VALUE!		6/22/19	Estimate	Brother	TZe-211	Amazon.com			0.05	#VALUE!	#VALUE!		#VALUE!
		0.5	P		Receive: Leader (tracked item Z; one leader for entire production run)
		2.4	P		Receive: W150 Meter Inventory Sticker 0.23.lbx (3x: unit, box, paperwork)
L2	L2	26.8	Inches	0.47" White	12mm		424		#VALUE!	#VALUE!	11/25/22	11/25/22	Brother	TZe-S231	PTD		https://www.ptouchdirect.com/ptouch/tzes231cs.html	0.05	#VALUE!	#VALUE!		#VALUE!
		1.4	P		Receive: Leaders (three .ods tracked items V, BC, S; one leader each for entire production run)
		10.8	P		Receive: W150 Inventory Sticker 0.47.lbx (3 each for 3 .ods tracked items V/BC/S: unit, box, paperwork)
		0.5	WC		Traco Output Trim R: Leader (one for entire production run)
		2.7	WC		Traco Output Trim R: W150 Traco Trim R VTS KΩF 0.47.lbx (edited for each Trim R Assembly)
		0.5	LA		Print and Apply Labels: Leader (one for entire production run)
		3.0	LA		Print and Apply Labels: W150 AC Plug Wire Label 0.47.lbx
		3.8	LA		Print and Apply Labels: W150 BTS Wire Label 0.47.lbx
		1.3	LA		Print and Apply Labels: W150 Load Supply 0.47.lbx
		2.9	LA		Print and Apply Labels: W150 Output 0.47.lbx
L3	L3	5.1	Inches	0.47" Yellow	12mm		301		#VALUE!	#VALUE!	11/25/22	11/25/22	Brother	TZe-S631	PTD		https://www.ptouchdirect.com/ptouch/tzes631.html	0.05	#VALUE!	#VALUE!		#VALUE!
		0.5	LA		Print and Apply Labels: Leader (one for entire production run)
		4.6	LA		Print and Apply Labels: W150 No User Serviceable Parts 0.47.lbx
L4	L4	2.2	Inches	0.7" White	18mm		409		#VALUE!	#VALUE!	11/25/22	11/25/22	Brother	TZe-S241	PTD		https://www.ptouchdirect.com/ptouch/tzes241.html	0.06	#VALUE!	#VALUE!		#VALUE!
		0.5	LA		Print and Apply Labels: Leader (one for entire production run)
		1.7	LA		Print and Apply Labels: W150 Meter 0.7.lbx
L5	L5	11.2	Inches	0.94" White	24mm		390		#VALUE!	#VALUE!	6/22/19	11/11/22	Brother	TZe-S251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	0.07	#VALUE!	#VALUE!		#VALUE!
		0.5	LA		Print and Apply Labels: Leader (one for entire production run)
		1.5	LA		Print and Apply Labels: W150 Battery Charger 0.94.lbx
		4.5	LA		Print and Apply Labels: W150 Operating Ranges 0.94.lbx
		3.8	LA		Print and Apply Labels: W150 SN Man'f 0.94.lbx (edited for each W150)
		1.0	LA		Print and Apply Labels: W150 Traco Vout Set Trim R 0.94.lbx
L6	L6	5.2	Inches	0.94" Yellow	24mm		353		#VALUE!	#VALUE!	6/22/19	11/11/22	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	0.07	#VALUE!	#VALUE!		#VALUE!
		0.5	LA		Print and Apply Labels: Leader (one for entire production run)
		3.8	LA		Print and Apply Labels: W150 Caution! 120 VAC 0.94 Yellow.lbx (3x)
		1.0	LA		Print and Apply Labels: W150 Chassis Ground Battery Negative 0.94 Yellow.lbx
				Accessories
		0		No Accessories yet

70					#VALUE!	#VALUE!	3.00	#VALUE!
			Subcounts (Assembly Steps)

## WP14-15O
WISPers: WP14-15O	C					ORDERING and INVENTORY					Run Quantity:	2	WP14 ... WP15		W150_4 ... W150_5

		From BoM for (1) WISPer				Stock Quantities				Order Information					$.$$
Part #	Part#	Quantity	Unit	Name	Specification	Before	Ordered	Used	Remaining	Order Date	Pricing Date	Manufacturer	Manufacturer Part Number	Supplier	Supplier Part Number	Web Link	Unit Cost	W150 / Subtotal	Production / Run / Subtotal	Tariff Tax S&H Miles	Production / Run / Total Cost
		Components
C1	C1	1	Each	Battery Charger	Battery Charger: 75 W		2	2		3/8/23	3/8/23	Mean Well	SCP-75-12	MOU	709-SCP75-12	BC12-13	33.58	33.58	67.16	8.44	75.60
C2	C2	1	Each	NTC Thermistor	NTC Thermistor: 100KOHM 4190K BEAD		10	2	10	3/8/23	3/8/23	Vishay	NTCLE100E3104HB0	DKE	BC2520-ND	https://www.digikey.com/en/products/detail/vishay-beyschlag-draloric-bc-components/NTCLE100E3104HB0/773995?s=N4IgTCBcDaIEIGEwFYwAYC0A5AIiAugL5A	0.81	0.81	1.62	0.71	2.33
C3	C3	1	Each	Diode	Diode: 800V/80A, With Mounting Hardware		2	2		3/8/23	3/8/23	Vishay	VS-80PF80	DKE	VS-80PF80-ND	https://www.digikey.com/en/products/detail/vishay-general-semiconductor-diodes-division/vs-80pf80/4932266	6.60	6.60	13.20	1.15	14.35
C4	C4	1	Each	Diode Bypass Contactor	Diode Suppression Contactor: 30A/28VDC		2	2		3/8/23	3/8/23	Omron	MJN1Z-E-RP-AC120	MOU	653-MJN1Z-E-RP-AC120	https://www.mouser.com/ProductDetail/Omron-Automation-and-Safety/MJN1Z-E-RP-AC120?qs=CqvodWcFzOePCe%2FIlIpfnw%3D%3D	38.46	38.46	76.92	9.66	86.58
C5	C5	1	Each	Load Supply	Load Supply: 13.5V 200W Switching Power Supply		2	2		3/8/23	3/8/23	Mean Well	RSP-200-13.5	SPSE	RSP-200-13.5	S20-21	49.20	49.20	98.40	40.15	138.55
C6	C6	1	Each	Battery Fuse Holder	ATM Fuse Holder: Inline, 30A, #12 AWG	10		2	8	11/25/22	2/19/23	NTE Electronics	74-IFHMAL30	DKE NTE	2368-74-IFHMAL30-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-ifhmal30/11651173	3.37	3.37	6.74		6.74
C7	C7	2	Each	Battery Fuses	ATM Fuse: 30A, Green	21		4	17	11/25/22	2/19/23	NTE Electronics	74-MAF30A	DKE NTE	2368-74-MAF30A-ND	https://www.digikey.com/en/products/detail/nte-electronics-inc/74-maf30a/11653142	0.23	0.45	0.90		0.90
C8	C8	1	Each	DC/DC Converter	DC to DC Converter: 150w, Wide Input 9-36vdc , Output 48-57.6vdc	3		2	1	10/14/22	10/14/22	Traco Power	TEP 150-2418WI	SPSE	TEP 150-2418WI	V14-15	220.35	220.35	440.70		440.70
C9	C9	1	Each	Trim Resistor	Resistor: 1/4W Metal Film 15.0KΩ 0.1%	3		2	1		2/18/23	Yageo	MFP-25BRD52-15K	DKE	15KADCT-ND	https://www.digikey.com/en/products/detail/yageo/MFP-25BRD52-15K/2058801?s=N4IgTCBcDaILIDEAKBaMBWAQgJQCLrBQEZ0BpEAXQF8g	0.50	0.50	1.01		1.01
C10	C10	1	Each	Meter	Meter: Digital Panel Voltmeter 6 to 75V Red LED, 1.2" Round Hole		2	2		11/21/22	3/10/23	Murata	DMR20-10-DCM-R-C	DKE	811-2858-ND	Z21-22	52.75	52.75	105.50	-105.50	0.00
C11	C11	1	Each	Meter Switch	Meter Switch: DP3T On-On-On, Panel Mount		2	2		3/8/23	3/8/23	NKK Switches	M2044SS1W01	DKE	360-2082-ND	https://www.digikey.com/en/products/detail/nkk-switches/M2044SS1W01/1007139	15.39	15.39	30.78	5.75	36.53
C12	C12	1	Each	DC/DC Output Switch	Traco Output Switch: SPST On-Off, Panel Mount		2	2		3/8/23	3/8/23	NKK Switches	M2011SS1W01	DKE	360-2827-ND	https://www.digikey.com/en/products/detail/nkk-switches/M2011SS1W01/1049352	4.73	4.73	9.46	1.77	11.23
C13	C13	1	Each	Barrier Strip	Barrier Strip: 3 Positions, Single Row, Bottom Termination Solder Turrets		2	2		3/8/23	3/8/23	Molex	387203803	DKE	WM20049-ND	https://www.digikey.com/en/products/detail/molex/0387203803/3599369	4.51	4.51	9.02	0.78	9.80
C14	C14	2	Each	Meter Assembly Fuses	Meter Assembly Fuses: 0.25A Slow Blow, 30VDC, Pigtail or Pico	55		4	51		2003?		230 2AG - 2A 250V				0.40	0.80	1.60		1.60
		Hardware
H1	H1	1	Each	Backplate	Backplate: Aluminum Sheet 10x14x0.080"		2	2		3/8/23	3/8/23		3003-H14 (10x14")	MBTF	080ALSM + 0000CUT		11.39	11.39	22.79	24.32	47.11
H2	H2	1	Each	Meter/Output Plate	Meter/Output Plate: Aluminum Sheet 3x5x0.080"		2	2		3/8/23	3/8/23		3003-H14 (3x5")	MBTF	080ALSM + 0000CUT		1.22	1.22	2.44	2.61	5.05
H3	H3	1	Oz	Paint	Paint: High Heat	32.2		2.8	29		10/15/22	Rust-Oleum	7778 BAR-B-Q BLACK	Amazon.com	7778830	https://www.amazon.com/gp/product/B0010O0C94/ref=ox_sc_act_title_1?smid=ATVPDKIKX0DER&th=1	0.50	0.70	1.41		1.41
H4	H4	4	Each	Backplate Feet	Backplate Feet: 1/2" High, Nylon, Screw Mount, Cylindrical, Recessed Center, 5/8" OD		25	8	17	3/8/23	3/8/23	Essentra Components	BRR025A	DKE	RPC5642-ND	https://www.digikey.com/en/products/detail/essentra-components/BRR025A/9343103	0.22	0.88	1.76	0.48	2.23
H5	H5	2	Each	3x0.5x6mm Star Drive Pan Head Screw	3x0.5x6mm Star Drive Pan Head Screw: T10 Torx, SS 18-8 (A-2)	96		4	92	11/25/22	11/25/22			BDC	19243	https://www.boltdepot.com/Product-Details.aspx?product=19243	0.06	0.11	0.22		0.22
H6	H6	2	Each	3mm Split Washer	3mm Split Washer: SS 18-8 (A-2)	96		4	92	11/25/22	11/25/22			BDC	4810	https://www.boltdepot.com/Product-Details.aspx?product=4810	0.02	0.03	0.06		0.06
H7	H7	4	Each	#6-32 Meter Plate Standoffs	#6-32 Meter Plate Standoffs: Male-Female, 1" High, 1/4" Hex, Aluminum		10	8	2	3/8/23	3/8/23	RAF Electronic Hardware	4542-632-AL	DKE	1772-1387-ND	https://www.digikey.com/en/products/detail/raf-electronic-hardware/4542-632-AL/7680798	0.44	1.77	3.54	0.38	3.92
H8	H8	10	Each	#6-32x3/8" Star Drive Pan Head Screw	#6-32x3/8" Star Drive Pan Head Screw: T15 Torx, SS 18-8	78		20	58	11/25/22	11/25/22			BDC	19124	https://www.boltdepot.com/Product-Details.aspx?product=19124	0.12	1.18	2.37		6.25
H9	H9	2	Each	#6-32x3/4" Star Drive Pan Head Screw	#6-32x3/4" Star Drive Pan Head Screw: T15 Torx, SS 18-8		100	4	92	3/8/23	3/8/23			BDC	19127	https://www.boltdepot.com/Product-Details.aspx?product=19127	0.14	0.28	0.56	3.88	4.44
H10	H10	4	Each	#6 Split Washer	#6 Split Washer: SS 18-8	90		8	78	11/25/22	11/25/22			BDC	2953	https://www.boltdepot.com/Product-Details.aspx?product=2953	0.02	0.10	0.20		0.20
H11	H11	12	Each	#6-32 KEPS Nut	#6-32 KEPS Nut: SS 18-8		100	24	72	3/8/23	3/8/23			BDC	12019	https://www.boltdepot.com/Product-Details.aspx?product=12019	0.05	0.60	1.20	1.39	2.59
H12	H12	4	Each	4x0.7x6mm Star Drive Pan Head Screw	4x0.7x6mm Star Drive Pan Head Screw: T20 Torx, SS 18-8 (A-2)	92		8	84	11/25/22	11/25/22			BDC	19246	https://www.boltdepot.com/Product-Details.aspx?product=19246	0.07	0.28	0.56		0.56
H13	H13	4	Each	4mm Split Washer	4mm Split Washer: SS 18-8 (A-2)	92		8	84	11/25/22	11/25/22			BDC	4811	https://www.boltdepot.com/Product-Details.aspx?product=4811	0.02	0.06	0.13		0.13
H14	H14	4	Each	#8-32x5/8" Star Drive Pan Head Screw	#8-32x5/8" Star Drive Pan Head Screw: T20 Torx, SS 18-8		100	8	92	3/8/23	3/8/23			BDC	19136	https://www.boltdepot.com/Product-Details.aspx?product=19136	0.15	0.61	1.22	4.27	5.49
H15	H15	4	Each	#8-32 KEPS Nut	#8-32 KEPS Nut: SS 18-8		100	8	92	3/8/23	3/8/23			BDC	12020	https://www.boltdepot.com/Product-Details.aspx?product=12020	0.06	0.25	0.49	1.72	2.21
H16	H16	1	Each	5/16"-18x1.25" Hex Head Tap Bolt	5/16"-18x1.25" Hex Head Tap Bolt	7		2	5		2/22/23			BDC	18314	https://www.boltdepot.com/Product-Details.aspx?product=18314	0.20	0.20	0.41		0.41
H17	H17	2	Each	5/16" External Star Washer	5/16" External Star Washer: SS 410	25		4	21		2/22/23			BDC	4081	https://www.boltdepot.com/Product-Details.aspx?product=4081	0.08	0.17	0.34		0.34
H18	H18	2	Each	5/16"-18 Nut	5/16"-18 Nut: SS 316			4			2/22/23			BDC	15984	https://www.boltdepot.com/Product-Details.aspx?product=15984	0.11	0.21	0.43		0.43
H19	H19	1	Each	5/16" Split Washer	5/16" Split Washer: Zinc plated grade 8 yellow			2			2/22/23			BDC	3038	https://www.boltdepot.com/Product-Details.aspx?product=3038	0.04	0.04	0.07		0.07
		Wire
W1	W1	40	Inches	#10 Stranded Black	#10 Stranded Black	151		80	71		2/23/23	Prysmian Group	76832.18.01	DKE	C76832B-100-ND	https://www.digikey.com/en/products/detail/prysmian-group/76832-18-01/5452535	0.07	2.71	5.43		5.43
W2	W2	28	Inches	#12 Stranded Red	#12 Stranded Red	59		56	3	5/26/20	2/23/23	Remington Industries	12STRREDGPT25	DKE	2328-12STRREDGPT25-ND	https://www.digikey.com/product-detail/en/12STRREDGPT25/2328-12STRREDGPT25-ND/11612528/?itemSeq=327489099	0.05	1.51	3.02		3.02
W3	W3	7	Inches	#12 Solid Red	#12 Solid Red			14.2			11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	0.11	0.22		0.22
W4	W4	19	Inches	#12 Solid Brown	#12 Solid Brown	297		38.6	258		11/6/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-12-Gauge-Brown-Solid-Copper-THHN-Wire-112-1658J/202304784	0.02	0.30	0.60		0.60
W5	W5	6	Inches	#14 Solid Bare	#14 Solid Bare			12			11/7/22	Cerrowire	THHN, 600v, 90⁰C	Home Depot		https://www.homedepot.com/p/Cerrowire-500-ft-14-Gauge-Gray-Solid-Copper-THHN-Wire-112-1460J/305306723	0.01	0.06	0.12		0.12
W6	W6	1	Each	AC Power Cord	AC Power Cord: NEMA, 15A 120VAC L/N/G, 5' 9"			2			Estimate					3.00	3.00	6.00		6.00
W7	W7	15	Inches	#16 Stranded Black	#16 Stranded Black			29.0			11/7/22	CNC Tech	1569-16-1-0500-001-1-TS	DKE	CN642B-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-001-1-TS/9450423	0.03	0.46	0.92		0.92
W8	W8	14	Inches	#16 Stranded White	#16 Stranded White			28.0			11/7/22	CNC Tech	1569-16-1-0500-002-1-TS	DKE	CN643W-25-ND	https://www.digikey.com/en/products/detail/cnc-tech/1569-16-1-0500-002-1-TS/9450424	0.03	0.44	0.89		0.89
W9	W9	5	Inches	#18 Solid Bare	#18 Solid Bare			10.0			Estimate					0.02	0.12	0.23		0.23
W10	W10	2	Inches	#18 Solid Blue	#18 Solid Blue			4.0			Estimate					0.02	0.05	0.09		0.09
W11	W11	2	Inches	#18 Solid Green	#18 Solid Green			4.0			Estimate					0.02	0.05	0.09		0.09
W12	W12	10	Inches	#18 Solid Red	#18 Solid Red			20.0			Estimate					0.02	0.23	0.47		0.47
W13	W13	12	Inches	#18 Solid Brown	#18 Solid Brown			23.4			Estimate					0.02	0.27	0.55		0.55
W14	W14	6	Inches	#18 Solid Yellow	#18 Solid Yellow			12.0			Estimate					0.02	0.14	0.28		0.28
W15	W15	9	Inches	#18 Solid Orange	#18 Solid Orange			18.0			Estimate					0.02	0.21	0.42		0.42
W16	W16	9	Inches	#18 Solid White	#18 Solid White			18.0			Estimate					0.02	0.21	0.42		0.42
W17	W17	9	Inches	#22 Solid Bare	#22 Solid Bare			18			11/7/22	SparkFun Electronics	PRT-08023 [Red]	DKE	1568-1570-ND	https://www.digikey.com/products/en?keywords=1568-1570-ND	0.01	0.08	0.17		0.17
W18	W18	41	Inches	#24 to #20 2-Conductor Stranded Zip/Rip Cord	#24 to #20 2-Conductor Stranded Zip/Rip Cord			82			Estimate					0.02	0.68	1.37		1.37
		Miscellaneous
M1	M1	4	Each	5/16" Ring Connector #10-12 AWG	5/16" Ring Connector #10-12 AWG: Bare (No Insulation)	101		8	93	11/25/22	11/25/22	3M	13-56	DKE	3M157204-ND	https://www.digikey.com/products/en?keywords=3M157204-ND	0.18	0.70	1.41		1.41
M2	M2	1	Each	5/16" Ring Connector #4 AWG	5/16" Ring Connector #4 AWG: Bare (No Insulation)	1	10	2	9	3/8/23	3/8/23	TE Connectivity	33470	MOU	571-33470	https://www.mouser.com/ProductDetail/TE-Connectivity/33470?qs=PhejhE5GxlxR3fqYNXf3FA%3D%3D	0.83	0.83	1.65	1.04	2.69
M3	M3	2	Each	1/4" Female Spade Connector #10-12 AWG	1/4" Female Spade Connector #10-12 AWG: Bare	30		4	26		11/9/22	Molex	192030379	DKE	WM19887-ND	https://www.digikey.com/en/products/detail/molex/0192030379/3187492	0.09	0.19	0.38		0.38
M4	M4	2	Each	1/4" Female Spade Connector #14-16 AWG	1/4" Female Spade Connector #14-16 AWG: Bare	28		4	24		11/9/22	Molex	192030390	DKE	WM19888-ND	https://www.digikey.com/en/products/detail/molex/0192030390/3187491	0.09	0.17	0.35		0.35
M5	M5	4	Inches	3/32" Shrink Tubing	3/32" Shrink Tubing	35		7.0	28	Unknown	Estimate					0.19	0.68	1.35		1.35
M6	M6	7	Inches	3/16" Shrink Tubing	3/16" Shrink Tubing	45.3		13.4	32	6/27/22	11/10/22	3M	EPS-200 3/16"BL48"BX	DKE	EPS2316-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-3-16-BL48-BX/260270	0.22	1.48	2.95		2.95
M7	M7	11	Inches	1/4” Shrink Tubing	1/4” Shrink Tubing	239		22.0	217	11/25/22	11/25/22	3M	EPS-200 1/4"BL 48"BX	DKE	EPS2014-ND	https://www.digikey.com/products/en?keywords=EPS2014-ND	0.25	2.74	5.48		5.48
M8	M8	3	Inches	1/2" Shrink Tubing	1/2" Shrink Tubing	48		6	42	6/27/22	11/10/22	3M	EPS-200 1/2" BL 48"BX	DKE	EPS2012-ND	https://www.digikey.com/en/products/detail/3m/EPS-200-1-2-BL-48-BX/260262	0.34	1.03	2.05		2.05
M9	M9	0	Oz	Penatrox a-13 Electrical Joint Compound	Penatrox a-13 Electrical Joint Compound	4.0		0.2	4		10/16/22	Burndy	PENA138	Amazon.com	PENETROX A-13, 8 fl. oz.	https://www.amazon.com/Burndy-A13-8-Oxide-Inhibiting-Compounds-Container/dp/B00CBKBZO2/ref=sr_1_1?gclid=Cj0KCQjw166aBhDEARIsAMEyZh7w66CXA1fkdfGT0na5LTNuqM_CwmKyOjJmdIP748Th28Dxvora2mkaAvNOEALw_wcB&hvadid=580957328063&hvdev=c&hvlocphy=9023208&hvnetw=g&hvqmt=b&hvrand=17878932423775935625&hvtargid=kwd-301888752915&hydadcr=3649_13538990&keywords=burndy+penetrox+a+13&qid=1665931056&qu=eyJxc2MiOiIxLjQ4IiwicXNhIjoiMC4wMCIsInFzcCI6IjAuMDAifQ%3D%3D&sr=8-1&ufe=app_do%3Aamzn1.fos.006c50ae-5d4c-4777-9bc0-4513d670b6bc	6.88	0.69	1.38		1.38
M10	M10	0	Oz	Epoxy	Epoxy: Resin and Hardener	9.3		0.1	9	8/9/22	8/9/22	Devcon	5 Minute Epoxy, 2 Bottles 8.50 Fl Oz total	Amazon.com			2.12	0.11	0.21		0.21
M11	M11	8	Grams	Solder	Solder: "44" Rosin Core .050"	297		16	281	5/26/20	11/10/22	Kester	24-6337-0053 / J-STD-006A	DKE	KE1108-ND	https://www.digikey.com/products/en?keywords=KE1108-ND	0.13	1.07	2.15		2.15
M12	M12	19	Each	Zip Tie	Zip Tie: 4", White	66		38	28	11/25/22	11/25/22	Belden	DT-04-18-9-C	DKE	BEL8889-ND	https://www.digikey.com/product-detail/en/belden-inc/DT-04-18-9-C/BEL8889-ND/8599226	0.04	0.69	1.38		1.38
M13	M13	3	Inches	Silver Tape	Silver Tape			6			8/1/18	Fasson	UL181A-P/181B-FX	Amazon.com	B00HRWUJBO		0.01	0.02	0.05		0.05
		Labels
L1	L1	3	Inches	0.23" White	0.23" White: 6mm			5.7		6/22/19	Estimate	Brother	TZe-211	Amazon.com			0.05	0.13	0.26		0.26
L2	L2	27	Inches	0.47" White	0.47" White: 12mm	424		53.5	370	11/25/22	11/25/22	Brother	TZe-S231	PTD		https://www.ptouchdirect.com/ptouch/tzes231cs.html	0.05	1.30	2.61		2.61
L3	L3	5	Inches	0.47" Yellow	0.47" Yellow: 12mm	301		10.1	291	11/25/22	11/25/22	Brother	TZe-S631	PTD		https://www.ptouchdirect.com/ptouch/tzes631.html	0.05	0.25	0.50		0.50
L4	L4	2	Inches	0.7" White	0.7" White: 18mm	409		4.3	405	11/25/22	11/25/22	Brother	TZe-S241	PTD		https://www.ptouchdirect.com/ptouch/tzes241.html	0.06	0.12	0.24		0.24
L5	L5	11	Inches	0.94" White	0.94" White: 24mm	390		22.4	367	6/22/19	11/11/22	Brother	TZe-S251	Amazon.com		https://www.amazon.com/s?k=brother+tze+S251&ref=nb_sb_noss_2	0.07	0.82	1.64		1.64
L6	L6	5	Inches	0.94" Yellow	0.94" Yellow: 24mm	353		10.4	342	6/22/19	11/11/22	Brother	TZ-FX651	Amazon.com		https://www.amazon.com/s/ref=nb_sb_noss_2?url=search-alias%3Daps&field-keywords=brother+TZ-FX651&rh=i%3Aaps%2Ck%3Abrother+TZ-FX651	0.07	0.37	0.75		0.75
		Accessories
				No Accessories yet

70		Ingredients (Unique Parts)					475.63	951.26	3.00	958.14

## WP14-15A
WISPers: WP14-15A	D				ASSEMBLY LABOR	Quantity:	2
						WP14 ... WP15	W150_4 ... W150_5

Labor				Assembly Phase Descriptions and Notes
Date Started	Date Completed	Hours	Hours Each	Part Number(s)	Procedure Specification	Problems, Exceptions	Next Time, Improvements
Su10/9/22	Mo3/13/23	32.0	16.0		Procurement [P]
Fr2/10/23		2.3	1.2	All	Prep: Copy and link the PARTS and ASSEMBLY LABOR sheets from the previous run and plan the next run / Generally all comments are left in place until they no longer apply (they can be edited for this run's data) / PARTS Sheet: (Do NOT set Quantity yet); (Collapse grouped subcount lines and be careful not to clobber them when editing!) / Copy Stock Quantities from Remaining to Before (values, highlighting and comments)* / Delete values from Ordered; Remove values, formulas, comments and highlighting from Remaining (select, delete, no fill) / Enter default formulas in Remaining (=Before+Ordered-Used, select Visible Rows Only when copying) / Clear cells (Backspace, values and formulas but not comments) in Tariff Tax S&H Miles; Set Quantity / ASSEMBLY LABOR Sheet: / Clear and unmerge cells in Date Started and Date Completed (include section headers; Backspace, do not clear comments) / Clear cells in Hours (exclude section headers; Backspace, do not clear comments) but do not unmerge cells; Set Quantity / Both Sheets: Record data for any already completed work	The Murata Meters were procured first due to their generous offer of two free samples (unusually high labor to track those samples), then everything else needed was ordered in one day / The Procurement [P] section was vastly expanded and improved (lots of R&D not assembly) / I spent time scanning and renaming annotated invoices for LIB (assembly and R&D) until I realized that we don't need to make a practice of doing this (they are all paper filed well enough to find if needed) and so I removed the requirement from Receive	Procurement should be performed all at once, working from these sheets / There were (5) parts ordered for this run that won't have to be ordered for a long time (screws, nuts and ring connectors) / Hours should be less for the next run due to unified and simplified procedures
					R&D: * Update PARTS and ASSEMBLY lists for design and procedure changes; Save important datasheets to LIB
Su10/9/22	We3/8/23	3.1	1.6	C1-C5 C10-C13 / H1 H2 H4 H7 / H9 H11 H14 H15 / M2	Plan: Orders pre-planned; Clear bench to layout parts; Take inventory as needed and update Stock Quantities > Before / Supplier Stock Checks: Order Information and Unit Cost updated as needed (comments for supplier stock levels for critical parts) / FTR: Make a list of parts to be ordered organized by supplier, part, quantities and $ (strategies determined)
Mo11/21/22		3.0	1.5		Place: Orders placed for the most questionable/critical parts/suppliers first / Record Ordered and Remaining quantities and Order Date; Purchases $ recorded in Budget Management (USB/SPF, estimate if needed) / ← List parts ordered for this Production Run here
We11/23/22	Fr3/10/23	5.5	2.8		Track: Orders followup as needed and communications with suppliers / Print final invoices received by email; Budget Management $ corrected/finalized (USB/SPF) / Monitor emails/communications/TODO until orders and invoices are received
Fr12/2/22	Mo3/13/23	18.1	9.1	L1 / L2	Receive: When orders arrive mark the shipping box with received date; Annotate invoices; Resolve supplier errors / Tariff/Tax/S&H/Miles amounts and comments finalized (delete all other unneeded comments); Hand labels for storage of parts / Tracked devices: Create and fill out Summary entries and History sheets; L1/L2 inventory labels printed and applied
Th5/25/23	Fr5/26/23	2.2	1.1		Paint and Scribe [PS]
Th5/25/23	05/25/23	0.6	0.3	H1 H2 H3	Paint Aluminum Plates: Weigh H3 paint; Set up on the porch; If air T is low paint in the sun, otherwise in the shade / H1 and H2 plates s/b 50-90⁰F (monitor closely with Fluke IRT), avoid overheating from the sun; Shake can vigorously for several minutes / Remove plastic covering and paint immediately, spraying 12-16" from backplate; Two or three light coats separated by minutes / Clear nozzle; Weigh H3 paint and record consumption; Allow to dry 12 hours at 75⁰F before scribing
Fr5/26/23		1.6	0.8	H1 H2 M13	Scribe Hole Locations on Plates: As per Hole Locations and Sizes drawings (Cardboard Template for Backplate and Meter/Output Plate) / On only one of the plates for the run (the top plate in milling the stacks); Browne & Sharpe; Angle blocks, M13 silver tape / Backplate: Scribe locations by halves / quadrants (measured from left side, right side, bottom, top) / Meter/Output Plate: Scribe locations measured from left side then bottom / Scribe lines should continue through all locations that are in line (except mounting and feet holes at the outer edges)
05/25/23		1.2	0.6		Clausing Mill [CM]
Th5/25/23		0.7	0.4		Clean and Oil the Clausing Mill: Table XYZ slides cleaned (papertowels); All oil zircs
Fr5/26/23		0.5	0.3		Prep: Gather and Layout Tooling ― All that will be needed to drill, mill and deburr the holes (common Clausing tools/wrenches not listed): / Vertical Vise (and table bolt sets) / Clamp Bolt Sets (Meter Plate, 4x, 6-32): 3/4" Torx pan head (T15); Lock washer (under head); KEPS nut (under plates) / Clamp Bolt Sets (Backplate, 2x, 5/16"-18): 1" HH tap bolt; Flat washer (under head); Star lockwasher (under backplates); Nut / Partical Board 3x5x3/4": Corners relieved / Partical Board 10x14x3/4": Relieved with openings in the mounting hole areas on top and bottom (for inserting the Clamp Bolt Sets) / C-Clamps: For temporary use in clamping the backplate stack together to move from Dad's vise to the mill / Drills: 3/32 (0.094); 1/8 (0.125); 9/64 (0.141); 11/64 (0.172); 1/4 (0.250); 9/32 (0.281); 5/16 (0.313) / Center Drills: #1 (~0.050/0.125) [3/32]; #2 (~0.080/0.187) [1/8, 9/64]; #3 (~0.110/0.250) [11/64] / Hole Saw 1-3/16" (not sure yet if we'll need the boring tool to enlarge the meter hole) / Headlamp; Countersink; Isopropyl Alcohol and Paper Towels for Clean Up
			0	H1	Clamp Backplate Stack Together: Stack all the backplates for the run in Dad's vise (Board, plates, paper on top) / Optimize alignment between the plates (right side edges sitting down on vise rods, short edges tapped into alignment) / Tighten vise and install C-Clamps in the area where the mounting/clamp holes are to go (in relieved area of Board underneath)
			0	H1	Mill Holes, Backplates: 10x14" partical board support; Cardboard protectors under clamps on Clausing table1 / Clamp the backplate stack down to the table firmly2 and remove the C-Clamps / Drill the two mounting holes, insert and tighten temporary 5/16"-18 bolts, nuts and washers to clamp the backplate stack together3 / Drill/mill all the holes for the right side4; Reset for the left side; Drill/mill all the holes for the left side4; Remove temporary 5/16"-18 bolts
			0	H2	Clamp Meter Plate Stack Together: Vertical Vise mounted on table (flipped down to 0⁰); Stack the plates by hand into the vise and tighten the vise jaws while maintaining alignment; Flip the vise up and set precise vertical; Spot and drill four 9/64" corner holes (Japanese collet); Insert and tighten four 6-32 Clamp Bolt Sets; Remove plates from vise and vise from table
			0	H2	Mill Holes, Meter Plates: 3x5" partical board support; Cardboard protectors under clamps on Clausing table / Locate and drill the meter hole (table locked, 1-3/16" hole saw)1; Locate and drill/cut the meter tab hole (table locked, 3/32", side cut)2 / Spot, overdrill and drill the small holes3; Drill the larger holes4
			0	H1 H2	Countersink/Deburr Plates: Individually clamped in Dad's vise (protect with paper) / Backplates: Countersink both sides of 1/4" holes (zip ties, Diode) / Meter Plates: Countersink both sides of 1/4 and 9/32" holes (zip tie, switches and barrier strip insulator holes)
			0	H1 H2	Completion: Clean backplates (isopropyl, paper towels); Clean up mill/garage areas (tools put away, sweep/vacuum)
		0	0		Hardware Assembly [HA]
			0	H4-H19 / M9 M12	Prep: Count out the parts H4-H19 in tuna cans; Weigh and warm M9 Penatrox* / Check/modify beginning inventory on M12 zip ties
			0	H1 H4 H14 H15	Feet Installed
			0	C1 H1 H5 H6 / M9 M12	Charger: Temporarily attach PCB wire bundle to grill with M12 zip tie / Apply M9 Penatrox to back; Mount with H5 screws and H6 split washers (M9 Penatrox*)
			0	C3 / H1 / M9	Diode: Apply M9 Penatrox on base and thread; Install included washers and nut; 11/16" wrench / Orientation/rotation: Solder tab hole should face up/down (not right/left) / 28 lbf-in maximum, tighten by feel, not aggressive, do not overtighten but make sure star washer is firmly dug into aluminum
			0	C4 H1 H8 H11	Contactor: Mount with H8 screws and H11 KEPS
			0	C5 H1 H12 H13 M9	Load Supply: Apply M9 Penatrox to back; Mount with H12 screws and H13 split washers (M9 Penatrox*)
			0	C8 H1 H8 H11 M9	Traco: Apply M9 Penatrox and mount with H8 screws and H11 KEPS
			0	H1 H16-H19 / M9	FG Post: Apply M9 Penatrox; H16 bolt, H17 star washers and H18 nut tightened onto backplate / Additional H18 top nut left loose for assembly of (2) ring connectors; (H19 split washer will be applied in WC before tightening)
			0	H1 H7 H11 M9	Meter/Output Plate Standoffs: Apply M9 Penatrox to H7 male end and mount to backplate with H11 KEPS
			0	C10 H2	Meter
			0	C11 H2	Meter Switch
			0	C12 H2	Traco Output Switch
			0	C13 H2 H9 H11	Barrier Strip: Mount with H9 screws and H11 KEPS; (Left side mounting screw will be loosened in WC to attach Gnd wire)
			0	H4-H19	Completion: Put away remaining parts (label with quantities/dates); Update Remaining Stock Quantities on PARTS list as needed
		0	0		Wiring and Cabling [WC]
			0	C2 C6 C7 C9 C14 / W1-W18 / M1-M4 M9-M11	Prep: Count out C2 NTCs, C6-C7 fuses/holders, C9 resistors and C14 fuses in tuna cans / Wire stocks W1-W18 laid out on the bench; Cut all wire and cable as per PARTS sheet*; Count out connectors M1-M4 in tuna cans / Check/update Remaining Stock Quantities for NTCs, fuses/holders, resistors, wire and connectors while counting and cutting / Warm M9 Penatrox*; Weigh M10 Epoxy and M11 Solder (record "before" weights in comments on PARTS sheet)
			0	C1 H1 / M5 M12	Charger Wires Prep: Remove temporary zip tie holding PCB wire bundle to grill / Cut C1 B+ red wire 10.5" from PCB; Cut other wires 3.0" from PCB / Charger B- black wire strip/twist/tin/clean 0.3"; M5 shrink on extra wires from C1 (+V blk, org, yel); Extras attached to grill with M12 zip tie
			0	C1 H1 / W6 M12	120 VAC Cord to Charger: W6 cut to 5' 9" long (if not done in Prep); Coil the plug end with M12 zip tie (temporary) / W6 strip outer jacket 1.5"; W6 L/N/G strip/twist/tin/clean 0.3"; Loosely attach to C1 L/N/G
			0	C1 C4 C5 H1 / W7 M4 M7	120 VAC Line from Charger to Contactor to Load Supply: W7x2 strip/twist 0.4"; W7x2 M4 spade crimp/solder/clean; M7 shrink / W7x2 strip/twist/tin/clean 0.3"; Attach to C4 lower left, C1 and C5 Line
			0	C1 C4 C5 H1 / W8 M4 M7 M12	120 VAC Neutral from Charger to Contactor to Load Supply: W8x2 strip/twist 0.4"; W8x2 M4 spade crimp/solder/clean; M7 shrink / W8x2 strip/twist/tin/clean 0.3"; Attach to C4 lower right, C1 and C5 Neutral / (3) M12 zip ties (below C1, below C5 and exit at bottom); Apply AC to check for DOAs (green LEDs on Charger and Load Supply)
			0	H1 H18 W1 / M1 M7 M9 M12	Battery Negative to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink; Repeat for other end / Attach to FG Post (M9 Penatrox bottom side, leave H18 top nut loose); M12 zip tie
			0	C4 / H1 H18 H19 / W1 / M1 M3 M7 M9	Contactor to FG Post: W1 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink / W1 strip/twist 0.4"; M3 spade crimp/solder/clean; M7 shrink / Apply M9 Penatrox and attach to C4 top left NC contact; Apply M10 Penatrox to ring connector bottom and top sides and place on FG Post / Add H19 split washer and H18 nut; Tighten H18 nut very tight on (2) ring connectors (Battery Negative, Contactor)
				C3-C5 / H1 / W4 / M3 M6 M9	Contactor to Diode to RSP -V: Cut 1" of insulation from the middle of W4 (measurement details to be determined) / W4 strip 0.3" (Contactor end); M3 spade crimp/solder/clean; M6 shrink; W4 strip 0.4" (RSP -V end) / Insert, bend and prefit W4 from C4 top right NC contact through C3 Diode Anode to C5 RSP -V right screw left side / Attach to C4 Contactor and C5 RSP -V (apply M9 Penatrox at both ends); Solder W4 to C3 Diode (quick, not too hot); Clean
			0	C5-C7 H1 / W2 W17 / M1 M7 M9 M12 M13	Battery Positive to RSP +V: W2 and C6 fuse holder strip/twist 1.0"; W17 butt splice wrap/torch/clean*; M7 shrink / C6 strip/twist 0.4"; M1 ring crimp/solder/clean; M7 shrink; Install C7 fuse; Attach C7 spare fuse with M13 silver tape / W2 strip/twist/tin/clean 0.4"; Apply M9 Penatrox and loosely attach to C5 +V left screw right side; M12 zip ties	W2 ~29.7" below backplate	Increased W2 length by 0.3"
			0	C5 C8 H1 / W3 W5 W17 / M7 M9	RSP +V to Traco +Vin: W5 bent into "V" shape* / W3 strip 1.0"; W5 W3 W17 butt splice wrap/torch/clean; M7 shrink; W3 strip 1.0" (voltmeter clip lead test point) / Bend and prefit W3 from C8 +Vin to C5 +V left screw left side (form vertical Extech test loop on left side); Attach to C8* / Apply M9 Penatrox and attach to C5	Shortened M7 from 2.0 to 1.8" / Applied Penatrox to Traco end and had to clean with Q-tip and acetone	Do not apply Penatrox on Traco end
			0	C5 C8 H1 / W4 W5 W17 / M7 M9	RSP -V to Traco -Vin: W5 bent into "V" shape / W4 strip 1.0"; W5 W4 W17 butt splice wrap/torch/clean; M7 shrink; W4 strip 0.4" / Bend and prefit W4 from C8 -Vin to C5 -V right screw right side; Attach to C8*; Apply M9 Penatrox and attach to C5	Applied Penatrox to Traco end and had to clean with Q-tip and acetone	Do not apply Penatrox on Traco end
			0	C1 C5 H1 M12	Charger B+ to RSP +V: C1 B+ strip/twist/tin/clean 0.4"; Attach to C5 +V right screw left side; M12 zip tie below C1 (Extech test loop)	Forgot to clean with acetone	Use acetone to clean solder flux
			0	C10 C13 / H2 H9 H11 / W9 / M9	Meter/Output Assembly GND: Remove H11 KEPS from H9 screw (C13 Barrier Strip left side mounting screw) / Wrap end of W9 around H9; Apply M9 Penatrox; Reapply and tighten H11 KEPS / Wrap middle of W9 around left side solder turret on C13 Barrier Strip; Wrap end of W9 around C10 Meter Switch pin 6 / Solder/clean connections on C10 and C13
			0	C11 H2 W9	Meter Switch Jumpers: Install 2xW9 jumpers on C11 (pins 3 to 5 and pins 9 to 11); Solder/clean
			0	C10 C11 H2 / W10 W11	Meter Switch to Meter Inputs: W10 and W11 strip 0.3" (Meter end) and 0.4" (Switch end) / Wrap W10 on C11 pin 8; Wrap W11 on C11 pin 2; Solder/clean; Attach W10 and W11 to C10 (+) and (-)
			0	C5 C14 / W12 W13 M6	Meter Fuse Assemblies: Two sets W12/C14/W12/M6 (RSP +V) and W13/C14/W13/M6 (RSP -V): W12s/W13s strip 0.4" from both ends / Straighten leads on fuses; W12s/W13s soldered to C14 fuses (4 butt splices); Clean and apply M6 shrink
				C11 H2 W12	Meter Switch Jumper (RSP +V): W12 strip 0.4" both ends; Wrap on pin 12 (solder/clean); Wrap on pin 10 (do not solder)
				C11 C14 H2 W12	Meter Fuse Assembly to Meter Switch (RSP +V): Wrap long end of W12 assembly made above around Meter Switch pin 10; Solder/clean
			0	C11 C12 H2 W13	Meter Switch to Output Switch (RSP -V): W13 strip 0.4" both ends; Wrap on C12 pin 2 (solder/clean); Wrap on C11 pin 4 (do not solder)
			0	C11 C14 H2 W13	Meter Fuse Assembly to Meter Switch (RSP -V): Wrap long end of W13 assembly made above around C11 pin 4; Solder/clean
			0	C8 C12 H2 W14	Output Switch to Traco Ctrl: Wrap W14 around C12 pin 3; Solder/clean
			0	C11 C13 H2 W15	Barrier Strip to Meter Switch (Traco +Vout): Wrap W15 on C11 pin 7 (solder/clean); Wrap W15 on C13 right side turret (do not solder)
			0	C8 C13 H2 W15	Barrier Strip to Traco +Vout: Wrap W15 on C13 right side turret; Solder/clean
				C11 C13 H2 W16	Barrier Strip to Meter Switch (Traco -Vout): Wrap W16 on C11 pin 1 (solder/clean); Wrap W16 on C13 center turret (do not solder)
				C8 C13 H2 W16	Barrier Strip to Traco -Vout: Wrap W16 on C13 center turret; Solder/clean
			0	C5 C8 C10-C14 / H1 H2 H7 H8 H10 / W12-W16 / M9 M12	Install Meter/Output Assembly: Apply M9 Penatrox to top of H7 Standoffs / Position assembly on standoffs and install H8 screws with H10 washers / Attach W12 Meter Fuse Assembly to C5 +V right screw right side; Attach W13 Meter Fuse Assembly to C5 -V left screw left side / Attach W14 to C8 Ctrl; Attach W15 to C8 +Vout (Extech test loop); Attach W16 to C8 -Vout; M12 zip ties
			0	C8 C9 M6 L1	Traco Output Trim R: C9 bend leads and cut to 0.6"; M6 shrink/crimp; Measure with Fluke, print and apply L1; Install on C8
			0	C1 C2 / W18 / M2 M5 M6 M8 / M10 M12	BTS: Assemble sensor to zip wire, epoxy into battery post connector and solder zip wire to charger CN2 connector pins: / Assemble C2 NTC sensor to W18 zip wire with layers of shrink: W18 split 1.5", strip/twist/tin 0.3" and preload with M5 shrink / C2 NTC cut to 0.6"; W18 C2 dual butt solder/clean/shrink; Add M6 shrink (crimp/seal tip) / Epoxy Sensor Assembly Into Ring with Double Layer of Shrink: Flatten M2 ring in garage vise for a snug fit to sensor; "Helping Hand" with paper towel underneath, 60⁰ angle down from ring (almost vertical); M10 epoxy, do not get epoxy on ring!; M8 shrink 2x crimp/seal / Solder BTS Assembly to CN2 Connector Pins: C1 heat and remove CN2 connector plastic shell; W18 split 0.7" strip/tin 0.4" / W18 bend small loops, M12 zip tie to side hole on C1, crimp to CN2 connector pins; Pencil iron tack solder/clean / M12 strain relief zip tie on C1 grill; (3) M12 zip ties *	BC10/WP12 BTS: Was already assembled to the zip wire and soldered to the CN2 pins [T48S]; Extends 48" below the W150 backplate bottom; Completely finished assembly of WP12 before coming back to assemble the BC11/WP13 BTS	Fabricate entire BTS assembly in this step / Finish all units in production run before proceeding
			0	C2 C6 C7 C9 C14 / W1-W18 / M1-M12	Completion: Check/update Remaining Stock Quantities for NTCs, fuses/holders, resistors, wire, connectors, shrink tubing and zip ties* / Weigh M9 Penatrox, M10 Epoxy and M11 Solder (update consumption on PARTS sheet) / M12 zip ties count checked/modified*; Tighten all wiring connection screws; Clean up the bench	Step not completed all at once (WP13 was delayed until after finishing WP12)*	Finish all units in production run before proceeding to Configuration and Testing / * Note on M9-M11 consumptions
		0	0		Configuration and Testing [CT]
			0		Prep: Each W150 is configured and tested individually; No battery is required; W150 next to Engel; Set Z19 for target 25.0⁰C / BTS and Z19 T2 bolted together in metal pipe with bubble wrap to keep air out of the pipe in center of Engel enclosure / ITECH and Fluke turned on (keep shop ambient stable throughout configuration and testing); ITECH Von Living 5.0v	WP12 and WP13 were not done one after the other (almost a month apart)	Save time by moving through all the W150s in the Production Run without interruptions
			0	C1	Charger Configuration: ITECH on end of battery cables, Sense ON; W150 AC power applied (T1 UPS) / Verify that contactor opens and that three supplies are up (green LEDs, Meter shows three voltages); Test Traco disable / ITECH CC 150mA; Stabilize Engel/BTS at 25.0⁰C; Adjust charger for target 13.500vI (record achieved value)	BC10/WP12: Charger adjusted on T48S (recorded achieved value)
			0	C1	Charger Burn-In: [ITECH remains on end of battery cables]; 90wIS* for >=12 hours ... / ITECH load OFF and disconnected (protect battery cable ends from accidental short)	BC10/WP12: Burn-in only 1.2 hours	Burn-in for >=12 hours
			0	C5	Load Supply Configuration: ITECH Sense on RSP +V and Diode anode*; No load (except Traco idle) / Wait for W150 stabilization (cool-down from burn-in, vI stable for 15m); Adjust Load Supply for target 13.700vI (record achieved value)	Hunted for the right screwdriver	Save time by moving through all the W150s in the Production Run without interruptions
			0	C5 C8	Load Supply and Traco Burn-In: ITECH with Sense on Traco output at Barrier Strip / 20wIS; Wait ~1h for stabilization (≤ ± 1mV change over a 15m period), record Traco output vI * / 180wIS for >=12 hours ... / ITECH load OFF and disconnected; W150 AC power disconnected; BTS removed from Engel / (Go to Prep for next W150 in Production Run)	Traco output vI was recorded at 0wIS and without sufficient time to stabilize	Record Traco output vI at 20wIS after sufficient stabilization
			0		Completion: After all the W150s are Configured and Tested: / Engel/Dinico/ITECH/Fluke OFF and Status=Available / Tighten ALL Screws; Tools put away	Not completed all at once (WP13 was delayed until after finishing WP12)	Finish all units in production run at the same time
		0	0		Labels Applied [LA]
			0	L3-L6	Print and Apply Labels: See PARTS for LBX files (filenames indicate locations on W150); Clean with isopropyl before applying* / Update PARTS list Labels Remaining Stock Quantities as needed (there's other consumption besides for the W150s)	Not completed all at once (WP13 was delayed until after finishing WP12)	Finish all units in production run at the same time
		0	0		Assembly Completion [AC]
			0		Photos
			0		Prep for Transport: Coil up AC Input and Battery Cables (twist ties, old stock); Box for protection and transport
			0	C1 C5 C8 C10	WISPer, tracked equipment and Location .ods records completed
			0		PARTS and ASSEMBLY LABOR sheets completed: FTR Assembly Hours totalled and checked against totals here; Protect sheets (no password)
		35.4	17.7		Entire Assembly Procedure Completed